## AQ 250 v2.5.7.1-400 AP3
HR | Parameter | Access | Length | Info
1 | Modbus requests | R/W=0 | 1 | Diagnostic request counter
2 | Modbus quality | R | 1 | Diagnostic quality
3 | Modbus errors | R/W=0 | 1 | Diagnostic error counter
4 | Modbus Ctrl OK | R/W=0 | 1 | Diagnostic Control OK counter
5 | Modbus Ctrl Errors | R/W=0 | 1 | Diagnostic Control Error counter
6 | Object1 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
7 | Object2 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
8 | Object3 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9 | Object4 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
10 | Object5 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
11 | Previous Event register | R | 6 | Event code
12 | Previous Event register | R | 6 | Event timestamp (ms)
13 | Previous Event register | R | 6 | Event timestamp (sec Hi-16bits)
14 | Previous Event register | R | 6 | Event timestamp (sec Lo-16bits)
15 | Previous Event register | R | 6 | Event sequential index
16 | Previous Event register | R | 6 | RESERVED
17 | Event register | R | 6 | Event code
18 | Event register | R | 6 | Event timestamp (ms)
19 | Event register | R | 6 | Event timestamp (sec Hi-16bits)
20 | Event register | R | 6 | Event timestamp (sec Lo-16bits)
21 | Event register | R | 6 | Event sequential index
22 | Event register | R | 6 | RESERVED
23 | System time | RW | 3 | System time (ms)
24 | System time | RW | 3 | System time (sec Hi-16bits)
25 | System time | RW | 3 | System time (sec Lo-16bits)
26 | MEAS1:Pri.Pha.curr.IL1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
27 |  |  |  | HR26 (Lo-16bits)
28 | MEAS1:Pri.Pha.curr.IL2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
29 |  |  |  | HR28 (Lo-16bits)
30 | MEAS1:Pri.Pha.curr.IL3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
31 |  |  |  | HR30 (Lo-16bits)
32 | MEAS1:Pha.angle IL1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
33 |  |  |  | HR32 (Lo-16bits)
34 | MEAS1:Pha.angle IL2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
35 |  |  |  | HR34 (Lo-16bits)
36 | MEAS1:Pha.angle IL3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
37 |  |  |  | HR36 (Lo-16bits)
38 | MEAS1:Pri.Res.curr.I01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
39 |  |  |  | HR38 (Lo-16bits)
40 | MEAS1:Res.curr.angle I01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
41 |  |  |  | HR40 (Lo-16bits)
42 | MEAS1:Pri.Res.curr.I02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
43 |  |  |  | HR42 (Lo-16bits)
44 | MEAS1:Res.curr.angle I02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
45 |  |  |  | HR44 (Lo-16bits)
46 | MEAS1:Pri.calc.I0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
47 |  |  |  | HR46 (Lo-16bits)
48 | MEAS1:Calculated I0 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
49 |  |  |  | HR48 (Lo-16bits)
50 | MEAS1:Pha.curr.IL1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
51 |  |  |  | HR50 (Lo-16bits)
52 | MEAS1:Pha.curr.IL2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
53 |  |  |  | HR52 (Lo-16bits)
54 | MEAS1:Pha.curr.IL3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
55 |  |  |  | HR54 (Lo-16bits)
56 | MEAS1:Pri.Positive sequence curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
57 |  |  |  | HR56 (Lo-16bits)
58 | MEAS1:Pri.Negative sequence curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
59 |  |  |  | HR58 (Lo-16bits)
60 | MEAS1:Pri.Zero sequence curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
61 |  |  |  | HR60 (Lo-16bits)
62 | MEAS1:Positive sequence curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
63 |  |  |  | HR62 (Lo-16bits)
64 | MEAS1:Negative sequence curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
65 |  |  |  | HR64 (Lo-16bits)
66 | MEAS1:Zero sequence curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
67 |  |  |  | HR66 (Lo-16bits)
68 | MEAS1:Res.curr.I01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
69 |  |  |  | HR68 (Lo-16bits)
70 | MEAS1:Res.curr.I02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
71 |  |  |  | HR70 (Lo-16bits)
72 | MEAS1:Pha.L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
73 |  |  |  | HR72 (Lo-16bits)
74 | MEAS1:Pha.L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
75 |  |  |  | HR74 (Lo-16bits)
76 | MEAS1:Pha.L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
77 |  |  |  | HR76 (Lo-16bits)
78 | MEAS1:Pha.L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
79 |  |  |  | HR78 (Lo-16bits)
80 | MEAS1:Pha.L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
81 |  |  |  | HR80 (Lo-16bits)
82 | MEAS1:Pha.L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
83 |  |  |  | HR82 (Lo-16bits)
84 | MEAS1:Res.I01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
85 |  |  |  | HR84 (Lo-16bits)
86 | MEAS1:Res.I01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
87 |  |  |  | HR86 (Lo-16bits)
88 | MEAS1:Res.I02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
89 |  |  |  | HR88 (Lo-16bits)
90 | MEAS1:Res.I02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
91 |  |  |  | HR90 (Lo-16bits)
92 | MEAS1:P-P curr.IL1 | R | 2 | FLOAT [0...500] (Hi-16bits)
93 |  |  |  | HR92 (Lo-16bits)
94 | MEAS1:P-P curr.IL2 | R | 2 | FLOAT [0...500] (Hi-16bits)
95 |  |  |  | HR94 (Lo-16bits)
96 | MEAS1:P-P curr.IL3 | R | 2 | FLOAT [0...500] (Hi-16bits)
97 |  |  |  | HR96 (Lo-16bits)
98 | MEAS1:P-P curr.I01 | R | 2 | FLOAT [0...500] (Hi-16bits)
99 |  |  |  | HR98 (Lo-16bits)
100 | MEAS1:P-P curr.I02 | R | 2 | FLOAT [0...500] (Hi-16bits)
101 |  |  |  | HR100 (Lo-16bits)
102 | MEAS1:IL1 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
103 |  |  |  | HR102 (Lo-16bits)
104 | MEAS1:IL1 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
105 |  |  |  | HR104 (Lo-16bits)
106 | MEAS1:IL1 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
107 |  |  |  | HR106 (Lo-16bits)
108 | MEAS1:IL1 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
109 |  |  |  | HR108 (Lo-16bits)
110 | MEAS1:IL1 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
111 |  |  |  | HR110 (Lo-16bits)
112 | MEAS1:IL1 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
113 |  |  |  | HR112 (Lo-16bits)
114 | MEAS1:IL1 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
115 |  |  |  | HR114 (Lo-16bits)
116 | MEAS1:IL1 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
117 |  |  |  | HR116 (Lo-16bits)
118 | MEAS1:IL1 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
119 |  |  |  | HR118 (Lo-16bits)
120 | MEAS1:IL1 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
121 |  |  |  | HR120 (Lo-16bits)
122 | MEAS1:IL1 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
123 |  |  |  | HR122 (Lo-16bits)
124 | MEAS1:IL1 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
125 |  |  |  | HR124 (Lo-16bits)
126 | MEAS1:IL1 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
127 |  |  |  | HR126 (Lo-16bits)
128 | MEAS1:IL1 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
129 |  |  |  | HR128 (Lo-16bits)
130 | MEAS1:IL1 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
131 |  |  |  | HR130 (Lo-16bits)
132 | MEAS1:IL1 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
133 |  |  |  | HR132 (Lo-16bits)
134 | MEAS1:IL1 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
135 |  |  |  | HR134 (Lo-16bits)
136 | MEAS1:IL1 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
137 |  |  |  | HR136 (Lo-16bits)
138 | MEAS1:IL1 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
139 |  |  |  | HR138 (Lo-16bits)
140 | MEAS1:IL1 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
141 |  |  |  | HR140 (Lo-16bits)
142 | MEAS1:IL1 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
143 |  |  |  | HR142 (Lo-16bits)
144 | MEAS1:IL1 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
145 |  |  |  | HR144 (Lo-16bits)
146 | MEAS1:IL1 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
147 |  |  |  | HR146 (Lo-16bits)
148 | MEAS1:IL1 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
149 |  |  |  | HR148 (Lo-16bits)
150 | MEAS1:IL1 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
151 |  |  |  | HR150 (Lo-16bits)
152 | MEAS1:IL1 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
153 |  |  |  | HR152 (Lo-16bits)
154 | MEAS1:IL1 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
155 |  |  |  | HR154 (Lo-16bits)
156 | MEAS1:IL1 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
157 |  |  |  | HR156 (Lo-16bits)
158 | MEAS1:IL1 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
159 |  |  |  | HR158 (Lo-16bits)
160 | MEAS1:IL1 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
161 |  |  |  | HR160 (Lo-16bits)
162 | MEAS1:IL1 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
163 |  |  |  | HR162 (Lo-16bits)
164 | MEAS1:IL2 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
165 |  |  |  | HR164 (Lo-16bits)
166 | MEAS1:IL2 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
167 |  |  |  | HR166 (Lo-16bits)
168 | MEAS1:IL2 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
169 |  |  |  | HR168 (Lo-16bits)
170 | MEAS1:IL2 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
171 |  |  |  | HR170 (Lo-16bits)
172 | MEAS1:IL2 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
173 |  |  |  | HR172 (Lo-16bits)
174 | MEAS1:IL2 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
175 |  |  |  | HR174 (Lo-16bits)
176 | MEAS1:IL2 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
177 |  |  |  | HR176 (Lo-16bits)
178 | MEAS1:IL2 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
179 |  |  |  | HR178 (Lo-16bits)
180 | MEAS1:IL2 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
181 |  |  |  | HR180 (Lo-16bits)
182 | MEAS1:IL2 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
183 |  |  |  | HR182 (Lo-16bits)
184 | MEAS1:IL2 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
185 |  |  |  | HR184 (Lo-16bits)
186 | MEAS1:IL2 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
187 |  |  |  | HR186 (Lo-16bits)
188 | MEAS1:IL2 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
189 |  |  |  | HR188 (Lo-16bits)
190 | MEAS1:IL2 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
191 |  |  |  | HR190 (Lo-16bits)
192 | MEAS1:IL2 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
193 |  |  |  | HR192 (Lo-16bits)
194 | MEAS1:IL2 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
195 |  |  |  | HR194 (Lo-16bits)
196 | MEAS1:IL2 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
197 |  |  |  | HR196 (Lo-16bits)
198 | MEAS1:IL2 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
199 |  |  |  | HR198 (Lo-16bits)
200 | MEAS1:IL2 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
201 |  |  |  | HR200 (Lo-16bits)
202 | MEAS1:IL2 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
203 |  |  |  | HR202 (Lo-16bits)
204 | MEAS1:IL2 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
205 |  |  |  | HR204 (Lo-16bits)
206 | MEAS1:IL2 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
207 |  |  |  | HR206 (Lo-16bits)
208 | MEAS1:IL2 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
209 |  |  |  | HR208 (Lo-16bits)
210 | MEAS1:IL2 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
211 |  |  |  | HR210 (Lo-16bits)
212 | MEAS1:IL2 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
213 |  |  |  | HR212 (Lo-16bits)
214 | MEAS1:IL2 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
215 |  |  |  | HR214 (Lo-16bits)
216 | MEAS1:IL2 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
217 |  |  |  | HR216 (Lo-16bits)
218 | MEAS1:IL2 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
219 |  |  |  | HR218 (Lo-16bits)
220 | MEAS1:IL2 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
221 |  |  |  | HR220 (Lo-16bits)
222 | MEAS1:IL2 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
223 |  |  |  | HR222 (Lo-16bits)
224 | MEAS1:IL2 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
225 |  |  |  | HR224 (Lo-16bits)
226 | MEAS1:IL3 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
227 |  |  |  | HR226 (Lo-16bits)
228 | MEAS1:IL3 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
229 |  |  |  | HR228 (Lo-16bits)
230 | MEAS1:IL3 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
231 |  |  |  | HR230 (Lo-16bits)
232 | MEAS1:IL3 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
233 |  |  |  | HR232 (Lo-16bits)
234 | MEAS1:IL3 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
235 |  |  |  | HR234 (Lo-16bits)
236 | MEAS1:IL3 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
237 |  |  |  | HR236 (Lo-16bits)
238 | MEAS1:IL3 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
239 |  |  |  | HR238 (Lo-16bits)
240 | MEAS1:IL3 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
241 |  |  |  | HR240 (Lo-16bits)
242 | MEAS1:IL3 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
243 |  |  |  | HR242 (Lo-16bits)
244 | MEAS1:IL3 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
245 |  |  |  | HR244 (Lo-16bits)
246 | MEAS1:IL3 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
247 |  |  |  | HR246 (Lo-16bits)
248 | MEAS1:IL3 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
249 |  |  |  | HR248 (Lo-16bits)
250 | MEAS1:IL3 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
251 |  |  |  | HR250 (Lo-16bits)
252 | MEAS1:IL3 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
253 |  |  |  | HR252 (Lo-16bits)
254 | MEAS1:IL3 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
255 |  |  |  | HR254 (Lo-16bits)
256 | MEAS1:IL3 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
257 |  |  |  | HR256 (Lo-16bits)
258 | MEAS1:IL3 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
259 |  |  |  | HR258 (Lo-16bits)
260 | MEAS1:IL3 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
261 |  |  |  | HR260 (Lo-16bits)
262 | MEAS1:IL3 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
263 |  |  |  | HR262 (Lo-16bits)
264 | MEAS1:IL3 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
265 |  |  |  | HR264 (Lo-16bits)
266 | MEAS1:IL3 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
267 |  |  |  | HR266 (Lo-16bits)
268 | MEAS1:IL3 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
269 |  |  |  | HR268 (Lo-16bits)
270 | MEAS1:IL3 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
271 |  |  |  | HR270 (Lo-16bits)
272 | MEAS1:IL3 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
273 |  |  |  | HR272 (Lo-16bits)
274 | MEAS1:IL3 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
275 |  |  |  | HR274 (Lo-16bits)
276 | MEAS1:IL3 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
277 |  |  |  | HR276 (Lo-16bits)
278 | MEAS1:IL3 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
279 |  |  |  | HR278 (Lo-16bits)
280 | MEAS1:IL3 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
281 |  |  |  | HR280 (Lo-16bits)
282 | MEAS1:IL3 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
283 |  |  |  | HR282 (Lo-16bits)
284 | MEAS1:IL3 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
285 |  |  |  | HR284 (Lo-16bits)
286 | MEAS1:IL3 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
287 |  |  |  | HR286 (Lo-16bits)
288 | MEAS1:I01 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
289 |  |  |  | HR288 (Lo-16bits)
290 | MEAS1:I01 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
291 |  |  |  | HR290 (Lo-16bits)
292 | MEAS1:I01 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
293 |  |  |  | HR292 (Lo-16bits)
294 | MEAS1:I01 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
295 |  |  |  | HR294 (Lo-16bits)
296 | MEAS1:I01 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
297 |  |  |  | HR296 (Lo-16bits)
298 | MEAS1:I01 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
299 |  |  |  | HR298 (Lo-16bits)
300 | MEAS1:I01 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
301 |  |  |  | HR300 (Lo-16bits)
302 | MEAS1:I01 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
303 |  |  |  | HR302 (Lo-16bits)
304 | MEAS1:I01 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
305 |  |  |  | HR304 (Lo-16bits)
306 | MEAS1:I01 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
307 |  |  |  | HR306 (Lo-16bits)
308 | MEAS1:I01 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
309 |  |  |  | HR308 (Lo-16bits)
310 | MEAS1:I01 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
311 |  |  |  | HR310 (Lo-16bits)
312 | MEAS1:I01 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
313 |  |  |  | HR312 (Lo-16bits)
314 | MEAS1:I01 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
315 |  |  |  | HR314 (Lo-16bits)
316 | MEAS1:I01 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
317 |  |  |  | HR316 (Lo-16bits)
318 | MEAS1:I01 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
319 |  |  |  | HR318 (Lo-16bits)
320 | MEAS1:I01 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
321 |  |  |  | HR320 (Lo-16bits)
322 | MEAS1:I01 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
323 |  |  |  | HR322 (Lo-16bits)
324 | MEAS1:I01 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
325 |  |  |  | HR324 (Lo-16bits)
326 | MEAS1:I01 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
327 |  |  |  | HR326 (Lo-16bits)
328 | MEAS1:I01 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
329 |  |  |  | HR328 (Lo-16bits)
330 | MEAS1:I01 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
331 |  |  |  | HR330 (Lo-16bits)
332 | MEAS1:I01 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
333 |  |  |  | HR332 (Lo-16bits)
334 | MEAS1:I01 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
335 |  |  |  | HR334 (Lo-16bits)
336 | MEAS1:I01 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
337 |  |  |  | HR336 (Lo-16bits)
338 | MEAS1:I01 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
339 |  |  |  | HR338 (Lo-16bits)
340 | MEAS1:I01 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
341 |  |  |  | HR340 (Lo-16bits)
342 | MEAS1:I01 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
343 |  |  |  | HR342 (Lo-16bits)
344 | MEAS1:I01 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
345 |  |  |  | HR344 (Lo-16bits)
346 | MEAS1:I01 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
347 |  |  |  | HR346 (Lo-16bits)
348 | MEAS1:I01 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
349 |  |  |  | HR348 (Lo-16bits)
350 | MEAS1:I02 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
351 |  |  |  | HR350 (Lo-16bits)
352 | MEAS1:I02 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
353 |  |  |  | HR352 (Lo-16bits)
354 | MEAS1:I02 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
355 |  |  |  | HR354 (Lo-16bits)
356 | MEAS1:I02 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
357 |  |  |  | HR356 (Lo-16bits)
358 | MEAS1:I02 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
359 |  |  |  | HR358 (Lo-16bits)
360 | MEAS1:I02 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
361 |  |  |  | HR360 (Lo-16bits)
362 | MEAS1:I02 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
363 |  |  |  | HR362 (Lo-16bits)
364 | MEAS1:I02 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
365 |  |  |  | HR364 (Lo-16bits)
366 | MEAS1:I02 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
367 |  |  |  | HR366 (Lo-16bits)
368 | MEAS1:I02 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
369 |  |  |  | HR368 (Lo-16bits)
370 | MEAS1:I02 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
371 |  |  |  | HR370 (Lo-16bits)
372 | MEAS1:I02 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
373 |  |  |  | HR372 (Lo-16bits)
374 | MEAS1:I02 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
375 |  |  |  | HR374 (Lo-16bits)
376 | MEAS1:I02 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
377 |  |  |  | HR376 (Lo-16bits)
378 | MEAS1:I02 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
379 |  |  |  | HR378 (Lo-16bits)
380 | MEAS1:I02 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
381 |  |  |  | HR380 (Lo-16bits)
382 | MEAS1:I02 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
383 |  |  |  | HR382 (Lo-16bits)
384 | MEAS1:I02 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
385 |  |  |  | HR384 (Lo-16bits)
386 | MEAS1:I02 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
387 |  |  |  | HR386 (Lo-16bits)
388 | MEAS1:I02 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
389 |  |  |  | HR388 (Lo-16bits)
390 | MEAS1:I02 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
391 |  |  |  | HR390 (Lo-16bits)
392 | MEAS1:I02 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
393 |  |  |  | HR392 (Lo-16bits)
394 | MEAS1:I02 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
395 |  |  |  | HR394 (Lo-16bits)
396 | MEAS1:I02 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
397 |  |  |  | HR396 (Lo-16bits)
398 | MEAS1:I02 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
399 |  |  |  | HR398 (Lo-16bits)
400 | MEAS1:I02 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
401 |  |  |  | HR400 (Lo-16bits)
402 | MEAS1:I02 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
403 |  |  |  | HR402 (Lo-16bits)
404 | MEAS1:I02 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
405 |  |  |  | HR404 (Lo-16bits)
406 | MEAS1:I02 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
407 |  |  |  | HR406 (Lo-16bits)
408 | MEAS1:I02 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
409 |  |  |  | HR408 (Lo-16bits)
410 | MEAS1:I02 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
411 |  |  |  | HR410 (Lo-16bits)
412 | MEAS2:Pri.Pha.curr.I''L1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
413 |  |  |  | HR412 (Lo-16bits)
414 | MEAS2:Pri.Pha.curr.I''L2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
415 |  |  |  | HR414 (Lo-16bits)
416 | MEAS2:Pri.Pha.curr.I''L3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
417 |  |  |  | HR416 (Lo-16bits)
418 | MEAS2:Pha.angle I''L1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
419 |  |  |  | HR418 (Lo-16bits)
420 | MEAS2:Pha.angle I''L2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
421 |  |  |  | HR420 (Lo-16bits)
422 | MEAS2:Pha.angle I''L3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
423 |  |  |  | HR422 (Lo-16bits)
424 | MEAS2:Pri.Res.curr.I''01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
425 |  |  |  | HR424 (Lo-16bits)
426 | MEAS2:Res.curr.angle I''01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
427 |  |  |  | HR426 (Lo-16bits)
428 | MEAS2:Pri.Res.curr.I''02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
429 |  |  |  | HR428 (Lo-16bits)
430 | MEAS2:Res.curr.angle I''02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
431 |  |  |  | HR430 (Lo-16bits)
432 | MEAS2:Pri.calc.I''0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
433 |  |  |  | HR432 (Lo-16bits)
434 | MEAS2:Calculated I''0 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
435 |  |  |  | HR434 (Lo-16bits)
436 | MEAS2:Pha.curr.I''L1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
437 |  |  |  | HR436 (Lo-16bits)
438 | MEAS2:Pha.curr.I''L2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
439 |  |  |  | HR438 (Lo-16bits)
440 | MEAS2:Pha.curr.I''L3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
441 |  |  |  | HR440 (Lo-16bits)
442 | MEAS2:I'' Pri.Positive sequence curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
443 |  |  |  | HR442 (Lo-16bits)
444 | MEAS2:I'' Pri.Negative sequence curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
445 |  |  |  | HR444 (Lo-16bits)
446 | MEAS2:I'' Pri.Zero sequence curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
447 |  |  |  | HR446 (Lo-16bits)
448 | MEAS2:I'' Positive sequence curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
449 |  |  |  | HR448 (Lo-16bits)
450 | MEAS2:I'' Negative sequence curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
451 |  |  |  | HR450 (Lo-16bits)
452 | MEAS2:I'' Zero sequence curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
453 |  |  |  | HR452 (Lo-16bits)
454 | MEAS2:Res.curr.I''01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
455 |  |  |  | HR454 (Lo-16bits)
456 | MEAS2:Res.curr.I''02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
457 |  |  |  | HR456 (Lo-16bits)
458 | MEAS2:Pha.I''L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
459 |  |  |  | HR458 (Lo-16bits)
460 | MEAS2:Pha.I''L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
461 |  |  |  | HR460 (Lo-16bits)
462 | MEAS2:Pha.I''L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
463 |  |  |  | HR462 (Lo-16bits)
464 | MEAS2:Pha.I''L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
465 |  |  |  | HR464 (Lo-16bits)
466 | MEAS2:Pha.I''L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
467 |  |  |  | HR466 (Lo-16bits)
468 | MEAS2:Pha.I''L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
469 |  |  |  | HR468 (Lo-16bits)
470 | MEAS2:Res.I''01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
471 |  |  |  | HR470 (Lo-16bits)
472 | MEAS2:Res.I''01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
473 |  |  |  | HR472 (Lo-16bits)
474 | MEAS2:Res.I''02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
475 |  |  |  | HR474 (Lo-16bits)
476 | MEAS2:Res.I''02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
477 |  |  |  | HR476 (Lo-16bits)
478 | MEAS2:P-P curr.I''L1 | R | 2 | FLOAT [0...500] (Hi-16bits)
479 |  |  |  | HR478 (Lo-16bits)
480 | MEAS2:P-P curr.I''L2 | R | 2 | FLOAT [0...500] (Hi-16bits)
481 |  |  |  | HR480 (Lo-16bits)
482 | MEAS2:P-P curr.I''L3 | R | 2 | FLOAT [0...500] (Hi-16bits)
483 |  |  |  | HR482 (Lo-16bits)
484 | MEAS2:P-P curr.I''01 | R | 2 | FLOAT [0...500] (Hi-16bits)
485 |  |  |  | HR484 (Lo-16bits)
486 | MEAS2:P-P curr.I''02 | R | 2 | FLOAT [0...500] (Hi-16bits)
487 |  |  |  | HR486 (Lo-16bits)
488 | MEAS2:I''L1 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
489 |  |  |  | HR488 (Lo-16bits)
490 | MEAS2:I''L1 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
491 |  |  |  | HR490 (Lo-16bits)
492 | MEAS2:I''L1 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
493 |  |  |  | HR492 (Lo-16bits)
494 | MEAS2:I''L1 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
495 |  |  |  | HR494 (Lo-16bits)
496 | MEAS2:I''L1 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
497 |  |  |  | HR496 (Lo-16bits)
498 | MEAS2:I''L1 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
499 |  |  |  | HR498 (Lo-16bits)
500 | MEAS2:I''L1 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
501 |  |  |  | HR500 (Lo-16bits)
502 | MEAS2:I''L1 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
503 |  |  |  | HR502 (Lo-16bits)
504 | MEAS2:I''L1 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
505 |  |  |  | HR504 (Lo-16bits)
506 | MEAS2:I''L1 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
507 |  |  |  | HR506 (Lo-16bits)
508 | MEAS2:I''L1 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
509 |  |  |  | HR508 (Lo-16bits)
510 | MEAS2:I''L1 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
511 |  |  |  | HR510 (Lo-16bits)
512 | MEAS2:I''L1 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
513 |  |  |  | HR512 (Lo-16bits)
514 | MEAS2:I''L1 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
515 |  |  |  | HR514 (Lo-16bits)
516 | MEAS2:I''L1 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
517 |  |  |  | HR516 (Lo-16bits)
518 | MEAS2:I''L1 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
519 |  |  |  | HR518 (Lo-16bits)
520 | MEAS2:I''L1 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
521 |  |  |  | HR520 (Lo-16bits)
522 | MEAS2:I''L1 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
523 |  |  |  | HR522 (Lo-16bits)
524 | MEAS2:I''L1 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
525 |  |  |  | HR524 (Lo-16bits)
526 | MEAS2:I''L1 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
527 |  |  |  | HR526 (Lo-16bits)
528 | MEAS2:I''L1 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
529 |  |  |  | HR528 (Lo-16bits)
530 | MEAS2:I''L1 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
531 |  |  |  | HR530 (Lo-16bits)
532 | MEAS2:I''L1 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
533 |  |  |  | HR532 (Lo-16bits)
534 | MEAS2:I''L1 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
535 |  |  |  | HR534 (Lo-16bits)
536 | MEAS2:I''L1 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
537 |  |  |  | HR536 (Lo-16bits)
538 | MEAS2:I''L1 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
539 |  |  |  | HR538 (Lo-16bits)
540 | MEAS2:I''L1 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
541 |  |  |  | HR540 (Lo-16bits)
542 | MEAS2:I''L1 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
543 |  |  |  | HR542 (Lo-16bits)
544 | MEAS2:I''L1 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
545 |  |  |  | HR544 (Lo-16bits)
546 | MEAS2:I''L1 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
547 |  |  |  | HR546 (Lo-16bits)
548 | MEAS2:I''L1 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
549 |  |  |  | HR548 (Lo-16bits)
550 | MEAS2:I''L2 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
551 |  |  |  | HR550 (Lo-16bits)
552 | MEAS2:I''L2 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
553 |  |  |  | HR552 (Lo-16bits)
554 | MEAS2:I''L2 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
555 |  |  |  | HR554 (Lo-16bits)
556 | MEAS2:I''L2 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
557 |  |  |  | HR556 (Lo-16bits)
558 | MEAS2:I''L2 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
559 |  |  |  | HR558 (Lo-16bits)
560 | MEAS2:I''L2 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
561 |  |  |  | HR560 (Lo-16bits)
562 | MEAS2:I''L2 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
563 |  |  |  | HR562 (Lo-16bits)
564 | MEAS2:I''L2 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
565 |  |  |  | HR564 (Lo-16bits)
566 | MEAS2:I''L2 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
567 |  |  |  | HR566 (Lo-16bits)
568 | MEAS2:I''L2 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
569 |  |  |  | HR568 (Lo-16bits)
570 | MEAS2:I''L2 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
571 |  |  |  | HR570 (Lo-16bits)
572 | MEAS2:I''L2 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
573 |  |  |  | HR572 (Lo-16bits)
574 | MEAS2:I''L2 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
575 |  |  |  | HR574 (Lo-16bits)
576 | MEAS2:I''L2 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
577 |  |  |  | HR576 (Lo-16bits)
578 | MEAS2:I''L2 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
579 |  |  |  | HR578 (Lo-16bits)
580 | MEAS2:I''L2 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
581 |  |  |  | HR580 (Lo-16bits)
582 | MEAS2:I''L2 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
583 |  |  |  | HR582 (Lo-16bits)
584 | MEAS2:I''L2 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
585 |  |  |  | HR584 (Lo-16bits)
586 | MEAS2:I''L2 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
587 |  |  |  | HR586 (Lo-16bits)
588 | MEAS2:I''L2 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
589 |  |  |  | HR588 (Lo-16bits)
590 | MEAS2:I''L2 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
591 |  |  |  | HR590 (Lo-16bits)
592 | MEAS2:I''L2 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
593 |  |  |  | HR592 (Lo-16bits)
594 | MEAS2:I''L2 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
595 |  |  |  | HR594 (Lo-16bits)
596 | MEAS2:I''L2 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
597 |  |  |  | HR596 (Lo-16bits)
598 | MEAS2:I''L2 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
599 |  |  |  | HR598 (Lo-16bits)
600 | MEAS2:I''L2 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
601 |  |  |  | HR600 (Lo-16bits)
602 | MEAS2:I''L2 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
603 |  |  |  | HR602 (Lo-16bits)
604 | MEAS2:I''L2 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
605 |  |  |  | HR604 (Lo-16bits)
606 | MEAS2:I''L2 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
607 |  |  |  | HR606 (Lo-16bits)
608 | MEAS2:I''L2 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
609 |  |  |  | HR608 (Lo-16bits)
610 | MEAS2:I''L2 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
611 |  |  |  | HR610 (Lo-16bits)
612 | MEAS2:I''L3 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
613 |  |  |  | HR612 (Lo-16bits)
614 | MEAS2:I''L3 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
615 |  |  |  | HR614 (Lo-16bits)
616 | MEAS2:I''L3 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
617 |  |  |  | HR616 (Lo-16bits)
618 | MEAS2:I''L3 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
619 |  |  |  | HR618 (Lo-16bits)
620 | MEAS2:I''L3 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
621 |  |  |  | HR620 (Lo-16bits)
622 | MEAS2:I''L3 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
623 |  |  |  | HR622 (Lo-16bits)
624 | MEAS2:I''L3 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
625 |  |  |  | HR624 (Lo-16bits)
626 | MEAS2:I''L3 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
627 |  |  |  | HR626 (Lo-16bits)
628 | MEAS2:I''L3 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
629 |  |  |  | HR628 (Lo-16bits)
630 | MEAS2:I''L3 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
631 |  |  |  | HR630 (Lo-16bits)
632 | MEAS2:I''L3 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
633 |  |  |  | HR632 (Lo-16bits)
634 | MEAS2:I''L3 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
635 |  |  |  | HR634 (Lo-16bits)
636 | MEAS2:I''L3 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
637 |  |  |  | HR636 (Lo-16bits)
638 | MEAS2:I''L3 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
639 |  |  |  | HR638 (Lo-16bits)
640 | MEAS2:I''L3 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
641 |  |  |  | HR640 (Lo-16bits)
642 | MEAS2:I''L3 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
643 |  |  |  | HR642 (Lo-16bits)
644 | MEAS2:I''L3 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
645 |  |  |  | HR644 (Lo-16bits)
646 | MEAS2:I''L3 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
647 |  |  |  | HR646 (Lo-16bits)
648 | MEAS2:I''L3 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
649 |  |  |  | HR648 (Lo-16bits)
650 | MEAS2:I''L3 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
651 |  |  |  | HR650 (Lo-16bits)
652 | MEAS2:I''L3 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
653 |  |  |  | HR652 (Lo-16bits)
654 | MEAS2:I''L3 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
655 |  |  |  | HR654 (Lo-16bits)
656 | MEAS2:I''L3 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
657 |  |  |  | HR656 (Lo-16bits)
658 | MEAS2:I''L3 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
659 |  |  |  | HR658 (Lo-16bits)
660 | MEAS2:I''L3 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
661 |  |  |  | HR660 (Lo-16bits)
662 | MEAS2:I''L3 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
663 |  |  |  | HR662 (Lo-16bits)
664 | MEAS2:I''L3 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
665 |  |  |  | HR664 (Lo-16bits)
666 | MEAS2:I''L3 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
667 |  |  |  | HR666 (Lo-16bits)
668 | MEAS2:I''L3 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
669 |  |  |  | HR668 (Lo-16bits)
670 | MEAS2:I''L3 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
671 |  |  |  | HR670 (Lo-16bits)
672 | MEAS2:I''L3 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
673 |  |  |  | HR672 (Lo-16bits)
674 | MEAS2:I''01 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
675 |  |  |  | HR674 (Lo-16bits)
676 | MEAS2:I''01 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
677 |  |  |  | HR676 (Lo-16bits)
678 | MEAS2:I''01 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
679 |  |  |  | HR678 (Lo-16bits)
680 | MEAS2:I''01 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
681 |  |  |  | HR680 (Lo-16bits)
682 | MEAS2:I''01 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
683 |  |  |  | HR682 (Lo-16bits)
684 | MEAS2:I''01 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
685 |  |  |  | HR684 (Lo-16bits)
686 | MEAS2:I''01 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
687 |  |  |  | HR686 (Lo-16bits)
688 | MEAS2:I''01 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
689 |  |  |  | HR688 (Lo-16bits)
690 | MEAS2:I''01 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
691 |  |  |  | HR690 (Lo-16bits)
692 | MEAS2:I''01 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
693 |  |  |  | HR692 (Lo-16bits)
694 | MEAS2:I''01 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
695 |  |  |  | HR694 (Lo-16bits)
696 | MEAS2:I''01 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
697 |  |  |  | HR696 (Lo-16bits)
698 | MEAS2:I''01 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
699 |  |  |  | HR698 (Lo-16bits)
700 | MEAS2:I''01 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
701 |  |  |  | HR700 (Lo-16bits)
702 | MEAS2:I''01 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
703 |  |  |  | HR702 (Lo-16bits)
704 | MEAS2:I''01 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
705 |  |  |  | HR704 (Lo-16bits)
706 | MEAS2:I''01 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
707 |  |  |  | HR706 (Lo-16bits)
708 | MEAS2:I''01 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
709 |  |  |  | HR708 (Lo-16bits)
710 | MEAS2:I''01 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
711 |  |  |  | HR710 (Lo-16bits)
712 | MEAS2:I''01 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
713 |  |  |  | HR712 (Lo-16bits)
714 | MEAS2:I''01 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
715 |  |  |  | HR714 (Lo-16bits)
716 | MEAS2:I''01 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
717 |  |  |  | HR716 (Lo-16bits)
718 | MEAS2:I''01 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
719 |  |  |  | HR718 (Lo-16bits)
720 | MEAS2:I''01 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
721 |  |  |  | HR720 (Lo-16bits)
722 | MEAS2:I''01 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
723 |  |  |  | HR722 (Lo-16bits)
724 | MEAS2:I''01 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
725 |  |  |  | HR724 (Lo-16bits)
726 | MEAS2:I''01 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
727 |  |  |  | HR726 (Lo-16bits)
728 | MEAS2:I''01 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
729 |  |  |  | HR728 (Lo-16bits)
730 | MEAS2:I''01 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
731 |  |  |  | HR730 (Lo-16bits)
732 | MEAS2:I''01 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
733 |  |  |  | HR732 (Lo-16bits)
734 | MEAS2:I''01 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
735 |  |  |  | HR734 (Lo-16bits)
736 | MEAS2:I''02 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
737 |  |  |  | HR736 (Lo-16bits)
738 | MEAS2:I''02 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
739 |  |  |  | HR738 (Lo-16bits)
740 | MEAS2:I''02 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
741 |  |  |  | HR740 (Lo-16bits)
742 | MEAS2:I''02 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
743 |  |  |  | HR742 (Lo-16bits)
744 | MEAS2:I''02 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
745 |  |  |  | HR744 (Lo-16bits)
746 | MEAS2:I''02 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
747 |  |  |  | HR746 (Lo-16bits)
748 | MEAS2:I''02 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
749 |  |  |  | HR748 (Lo-16bits)
750 | MEAS2:I''02 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
751 |  |  |  | HR750 (Lo-16bits)
752 | MEAS2:I''02 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
753 |  |  |  | HR752 (Lo-16bits)
754 | MEAS2:I''02 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
755 |  |  |  | HR754 (Lo-16bits)
756 | MEAS2:I''02 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
757 |  |  |  | HR756 (Lo-16bits)
758 | MEAS2:I''02 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
759 |  |  |  | HR758 (Lo-16bits)
760 | MEAS2:I''02 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
761 |  |  |  | HR760 (Lo-16bits)
762 | MEAS2:I''02 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
763 |  |  |  | HR762 (Lo-16bits)
764 | MEAS2:I''02 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
765 |  |  |  | HR764 (Lo-16bits)
766 | MEAS2:I''02 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
767 |  |  |  | HR766 (Lo-16bits)
768 | MEAS2:I''02 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
769 |  |  |  | HR768 (Lo-16bits)
770 | MEAS2:I''02 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
771 |  |  |  | HR770 (Lo-16bits)
772 | MEAS2:I''02 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
773 |  |  |  | HR772 (Lo-16bits)
774 | MEAS2:I''02 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
775 |  |  |  | HR774 (Lo-16bits)
776 | MEAS2:I''02 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
777 |  |  |  | HR776 (Lo-16bits)
778 | MEAS2:I''02 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
779 |  |  |  | HR778 (Lo-16bits)
780 | MEAS2:I''02 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
781 |  |  |  | HR780 (Lo-16bits)
782 | MEAS2:I''02 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
783 |  |  |  | HR782 (Lo-16bits)
784 | MEAS2:I''02 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
785 |  |  |  | HR784 (Lo-16bits)
786 | MEAS2:I''02 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
787 |  |  |  | HR786 (Lo-16bits)
788 | MEAS2:I''02 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
789 |  |  |  | HR788 (Lo-16bits)
790 | MEAS2:I''02 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
791 |  |  |  | HR790 (Lo-16bits)
792 | MEAS2:I''02 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
793 |  |  |  | HR792 (Lo-16bits)
794 | MEAS2:I''02 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
795 |  |  |  | HR794 (Lo-16bits)
796 | MEAS2:I''02 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
797 |  |  |  | HR796 (Lo-16bits)
798 | MEAS3:U1 Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
799 |  |  |  | HR798 (Lo-16bits)
800 | MEAS3:U1 Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
801 |  |  |  | HR800 (Lo-16bits)
802 | MEAS3:U2 Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
803 |  |  |  | HR802 (Lo-16bits)
804 | MEAS3:U2 Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
805 |  |  |  | HR804 (Lo-16bits)
806 | MEAS3:U3 Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
807 |  |  |  | HR806 (Lo-16bits)
808 | MEAS3:U3 Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
809 |  |  |  | HR808 (Lo-16bits)
810 | MEAS3:U4 Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
811 |  |  |  | HR810 (Lo-16bits)
812 | MEAS3:U4 Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
813 |  |  |  | HR812 (Lo-16bits)
814 | MEAS3:U1 Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
815 |  |  |  | HR814 (Lo-16bits)
816 | MEAS3:U1 Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
817 |  |  |  | HR816 (Lo-16bits)
818 | MEAS3:U2 Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
819 |  |  |  | HR818 (Lo-16bits)
820 | MEAS3:U2 Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
821 |  |  |  | HR820 (Lo-16bits)
822 | MEAS3:U3 Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
823 |  |  |  | HR822 (Lo-16bits)
824 | MEAS3:U3 Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
825 |  |  |  | HR824 (Lo-16bits)
826 | MEAS3:U4 Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
827 |  |  |  | HR826 (Lo-16bits)
828 | MEAS3:U4 Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
829 |  |  |  | HR828 (Lo-16bits)
830 | MEAS3:Positive sequence volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
831 |  |  |  | HR830 (Lo-16bits)
832 | MEAS3:Positive sequence volt.sec | R | 2 | FLOAT [0...480] (Hi-16bits)
833 |  |  |  | HR832 (Lo-16bits)
834 | MEAS3:Negative sequence volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
835 |  |  |  | HR834 (Lo-16bits)
836 | MEAS3:Negative sequence volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
837 |  |  |  | HR836 (Lo-16bits)
838 | MEAS3:Zero sequence Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
839 |  |  |  | HR838 (Lo-16bits)
840 | MEAS3:Zero sequence Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
841 |  |  |  | HR840 (Lo-16bits)
842 | MEAS3:U0 Calc.Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
843 |  |  |  | HR842 (Lo-16bits)
844 | MEAS3:U0 Calc.Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
845 |  |  |  | HR844 (Lo-16bits)
846 | MEAS3:U1 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
847 |  |  |  | HR846 (Lo-16bits)
848 | MEAS3:U2 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
849 |  |  |  | HR848 (Lo-16bits)
850 | MEAS3:U3 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
851 |  |  |  | HR850 (Lo-16bits)
852 | MEAS3:U4 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
853 |  |  |  | HR852 (Lo-16bits)
854 | MEAS3:Pos.Seq volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
855 |  |  |  | HR854 (Lo-16bits)
856 | MEAS3:Negative sequence volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
857 |  |  |  | HR856 (Lo-16bits)
858 | MEAS3:Zero sequence volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
859 |  |  |  | HR858 (Lo-16bits)
860 | MEAS3:System volt UL12 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
861 |  |  |  | HR860 (Lo-16bits)
862 | MEAS3:System volt UL12 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
863 |  |  |  | HR862 (Lo-16bits)
864 | MEAS3:System volt UL12 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
865 |  |  |  | HR864 (Lo-16bits)
866 | MEAS3:System volt UL23 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
867 |  |  |  | HR866 (Lo-16bits)
868 | MEAS3:System volt UL23 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
869 |  |  |  | HR868 (Lo-16bits)
870 | MEAS3:System volt UL23 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
871 |  |  |  | HR870 (Lo-16bits)
872 | MEAS3:System volt UL31 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
873 |  |  |  | HR872 (Lo-16bits)
874 | MEAS3:System volt UL31 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
875 |  |  |  | HR874 (Lo-16bits)
876 | MEAS3:System volt UL31 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
877 |  |  |  | HR876 (Lo-16bits)
878 | MEAS3:System volt UL1 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
879 |  |  |  | HR878 (Lo-16bits)
880 | MEAS3:System volt UL1 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
881 |  |  |  | HR880 (Lo-16bits)
882 | MEAS3:System volt UL1 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
883 |  |  |  | HR882 (Lo-16bits)
884 | MEAS3:System volt UL2 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
885 |  |  |  | HR884 (Lo-16bits)
886 | MEAS3:System volt UL2 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
887 |  |  |  | HR886 (Lo-16bits)
888 | MEAS3:System volt UL2 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
889 |  |  |  | HR888 (Lo-16bits)
890 | MEAS3:System volt UL3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
891 |  |  |  | HR890 (Lo-16bits)
892 | MEAS3:System volt UL3 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
893 |  |  |  | HR892 (Lo-16bits)
894 | MEAS3:System volt UL3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
895 |  |  |  | HR894 (Lo-16bits)
896 | MEAS3:System volt U0 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
897 |  |  |  | HR896 (Lo-16bits)
898 | MEAS3:System volt U0 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
899 |  |  |  | HR898 (Lo-16bits)
900 | MEAS3:System volt U0 mag(%) | R | 2 | FLOAT [0...120] (Hi-16bits)
901 |  |  |  | HR900 (Lo-16bits)
902 | MEAS3:System volt U0 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
903 |  |  |  | HR902 (Lo-16bits)
904 | MEAS3:System volt U3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
905 |  |  |  | HR904 (Lo-16bits)
906 | MEAS3:System volt U3 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
907 |  |  |  | HR906 (Lo-16bits)
908 | MEAS3:System volt U3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
909 |  |  |  | HR908 (Lo-16bits)
910 | MEAS3:System volt U4 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
911 |  |  |  | HR910 (Lo-16bits)
912 | MEAS3:System volt U4 mag (kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
913 |  |  |  | HR912 (Lo-16bits)
914 | MEAS3:System volt U4 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
915 |  |  |  | HR914 (Lo-16bits)
916 | MEAS3:System volt UL1 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
917 |  |  |  | HR916 (Lo-16bits)
918 | MEAS3:System volt UL2 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
919 |  |  |  | HR918 (Lo-16bits)
920 | MEAS3:System volt UL3 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
921 |  |  |  | HR920 (Lo-16bits)
922 | MEAS3:U1 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
923 |  |  |  | HR922 (Lo-16bits)
924 | MEAS3:U1 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
925 |  |  |  | HR924 (Lo-16bits)
926 | MEAS3:U1 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
927 |  |  |  | HR926 (Lo-16bits)
928 | MEAS3:U1 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
929 |  |  |  | HR928 (Lo-16bits)
930 | MEAS3:U1 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
931 |  |  |  | HR930 (Lo-16bits)
932 | MEAS3:U1 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
933 |  |  |  | HR932 (Lo-16bits)
934 | MEAS3:U1 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
935 |  |  |  | HR934 (Lo-16bits)
936 | MEAS3:U1 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
937 |  |  |  | HR936 (Lo-16bits)
938 | MEAS3:U1 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
939 |  |  |  | HR938 (Lo-16bits)
940 | MEAS3:U1 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
941 |  |  |  | HR940 (Lo-16bits)
942 | MEAS3:U1 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
943 |  |  |  | HR942 (Lo-16bits)
944 | MEAS3:U1 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
945 |  |  |  | HR944 (Lo-16bits)
946 | MEAS3:U1 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
947 |  |  |  | HR946 (Lo-16bits)
948 | MEAS3:U1 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
949 |  |  |  | HR948 (Lo-16bits)
950 | MEAS3:U1 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
951 |  |  |  | HR950 (Lo-16bits)
952 | MEAS3:U1 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
953 |  |  |  | HR952 (Lo-16bits)
954 | MEAS3:U1 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
955 |  |  |  | HR954 (Lo-16bits)
956 | MEAS3:U1 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
957 |  |  |  | HR956 (Lo-16bits)
958 | MEAS3:U1 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
959 |  |  |  | HR958 (Lo-16bits)
960 | MEAS3:U1 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
961 |  |  |  | HR960 (Lo-16bits)
962 | MEAS3:U1 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
963 |  |  |  | HR962 (Lo-16bits)
964 | MEAS3:U1 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
965 |  |  |  | HR964 (Lo-16bits)
966 | MEAS3:U1 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
967 |  |  |  | HR966 (Lo-16bits)
968 | MEAS3:U1 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
969 |  |  |  | HR968 (Lo-16bits)
970 | MEAS3:U1 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
971 |  |  |  | HR970 (Lo-16bits)
972 | MEAS3:U1 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
973 |  |  |  | HR972 (Lo-16bits)
974 | MEAS3:U1 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
975 |  |  |  | HR974 (Lo-16bits)
976 | MEAS3:U1 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
977 |  |  |  | HR976 (Lo-16bits)
978 | MEAS3:U1 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
979 |  |  |  | HR978 (Lo-16bits)
980 | MEAS3:U1 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
981 |  |  |  | HR980 (Lo-16bits)
982 | MEAS3:U1 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
983 |  |  |  | HR982 (Lo-16bits)
984 | MEAS3:U2 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
985 |  |  |  | HR984 (Lo-16bits)
986 | MEAS3:U2 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
987 |  |  |  | HR986 (Lo-16bits)
988 | MEAS3:U2 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
989 |  |  |  | HR988 (Lo-16bits)
990 | MEAS3:U2 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
991 |  |  |  | HR990 (Lo-16bits)
992 | MEAS3:U2 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
993 |  |  |  | HR992 (Lo-16bits)
994 | MEAS3:U2 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
995 |  |  |  | HR994 (Lo-16bits)
996 | MEAS3:U2 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
997 |  |  |  | HR996 (Lo-16bits)
998 | MEAS3:U2 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
999 |  |  |  | HR998 (Lo-16bits)
1000 | MEAS3:U2 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1001 |  |  |  | HR1000 (Lo-16bits)
1002 | MEAS3:U2 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1003 |  |  |  | HR1002 (Lo-16bits)
1004 | MEAS3:U2 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1005 |  |  |  | HR1004 (Lo-16bits)
1006 | MEAS3:U2 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1007 |  |  |  | HR1006 (Lo-16bits)
1008 | MEAS3:U2 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1009 |  |  |  | HR1008 (Lo-16bits)
1010 | MEAS3:U2 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1011 |  |  |  | HR1010 (Lo-16bits)
1012 | MEAS3:U2 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1013 |  |  |  | HR1012 (Lo-16bits)
1014 | MEAS3:U2 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1015 |  |  |  | HR1014 (Lo-16bits)
1016 | MEAS3:U2 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1017 |  |  |  | HR1016 (Lo-16bits)
1018 | MEAS3:U2 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1019 |  |  |  | HR1018 (Lo-16bits)
1020 | MEAS3:U2 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1021 |  |  |  | HR1020 (Lo-16bits)
1022 | MEAS3:U2 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1023 |  |  |  | HR1022 (Lo-16bits)
1024 | MEAS3:U2 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1025 |  |  |  | HR1024 (Lo-16bits)
1026 | MEAS3:U2 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1027 |  |  |  | HR1026 (Lo-16bits)
1028 | MEAS3:U2 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1029 |  |  |  | HR1028 (Lo-16bits)
1030 | MEAS3:U2 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1031 |  |  |  | HR1030 (Lo-16bits)
1032 | MEAS3:U2 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1033 |  |  |  | HR1032 (Lo-16bits)
1034 | MEAS3:U2 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1035 |  |  |  | HR1034 (Lo-16bits)
1036 | MEAS3:U2 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1037 |  |  |  | HR1036 (Lo-16bits)
1038 | MEAS3:U2 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1039 |  |  |  | HR1038 (Lo-16bits)
1040 | MEAS3:U2 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1041 |  |  |  | HR1040 (Lo-16bits)
1042 | MEAS3:U2 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1043 |  |  |  | HR1042 (Lo-16bits)
1044 | MEAS3:U2 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1045 |  |  |  | HR1044 (Lo-16bits)
1046 | MEAS3:U3 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
1047 |  |  |  | HR1046 (Lo-16bits)
1048 | MEAS3:U3 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1049 |  |  |  | HR1048 (Lo-16bits)
1050 | MEAS3:U3 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1051 |  |  |  | HR1050 (Lo-16bits)
1052 | MEAS3:U3 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1053 |  |  |  | HR1052 (Lo-16bits)
1054 | MEAS3:U3 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1055 |  |  |  | HR1054 (Lo-16bits)
1056 | MEAS3:U3 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1057 |  |  |  | HR1056 (Lo-16bits)
1058 | MEAS3:U3 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1059 |  |  |  | HR1058 (Lo-16bits)
1060 | MEAS3:U3 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1061 |  |  |  | HR1060 (Lo-16bits)
1062 | MEAS3:U3 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1063 |  |  |  | HR1062 (Lo-16bits)
1064 | MEAS3:U3 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1065 |  |  |  | HR1064 (Lo-16bits)
1066 | MEAS3:U3 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1067 |  |  |  | HR1066 (Lo-16bits)
1068 | MEAS3:U3 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1069 |  |  |  | HR1068 (Lo-16bits)
1070 | MEAS3:U3 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1071 |  |  |  | HR1070 (Lo-16bits)
1072 | MEAS3:U3 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1073 |  |  |  | HR1072 (Lo-16bits)
1074 | MEAS3:U3 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1075 |  |  |  | HR1074 (Lo-16bits)
1076 | MEAS3:U3 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1077 |  |  |  | HR1076 (Lo-16bits)
1078 | MEAS3:U3 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1079 |  |  |  | HR1078 (Lo-16bits)
1080 | MEAS3:U3 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1081 |  |  |  | HR1080 (Lo-16bits)
1082 | MEAS3:U3 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1083 |  |  |  | HR1082 (Lo-16bits)
1084 | MEAS3:U3 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1085 |  |  |  | HR1084 (Lo-16bits)
1086 | MEAS3:U3 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1087 |  |  |  | HR1086 (Lo-16bits)
1088 | MEAS3:U3 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1089 |  |  |  | HR1088 (Lo-16bits)
1090 | MEAS3:U3 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1091 |  |  |  | HR1090 (Lo-16bits)
1092 | MEAS3:U3 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1093 |  |  |  | HR1092 (Lo-16bits)
1094 | MEAS3:U3 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1095 |  |  |  | HR1094 (Lo-16bits)
1096 | MEAS3:U3 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1097 |  |  |  | HR1096 (Lo-16bits)
1098 | MEAS3:U3 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1099 |  |  |  | HR1098 (Lo-16bits)
1100 | MEAS3:U3 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1101 |  |  |  | HR1100 (Lo-16bits)
1102 | MEAS3:U3 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1103 |  |  |  | HR1102 (Lo-16bits)
1104 | MEAS3:U3 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1105 |  |  |  | HR1104 (Lo-16bits)
1106 | MEAS3:U3 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1107 |  |  |  | HR1106 (Lo-16bits)
1108 | MEAS3:U4 fundamental | R | 2 | FLOAT [0...100000] (Hi-16bits)
1109 |  |  |  | HR1108 (Lo-16bits)
1110 | MEAS3:U4 2nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1111 |  |  |  | HR1110 (Lo-16bits)
1112 | MEAS3:U4 3rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1113 |  |  |  | HR1112 (Lo-16bits)
1114 | MEAS3:U4 4th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1115 |  |  |  | HR1114 (Lo-16bits)
1116 | MEAS3:U4 5th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1117 |  |  |  | HR1116 (Lo-16bits)
1118 | MEAS3:U4 6th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1119 |  |  |  | HR1118 (Lo-16bits)
1120 | MEAS3:U4 7th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1121 |  |  |  | HR1120 (Lo-16bits)
1122 | MEAS3:U4 8th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1123 |  |  |  | HR1122 (Lo-16bits)
1124 | MEAS3:U4 9th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1125 |  |  |  | HR1124 (Lo-16bits)
1126 | MEAS3:U4 10th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1127 |  |  |  | HR1126 (Lo-16bits)
1128 | MEAS3:U4 11th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1129 |  |  |  | HR1128 (Lo-16bits)
1130 | MEAS3:U4 12th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1131 |  |  |  | HR1130 (Lo-16bits)
1132 | MEAS3:U4 13th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1133 |  |  |  | HR1132 (Lo-16bits)
1134 | MEAS3:U4 14th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1135 |  |  |  | HR1134 (Lo-16bits)
1136 | MEAS3:U4 15th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1137 |  |  |  | HR1136 (Lo-16bits)
1138 | MEAS3:U4 16th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1139 |  |  |  | HR1138 (Lo-16bits)
1140 | MEAS3:U4 17th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1141 |  |  |  | HR1140 (Lo-16bits)
1142 | MEAS3:U4 18th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1143 |  |  |  | HR1142 (Lo-16bits)
1144 | MEAS3:U4 19th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1145 |  |  |  | HR1144 (Lo-16bits)
1146 | MEAS3:U4 20th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1147 |  |  |  | HR1146 (Lo-16bits)
1148 | MEAS3:U4 21st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1149 |  |  |  | HR1148 (Lo-16bits)
1150 | MEAS3:U4 22nd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1151 |  |  |  | HR1150 (Lo-16bits)
1152 | MEAS3:U4 23rd harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1153 |  |  |  | HR1152 (Lo-16bits)
1154 | MEAS3:U4 24th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1155 |  |  |  | HR1154 (Lo-16bits)
1156 | MEAS3:U4 25th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1157 |  |  |  | HR1156 (Lo-16bits)
1158 | MEAS3:U4 26th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1159 |  |  |  | HR1158 (Lo-16bits)
1160 | MEAS3:U4 27th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1161 |  |  |  | HR1160 (Lo-16bits)
1162 | MEAS3:U4 28th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1163 |  |  |  | HR1162 (Lo-16bits)
1164 | MEAS3:U4 29th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1165 |  |  |  | HR1164 (Lo-16bits)
1166 | MEAS3:U4 30th harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1167 |  |  |  | HR1166 (Lo-16bits)
1168 | MEAS3:U4 31st harmonic | R | 2 | FLOAT [0...100000] (Hi-16bits)
1169 |  |  |  | HR1168 (Lo-16bits)
1170 | POW1:Export Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1171 |  |  |  | HR1170 (Lo-16bits)
1172 | POW1:Export Active Energy (P) kWh | R(W) | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1173 |  |  |  | HR1172 (Lo-16bits)
1174 | POW1:Import Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1175 |  |  |  | HR1174 (Lo-16bits)
1176 | POW1:Import Active Energy (P) kWh | R(W) | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1177 |  |  |  | HR1176 (Lo-16bits)
1178 | POW1:Active Energy (P) Export/Import balance MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1179 |  |  |  | HR1178 (Lo-16bits)
1180 | POW1:Active Energy (P) Export/Import balance kWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1181 |  |  |  | HR1180 (Lo-16bits)
1182 | POW1:Imported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1183 |  |  |  | HR1182 (Lo-16bits)
1184 | POW1:Imported (Q) while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1185 |  |  |  | HR1184 (Lo-16bits)
1186 | POW1:Imported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1187 |  |  |  | HR1186 (Lo-16bits)
1188 | POW1:Imported (Q) while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1189 |  |  |  | HR1188 (Lo-16bits)
1190 | POW1:Reactive Energy (Q) balance while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1191 |  |  |  | HR1190 (Lo-16bits)
1192 | POW1:Reactive Energy (Q) balance while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1193 |  |  |  | HR1192 (Lo-16bits)
1194 | POW1:Exported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1195 |  |  |  | HR1194 (Lo-16bits)
1196 | POW1:Exported (Q) while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1197 |  |  |  | HR1196 (Lo-16bits)
1198 | POW1:Exported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1199 |  |  |  | HR1198 (Lo-16bits)
1200 | POW1:Exported (Q) while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1201 |  |  |  | HR1200 (Lo-16bits)
1202 | POW1:Reactive Energy (Q) balance while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1203 |  |  |  | HR1202 (Lo-16bits)
1204 | POW1:Reactive Energy (Q) balance while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1205 |  |  |  | HR1204 (Lo-16bits)
1206 | POW1:Reset 3ph energies | R(W) | 1 | 0=-;1=Reset
1207 | POW1:POW1 3PH Apparent power (S) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1208 |  |  |  | HR1207 (Lo-16bits)
1209 | POW1:POW1 3PH Apparent power (S MVA) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1210 |  |  |  | HR1209 (Lo-16bits)
1211 | POW1:POW1 3PH Active power (P) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1212 |  |  |  | HR1211 (Lo-16bits)
1213 | POW1:POW1 3PH Active power (P MW) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1214 |  |  |  | HR1213 (Lo-16bits)
1215 | POW1:POW1 3PH Reactive power (Q) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1216 |  |  |  | HR1215 (Lo-16bits)
1217 | POW1:POW1 3PH Reactive power (QMVar) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1218 |  |  |  | HR1217 (Lo-16bits)
1219 | POW1:POW1 3PH Tan(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1220 |  |  |  | HR1219 (Lo-16bits)
1221 | POW1:POW1 3PH Cos(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1222 |  |  |  | HR1221 (Lo-16bits)
1223 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1224 |  |  |  | HR1223 (Lo-16bits)
1225 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1226 |  |  |  | HR1225 (Lo-16bits)
1227 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1228 |  |  |  | HR1227 (Lo-16bits)
1229 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1230 |  |  |  | HR1229 (Lo-16bits)
1231 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1232 |  |  |  | HR1231 (Lo-16bits)
1233 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1234 |  |  |  | HR1233 (Lo-16bits)
1235 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1236 |  |  |  | HR1235 (Lo-16bits)
1237 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1238 |  |  |  | HR1237 (Lo-16bits)
1239 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1240 |  |  |  | HR1239 (Lo-16bits)
1241 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1242 |  |  |  | HR1241 (Lo-16bits)
1243 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1244 |  |  |  | HR1243 (Lo-16bits)
1245 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1246 |  |  |  | HR1245 (Lo-16bits)
1247 | FREQS:f atm. Protections (when not measurable returns to nominal) | R | 2 | FLOAT [0...75] (Hi-16bits)
1248 |  |  |  | HR1247 (Lo-16bits)
1249 | DIGI:DIs | R | 2 | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32 (Hi-16bits)
1250 |  |  |  | HR1249 (Lo-16bits)
1251 | DIGI:DIs | R | 2 | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51;19b=DI52;20b=DI53;21b=DI54;22b=DI55;23b=DI56;24b=DI57;25b=DI58;26b=DI59;27b=DI60;28b=DI61;29b=DI62;30b=DI63;31b=DI64 (Hi-16bits)
1252 |  |  |  | HR1251 (Lo-16bits)
1253 | RELE:Outputs status | R | 2 | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15;15b=O16;16b=O17;17b=O18;18b=O19;19b=O20;20b=O21;21b=O22;22b=O23;23b=O24;24b=O25;25b=O26;26b=O27;27b=O28;28b=O29;29b=O30;30b=O31;31b=O32 (Hi-16bits)
1254 |  |  |  | HR1253 (Lo-16bits)
1255 | SGS:Active setting group | R | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
1256 | SGS:Force setting group | R(W) | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1257 | SGS:Force setting group change | R(W) | 1 | 0=Disabled;1=Enabled
1258 | SGS:Used setting groups | R(W) | 1 | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
1259 | SGS:Remote setting group change | R(W) | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1260 | LOGIC:Reset Latches | RW | 1 | 0=-;1=Reset
1261 | NOC1:I> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1262 | NOC2:I>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1263 | NOC3:I>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1264 | NOC4:I>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1265 | DOC1:Idir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1266 | DOC2:Idir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1267 | DOC3:Idir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1268 | DOC4:Idir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1269 | NEF1:I0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1270 | NEF1:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
1271 | NEF2:I0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1272 | NEF2:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
1273 | NEF3:I0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1274 | NEF3:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
1275 | NEF4:I0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1276 | NEF4:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
1277 | DEF1:I0dir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
1278 | DEF1:U0> measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
1279 | DEF1:I0 direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
1280 | DEF2:I0dir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
1281 | DEF2:U0>> measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
1282 | DEF2:I0 direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
1283 | DEF3:I0dir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
1284 | DEF3:U0>>> measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
1285 | DEF3:I0 direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
1286 | DEF4:I0dir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
1287 | DEF4:U0>>>> measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
1288 | DEF4:I0 direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
1289 | IEF1:I0Int> condition | R | 1 | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
1290 | IEF1:U0> measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
1291 | CUB1:I2> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1292 | CUB2:I2>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1293 | CUB3:I2>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1294 | CUB4:I2>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1295 | HOC1:Ih> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1296 | HOC1:L1 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1297 |  |  |  | HR1296 (Lo-16bits)
1298 | HOC1:L1 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1299 |  |  |  | HR1298 (Lo-16bits)
1300 | HOC1:L2 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1301 |  |  |  | HR1300 (Lo-16bits)
1302 | HOC1:L2 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1303 |  |  |  | HR1302 (Lo-16bits)
1304 | HOC1:L3 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1305 |  |  |  | HR1304 (Lo-16bits)
1306 | HOC1:L3 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1307 |  |  |  | HR1306 (Lo-16bits)
1308 | HOC1:I01 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1309 |  |  |  | HR1308 (Lo-16bits)
1310 | HOC1:I01 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1311 |  |  |  | HR1310 (Lo-16bits)
1312 | HOC1:I02 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1313 |  |  |  | HR1312 (Lo-16bits)
1314 | HOC1:I02 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1315 |  |  |  | HR1314 (Lo-16bits)
1316 | HOC2:Ih>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1317 | HOC2:L1 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1318 |  |  |  | HR1317 (Lo-16bits)
1319 | HOC2:L1 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1320 |  |  |  | HR1319 (Lo-16bits)
1321 | HOC2:L2 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1322 |  |  |  | HR1321 (Lo-16bits)
1323 | HOC2:L2 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1324 |  |  |  | HR1323 (Lo-16bits)
1325 | HOC2:L3 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1326 |  |  |  | HR1325 (Lo-16bits)
1327 | HOC2:L3 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1328 |  |  |  | HR1327 (Lo-16bits)
1329 | HOC2:I01 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1330 |  |  |  | HR1329 (Lo-16bits)
1331 | HOC2:I01 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1332 |  |  |  | HR1331 (Lo-16bits)
1333 | HOC2:I02 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1334 |  |  |  | HR1333 (Lo-16bits)
1335 | HOC2:I02 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1336 |  |  |  | HR1335 (Lo-16bits)
1337 | HOC3:Ih>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1338 | HOC3:L1 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1339 |  |  |  | HR1338 (Lo-16bits)
1340 | HOC3:L1 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1341 |  |  |  | HR1340 (Lo-16bits)
1342 | HOC3:L2 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1343 |  |  |  | HR1342 (Lo-16bits)
1344 | HOC3:L2 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1345 |  |  |  | HR1344 (Lo-16bits)
1346 | HOC3:L3 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1347 |  |  |  | HR1346 (Lo-16bits)
1348 | HOC3:L3 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1349 |  |  |  | HR1348 (Lo-16bits)
1350 | HOC3:I01 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1351 |  |  |  | HR1350 (Lo-16bits)
1352 | HOC3:I01 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1353 |  |  |  | HR1352 (Lo-16bits)
1354 | HOC3:I02 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1355 |  |  |  | HR1354 (Lo-16bits)
1356 | HOC3:I02 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1357 |  |  |  | HR1356 (Lo-16bits)
1358 | HOC4:Ih>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1359 | HOC4:L1 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1360 |  |  |  | HR1359 (Lo-16bits)
1361 | HOC4:L1 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1362 |  |  |  | HR1361 (Lo-16bits)
1363 | HOC4:L2 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1364 |  |  |  | HR1363 (Lo-16bits)
1365 | HOC4:L2 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1366 |  |  |  | HR1365 (Lo-16bits)
1367 | HOC4:L3 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1368 |  |  |  | HR1367 (Lo-16bits)
1369 | HOC4:L3 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1370 |  |  |  | HR1369 (Lo-16bits)
1371 | HOC4:I01 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1372 |  |  |  | HR1371 (Lo-16bits)
1373 | HOC4:I01 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1374 |  |  |  | HR1373 (Lo-16bits)
1375 | HOC4:I02 harmonic (p.u.) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1376 |  |  |  | HR1375 (Lo-16bits)
1377 | HOC4:I02 harmonic (%) | R | 2 | FLOAT [0...100000] (Hi-16bits)
1378 |  |  |  | HR1377 (Lo-16bits)
1379 | CLP1:CLP condition | R | 1 | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
1380 | CBF1:CBFP condition | R | 1 | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
1381 | TRF1:Transformer is now | R | 1 | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
1382 | DIF1:Idx> condition | R | 2 | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On (Hi-16bits)
1383 |  |  |  | HR1382 (Lo-16bits)
1384 | DIF1:L1 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
1385 | DIF1:L2 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
1386 | DIF1:L3 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
1387 | REF1:I0d> condition | R | 1 | 0=Normal;1=Trip;2=Blocked
1388 | TOLT1:TT> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
1389 | TOLT1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
1390 | TOLT1:Temp C or F deg | R(W) | 1 | 0=C;1=F
1391 | TOLT1:Ambient Temp Sel | R(W) | 1 | 0=Manual Set;1=RTD Meas
1392 | TOLT1:RTD Sensor | R | 1 | 0=Invalid;1=OK
1393 | TOLF1:TF> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
1394 | TOLF1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
1395 | TOLF1:Temp C or F deg | R(W) | 1 | 0=C;1=F
1396 | TOLF1:Ambient Temp Sel | R(W) | 1 | 0=Manual Set;1=RTD Meas
1397 | TOLF1:RTD Sensor | R(W) | 1 | 0=Invalid;1=OK
1398 | TOLF1:Set or Estimate tau (t const) | R(W) | 1 | 0=Set;1=Estimate
1399 | MST1:Motor is now | R | 1 | 0=Stopped;1=Starting;2=Running;3=Stalled
1400 | TOLM1:TM> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
1401 | TOLM1:Motor status | R | 1 | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
1402 | TOLM1:Temp C or F deg | R(W) | 1 | 0=C;1=F
1403 | TOLM1:NPS Biasing in use | R(W) | 1 | 0=No NPS biasing;1=NPS Biasing in use
1404 | TOLM1:Time constants | R(W) | 1 | 0=Single;1=Multiple
1405 | TOLM1:Estimate Short TC and timings | R(W) | 1 | 0=Set manually;1=Estimate (on-line)
1406 | TOLM1:T const dyn. balancing | R(W) | 1 | 0=Fixed;1=Dynamic
1407 | TOLM1:Dev.Temp (tmax) | R(W) | 1 | 0=A;1=B;2=F;3=H;4=Manual set
1408 | TOLM1:Amb. T Selection | R(W) | 1 | 0=Manual set;1=RTD
1409 | TOLM1:RTD Sensor | R | 1 | 0=Invalid;1=OK
1410 | LCR1:ISt> condition | R | 1 | 0=Normal;1=Start;2=Set time Trip;3=M cap Trip;4=Blocked
1411 | FSP1:N> condition | R | 1 | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
1412 | NUC1:I< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1413 | MJP1:Im> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1414 | OV1:U> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1415 | OV2:U>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1416 | OV3:U>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1417 | OV4:U>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1418 | UV1:U< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On;5=Block input active
1419 | UV2:U<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On;5=Block input active
1420 | UV3:U<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On;5=Block input active
1421 | UV4:U<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On;5=Block input active
1422 | NOV1:U0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1423 | NOV1:U0> measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
1424 | NOV2:U0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1425 | NOV2:U0>> measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
1426 | NOV3:U0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1427 | NOV3:U0>>> measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
1428 | NOV4:U0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1429 | NOV4:U0>>>> measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
1430 | VUB1:U1/2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1431 | VUB2:U1/2 >>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1432 | VUB3:U1/2 >>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1433 | VUB4:U1/2 >>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1434 | FRQC1:f> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1435 | FRQC1:f>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1436 | FRQC1:f>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1437 | FRQC1:f>>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1438 | FRQC1:f< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1439 | FRQC1:f<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1440 | FRQC1:f<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1441 | FRQC1:f<<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1442 | FRQV1:f> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1443 | FRQV1:f>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1444 | FRQV1:f>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1445 | FRQV1:f>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1446 | FRQV1:f< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1447 | FRQV1:f<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1448 | FRQV1:f<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1449 | FRQV1:f<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Block input active
1450 | DFT1:df/dt >/< (1) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1451 | DFT1:df/dt >/< (2) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1452 | DFT1:df/dt >/< (3) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1453 | DFT1:df/dt >/< (4) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1454 | DFT1:df/dt >/< (5) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1455 | DFT1:df/dt >/< (6) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1456 | DFT1:df/dt >/< (7) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1457 | DFT1:df/dt >/< (8) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1458 | GST1:Generator is now | R | 1 | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
1459 | OPW1:P> condition (OBSOLETE) | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1460 | UPW1:P< condition (OBSOLETE) | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1461 | RPW1:Prev> condition (OBSOLETE) | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1462 | SEF1:U03rd< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1463 | SEF1:U03rd< measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
1464 | UEX1:Q< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1465 | UIM1:Z< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1466 | VOC1:Iv> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1467 | VOC1:Voltage measurement | R | 1 | 0=Invalid U1 not avail.;1=Ok
1468 | VHZ1:V/Hz(1) > condition | R | 1 | 0=Normal;1=Start;;2=Alarm;3=Trip;4=Blocked
1469 | UPF1:PF< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
1470 | ARC1:I/I0 Arc> condition | R | 2 | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked (Hi-16bits)
1471 |  |  |  | HR1470 (Lo-16bits)
1472 | CTS1:CTS1 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
1473 | CTS2:CTS2 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
1474 | VTS1:VTS condition | R | 1 | 0=Normal;1=Start;2=VTLinefail;3=VTBusfail;4=Blocked
1475 | VTS1:Bus voltages | R | 1 | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
1476 | FLX1:Fault locator condition | R | 1 | 0=Idle;1=Triggered;2=Calc ready
1477 | THD1:THD condition | R | 1 | 0=Normal;1=Start;2=Alarm;3=Blocked
1478 | CBW1:CBW condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On
1479 | NJK1:U0> RECL condition | R | 1 | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
1480 | SOF1:SOTF condition | R | 1 | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
1481 | SYN1:SYN1 Condition | R | 2 | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok;7b=SYN1 block input active (Hi-16bits)
1482 |  |  |  | HR1481 (Lo-16bits)
1483 | SYN1:SYN2 Condition | R | 2 | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok;7b=SYN2 block input active (Hi-16bits)
1484 |  |  |  | HR1483 (Lo-16bits)
1485 | SYN1:SYN3 Condition | R | 2 | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok;7b=SYN3 block input active (Hi-16bits)
1486 |  |  |  | HR1485 (Lo-16bits)
1487 | OBJ1:Object1 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1488 | OBJ2:Object2 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1489 | OBJ3:Object3 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1490 | OBJ4:Object4 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1491 | OBJ5:Object5 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1492 | CIN1:Ind.1 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1493 | CIN2:Ind.2 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1494 | CIN3:Ind.3 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1495 | CIN4:Ind.4 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1496 | CIN5:Ind.5 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1497 | AR1:AR status | R | 2 | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Gen. reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Shot reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear (Hi-16bits)
1498 |  |  |  | HR1497 (Lo-16bits)
1499 | AR1:Timer active | R | 1 | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
1500 | VRG1:Vreg settings condition | R | 2 | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok (Hi-16bits)
1501 |  |  |  | HR1500 (Lo-16bits)
1502 | VRG1:Vreg condition | R | 2 | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on (Hi-16bits)
1503 |  |  |  | HR1502 (Lo-16bits)
1504 | VRG1:Vreg timer active | R | 1 | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
1505 | VRG1:Voltage measurement condition | R | 1 | 0=Not configured;1=System U12;2=System U23;3=System U31;4=VT4 meas U12;5=VT4 meas U23;6=VT4 meas U31;7=VT4 conf not ok
1506 | EMON1:I> (50) Monitor condition | R | 1 | 0=Normal;1=FLTdetected
1507 | EMON1:I0> (50N) Monitor condition | R | 1 | 0=Normal;1=FLTdetected
1508 | EMON1:Idir> (67) Monitor condition | R | 1 | 0=Normal;1=FLTdetected
1509 | EMON1:I0dir> (67N) Monitor condition | R | 1 | 0=Normal;1=FLTdetected
1510 | EMON1:I0Int> (67NT) Monitor condition | R | 1 | 0=Normal;1=FLTFW;2=FLTREV
1511 | EMON1:U< (27) Monitor condition | R | 1 | 0=Normal;1=Undervoltage;2=Novoltage
1512 | EMON1:U0> (59N) Monitor condition | R | 1 | 0=Normal;1=FLTdetected
1513 | EMON1:FL (21FL) Monitor condition | R | 1 | 0=Normal;1=FLTdetected
1514 | MEAS1:Meas1 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
1515 |  |  |  | HR1514 (Lo-16bits)
1516 | DIF1:REFHV> condition | R | 2 | 0b=HV REF Blocked;1b=HV REF Trip (Hi-16bits)
1517 |  |  |  | HR1516 (Lo-16bits)
1518 | DIF1:REFLV> condition | R | 2 | 0b=LV REF Blocked;1b=LV REF Trip (Hi-16bits)
1519 |  |  |  | HR1518 (Lo-16bits)
1520 | ALARM:Alarms 1-32 | R | 2 | 0b=A1;1b=A2;2b=A3;3b=A4;4b=A5;5b=A6;6b=A7;7b=A8;8b=A9;9b=A10;10b=A11;11b=A12;12b=A13;13b=A14;14b=A15;15b=A16;16b=A17;17b=A18;18b=A19;19b=A20;20b=A21;21b=A22;22b=A23;23b=A24;24b=A25;25b=A26;26b=A27;27b=A28;28b=A29;29b=A30;30b=A31;31b=A32 (Hi-16bits)
1521 |  |  |  | HR1520 (Lo-16bits)
1522 | ALARM:Alarms 33-64 | R | 2 | 0b=A33;1b=A34;2b=A35;3b=A36;4b=A37;5b=A38;6b=A39;7b=A40;8b=A41;9b=A42;10b=A43;11b=A44;12b=A45;13b=A46;14b=A47;15b=A48;16b=A49;17b=A50;18b=A51;19b=A52;20b=A53;21b=A54;22b=A55;23b=A56;24b=A57;25b=A58;26b=A59;27b=A60;28b=A61;29b=A62;30b=A63;31b=A64 (Hi-16bits)
1523 |  |  |  | HR1522 (Lo-16bits)
1524 | DIAG:Configuration changed | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1525 |  |  |  | HR1524 (Lo-16bits)
1526 | RTDIN:S1 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1527 |  |  |  | HR1526 (Lo-16bits)
1528 | RTDIN:S2 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1529 |  |  |  | HR1528 (Lo-16bits)
1530 | RTDIN:S3 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1531 |  |  |  | HR1530 (Lo-16bits)
1532 | RTDIN:S4 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1533 |  |  |  | HR1532 (Lo-16bits)
1534 | RTDIN:S5 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1535 |  |  |  | HR1534 (Lo-16bits)
1536 | RTDIN:S6 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1537 |  |  |  | HR1536 (Lo-16bits)
1538 | RTDIN:S7 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1539 |  |  |  | HR1538 (Lo-16bits)
1540 | RTDIN:S7 Measurement mA | R | 2 | FLOAT [0...20] (Hi-16bits)
1541 |  |  |  | HR1540 (Lo-16bits)
1542 | RTDIN:S8 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1543 |  |  |  | HR1542 (Lo-16bits)
1544 | RTDIN:S8 Measurement mA | R | 2 | FLOAT [0...20] (Hi-16bits)
1545 |  |  |  | HR1544 (Lo-16bits)
1546 | RTDIN:S9 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1547 |  |  |  | HR1546 (Lo-16bits)
1548 | RTDIN:S10 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1549 |  |  |  | HR1548 (Lo-16bits)
1550 | RTDIN:S11 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1551 |  |  |  | HR1550 (Lo-16bits)
1552 | RTDIN:S12 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1553 |  |  |  | HR1552 (Lo-16bits)
1554 | RTDIN:S13 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1555 |  |  |  | HR1554 (Lo-16bits)
1556 | RTDIN:S14 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1557 |  |  |  | HR1556 (Lo-16bits)
1558 | RTDIN:S15 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1559 |  |  |  | HR1558 (Lo-16bits)
1560 | RTDIN:S15 Measurement mA | R | 2 | FLOAT [0...20] (Hi-16bits)
1561 |  |  |  | HR1560 (Lo-16bits)
1562 | RTDIN:S16 Measurement(Raw) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1563 |  |  |  | HR1562 (Lo-16bits)
1564 | RTDIN:S16 Measurement mA | R | 2 | FLOAT [0...20] (Hi-16bits)
1565 |  |  |  | HR1564 (Lo-16bits)
1566 | RTD1:S1 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1567 |  |  |  | HR1566 (Lo-16bits)
1568 | RTD1:S2 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1569 |  |  |  | HR1568 (Lo-16bits)
1570 | RTD1:S3 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1571 |  |  |  | HR1570 (Lo-16bits)
1572 | RTD1:S4 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1573 |  |  |  | HR1572 (Lo-16bits)
1574 | RTD1:S5 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1575 |  |  |  | HR1574 (Lo-16bits)
1576 | RTD1:S6 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1577 |  |  |  | HR1576 (Lo-16bits)
1578 | RTD1:S7 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1579 |  |  |  | HR1578 (Lo-16bits)
1580 | RTD1:S8 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1581 |  |  |  | HR1580 (Lo-16bits)
1582 | RTD1:S9 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1583 |  |  |  | HR1582 (Lo-16bits)
1584 | RTD1:S10 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1585 |  |  |  | HR1584 (Lo-16bits)
1586 | RTD1:S11 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1587 |  |  |  | HR1586 (Lo-16bits)
1588 | RTD1:S12 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1589 |  |  |  | HR1588 (Lo-16bits)
1590 | RTD1:S1 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1591 |  |  |  | HR1590 (Lo-16bits)
1592 | RTD1:S1 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1593 |  |  |  | HR1592 (Lo-16bits)
1594 | RTD1:S2 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1595 |  |  |  | HR1594 (Lo-16bits)
1596 | RTD1:S2 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1597 |  |  |  | HR1596 (Lo-16bits)
1598 | RTD1:S3 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1599 |  |  |  | HR1598 (Lo-16bits)
1600 | RTD1:S3 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1601 |  |  |  | HR1600 (Lo-16bits)
1602 | RTD1:S4 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1603 |  |  |  | HR1602 (Lo-16bits)
1604 | RTD1:S4 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1605 |  |  |  | HR1604 (Lo-16bits)
1606 | RTD1:S5 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1607 |  |  |  | HR1606 (Lo-16bits)
1608 | RTD1:S5 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1609 |  |  |  | HR1608 (Lo-16bits)
1610 | RTD1:S6 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1611 |  |  |  | HR1610 (Lo-16bits)
1612 | RTD1:S6 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1613 |  |  |  | HR1612 (Lo-16bits)
1614 | RTD1:S7 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1615 |  |  |  | HR1614 (Lo-16bits)
1616 | RTD1:S7 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1617 |  |  |  | HR1616 (Lo-16bits)
1618 | RTD1:S8 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1619 |  |  |  | HR1618 (Lo-16bits)
1620 | RTD1:S8 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1621 |  |  |  | HR1620 (Lo-16bits)
1622 | RTD1:S9 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1623 |  |  |  | HR1622 (Lo-16bits)
1624 | RTD1:S9 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1625 |  |  |  | HR1624 (Lo-16bits)
1626 | RTD1:S10 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1627 |  |  |  | HR1626 (Lo-16bits)
1628 | RTD1:S10 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1629 |  |  |  | HR1628 (Lo-16bits)
1630 | RTD1:S11 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1631 |  |  |  | HR1630 (Lo-16bits)
1632 | RTD1:S11 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1633 |  |  |  | HR1632 (Lo-16bits)
1634 | RTD1:S12 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1635 |  |  |  | HR1634 (Lo-16bits)
1636 | VHZ1:V/Hz(2) > condition | R | 1 | 0=Normal;1=Start;;2=Alarm;3=Trip;4=Blocked
1637 | RTD1:S12 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1638 |  |  |  | HR1637 (Lo-16bits)
1639 | UIM2:Z<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1640 | RTD1:S1 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1641 |  |  |  | HR1640 (Lo-16bits)
1642 | RTD1:S2 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1643 |  |  |  | HR1642 (Lo-16bits)
1644 | RTD1:S3 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1645 |  |  |  | HR1644 (Lo-16bits)
1646 | RTD1:S4 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1647 |  |  |  | HR1646 (Lo-16bits)
1648 | RTD1:S5 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1649 |  |  |  | HR1648 (Lo-16bits)
1650 | RTD1:S6 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1651 |  |  |  | HR1650 (Lo-16bits)
1652 | RTD1:S7 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1653 |  |  |  | HR1652 (Lo-16bits)
1654 | RTD1:S8 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1655 |  |  |  | HR1654 (Lo-16bits)
1656 | RTD1:S9 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1657 |  |  |  | HR1656 (Lo-16bits)
1658 | RTD1:S10 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1659 |  |  |  | HR1658 (Lo-16bits)
1660 | RTD1:S11 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1661 |  |  |  | HR1660 (Lo-16bits)
1662 | RTD1:S12 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1663 |  |  |  | HR1662 (Lo-16bits)
1664 | MBIO:MBIO ModA Ch1 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1665 |  |  |  | HR1664 (Lo-16bits)
1666 | MBIO:MBIO ModA Ch2 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1667 |  |  |  | HR1666 (Lo-16bits)
1668 | MBIO:MBIO ModA Ch3 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1669 |  |  |  | HR1668 (Lo-16bits)
1670 | MBIO:MBIO ModA Ch4 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1671 |  |  |  | HR1670 (Lo-16bits)
1672 | MBIO:MBIO ModA Ch5 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1673 |  |  |  | HR1672 (Lo-16bits)
1674 | MBIO:MBIO ModA Ch6 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1675 |  |  |  | HR1674 (Lo-16bits)
1676 | MBIO:MBIO ModA Ch7 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1677 |  |  |  | HR1676 (Lo-16bits)
1678 | MBIO:MBIO ModA Ch8 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1679 |  |  |  | HR1678 (Lo-16bits)
1680 | MBIO:MBIO ModB Ch1 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1681 |  |  |  | HR1680 (Lo-16bits)
1682 | MBIO:MBIO ModB Ch2 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1683 |  |  |  | HR1682 (Lo-16bits)
1684 | MBIO:MBIO ModB Ch3 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1685 |  |  |  | HR1684 (Lo-16bits)
1686 | MBIO:MBIO ModB Ch4 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1687 |  |  |  | HR1686 (Lo-16bits)
1688 | MBIO:MBIO ModB Ch5 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1689 |  |  |  | HR1688 (Lo-16bits)
1690 | MBIO:MBIO ModB Ch6 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1691 |  |  |  | HR1690 (Lo-16bits)
1692 | MBIO:MBIO ModB Ch7 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1693 |  |  |  | HR1692 (Lo-16bits)
1694 | MBIO:MBIO ModB Ch8 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1695 |  |  |  | HR1694 (Lo-16bits)
1696 | MBIO:MBIO ModC Ch1 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1697 |  |  |  | HR1696 (Lo-16bits)
1698 | MBIO:MBIO ModC Ch2 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1699 |  |  |  | HR1698 (Lo-16bits)
1700 | MBIO:MBIO ModC Ch3 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1701 |  |  |  | HR1700 (Lo-16bits)
1702 | MBIO:MBIO ModC Ch4 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1703 |  |  |  | HR1702 (Lo-16bits)
1704 | MBIO:MBIO ModC Ch5 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1705 |  |  |  | HR1704 (Lo-16bits)
1706 | MBIO:MBIO ModC Ch6 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1707 |  |  |  | HR1706 (Lo-16bits)
1708 | MBIO:MBIO ModC Ch7 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1709 |  |  |  | HR1708 (Lo-16bits)
1710 | MBIO:MBIO ModC Ch8 Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1711 |  |  |  | HR1710 (Lo-16bits)
1712 | OBJ6:Object6 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1713 | OBJ7:Object7 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1714 | OBJ8:Object8 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1715 | OBJ9:Object9 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1716 | OBJ10:Object10 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
1717 | VRG1:Voltage now | R | 2 | FLOAT [0...140] (Hi-16bits)
1718 |  |  |  | HR1717 (Lo-16bits)
1719 | VRG1:Voltage difference to set target | R | 2 | FLOAT [-100...140] (Hi-16bits)
1720 |  |  |  | HR1719 (Lo-16bits)
1721 | VRG1:Tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
1722 |  |  |  | HR1721 (Lo-16bits)
1723 | VRG1:Absolute tap location | R | 2 | FLOAT [0...50] (Hi-16bits)
1724 |  |  |  | HR1723 (Lo-16bits)
1725 | VRG1:Control mode | R | 1 | 0=Auto;1=Manual (loc&rem)
1726 | VRG1:Remote tap control input | R(W) | 1 | 0=Stop;1=Lower;2=Higher
1727 | VJP1:Vector jump <DELTA><alpha> > condition | R | 1 | 0=Normal;1=Blocked;2=Trip;3=Alarm
1728 | LOGIC1:Logic out 1-32 | R(W) | 2 | UINT32 [0...4294967295] (Hi-16bits)
1729 |  |  |  | HR1728 (Lo-16bits)
1730 | PGS1:PS1 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1731 | VJP1:Selected voltage measurement | R | 1 | 0=Selection Ok;1=Selection not available
1732 | PGS1:PS2 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1733 | PGS1:PS3 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1734 | PGS1:PS4 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1735 | PGS1:PS5 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1736 | PGS1:PS6 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1737 | PGS1:PS7 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1738 | PGS1:PS8 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1739 | PGS1:PS9 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1740 | PGS1:PS10 >/< Condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1741 | ASC1:Curve1 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1742 |  |  |  | HR1741 (Lo-16bits)
1743 | ASC1:Curve1 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1744 |  |  |  | HR1743 (Lo-16bits)
1745 | ASC1:Curve2 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1746 |  |  |  | HR1745 (Lo-16bits)
1747 | ASC1:Curve2 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1748 |  |  |  | HR1747 (Lo-16bits)
1749 | ASC1:Curve3 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1750 |  |  |  | HR1749 (Lo-16bits)
1751 | ASC1:Curve3 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1752 |  |  |  | HR1751 (Lo-16bits)
1753 | ASC1:Curve4 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1754 |  |  |  | HR1753 (Lo-16bits)
1755 | ASC1:Curve4 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1756 |  |  |  | HR1755 (Lo-16bits)
1757 | GMAG:Command AVR (remote) | R(W) | 1 | 0=Off;1=On
1758 | GMAG:Command FCR (remote) | R(W) | 1 | 0=Off;1=On
1759 | GMAG:Command MVAR (remote) | R(W) | 1 | 0=Off;1=On
1760 | GMAG:Command PF (remote) | R(W) | 1 | 0=Off;1=On
1761 | GMAG:Unload Q (remote) | R(W) | 1 | 0=Off;1=On
1762 | GMAG:Reset (remote) | R(W) | 1 | 0=Off;1=On
1763 | GMAG:AVR Ref execute (remote) | R(W) | 1 | 0=Off;1=On
1764 | GMAG:AVR Ref value (remote) | R(W) | 2 | FLOAT [0...450000] (Hi-16bits)
1765 |  |  |  | HR1764 (Lo-16bits)
1766 | GMAG:FCR Ref execute (remote) | R(W) | 1 | 0=Off;1=On
1767 | GMAG:FCR Ref value (remote) | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
1768 |  |  |  | HR1767 (Lo-16bits)
1769 | GMAG:MVar Ref execute (remote) | R(W) | 1 | 0=Off;1=On
1770 | GMAG:MVar Ref value (MVar) (remote) | R(W) | 2 | FLOAT [-1000...1000] (Hi-16bits)
1771 |  |  |  | HR1770 (Lo-16bits)
1772 | GMAG:PF Ref execute (remote) | R(W) | 1 | 0=Off;1=On
1773 | GMAG:PF Ref value (remote) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
1774 |  |  |  | HR1773 (Lo-16bits)
1775 | GMAG:Open FB command (remote) | R(W) | 1 | 0=Off;1=On
1776 | GMAG:Close FB command (remote) | R(W) | 1 | 0=Off;1=On
1777 | GMAG:AVR speed 90 (remote) | R(W) | 1 | 0=Off;1=On
1778 | GMAG:Ind GB closed (remote) | R(W) | 1 | 0=Off;1=On
1779 | GMAG:Island mode (remote) | R(W) | 1 | 0=Off;1=On
1780 | GMAG:Command voltage matching (remote) | R(W) | 1 | 0=Off;1=On
1781 | GMAG:Grid voltage (remote) | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
1782 |  |  |  | HR1781 (Lo-16bits)
1783 | GMAG:AVR Ref start (remote) | R(W) | 1 | 0=Off;1=On
1784 | GMAG:Field current (remote) | R | 2 | FLOAT [-500...500] (Hi-16bits)
1785 |  |  |  | HR1784 (Lo-16bits)
1786 | GMAG:AVR Ref actual (remote) | R | 2 | FLOAT [-500...500] (Hi-16bits)
1787 |  |  |  | HR1786 (Lo-16bits)
1788 | GMAG:FCR Ref actual (remote) | R | 2 | FLOAT [-500...500] (Hi-16bits)
1789 |  |  |  | HR1788 (Lo-16bits)
1790 | GMAG:MVAR Ref actual (remote) | R | 2 | FLOAT [-500...500] (Hi-16bits)
1791 |  |  |  | HR1790 (Lo-16bits)
1792 | GMAG:PF Ref actual (remote) | R | 2 | FLOAT [-500...500] (Hi-16bits)
1793 |  |  |  | HR1792 (Lo-16bits)
1794 | GMAG:Mode MVAR (remote) | R | 1 | 0=Off;1=On
1795 | GMAG:Mode PF (remote) | R | 1 | 0=Off;1=On
1796 | DIGI:DIs | R | 2 | 0b=DI65;1b=DI66;2b=DI67;3b=DI68;4b=DI69;5b=DI70;6b=DI71;7b=DI72;8b=DI73;9b=DI74;10b=DI75;11b=DI76;12b=DI77;13b=DI78;14b=DI79;15b=DI80;16b=DI81;17b=DI82;18b=DI83;19b=DI84;20b=DI85;21b=DI86;22b=DI87;23b=DI88;24b=DI89;25b=DI90;26b=DI91;27b=DI92;28b=DI93;29b=DI94;30b=DI95;31b=DI96 (Hi-16bits)
1797 |  |  |  | HR1796 (Lo-16bits)
1798 | DIGI:DIs | R | 2 | 0b=DI97;1b=DI98;2b=DI99;3b=DI100;4b=DI101;5b=DI102;6b=DI103;7b=DI104;8b=DI105;9b=DI106;10b=DI107;11b=DI108;12b=DI109;13b=DI110;14b=DI111;15b=DI112;16b=DI113;17b=DI114;18b=DI115;19b=DI116;20b=DI117;21b=DI118;22b=DI119;23b=DI120;24b=DI121;25b=DI122;26b=DI123;27b=DI124;28b=DI125;29b=DI126;30b=DI127;31b=DI128 (Hi-16bits)
1799 |  |  |  | HR1798 (Lo-16bits)
1800 | RELE:Outputs status | R | 2 | 0b=O33;1b=O34;2b=O35 (Hi-16bits)
1801 |  |  |  | HR1800 (Lo-16bits)
1802 | GMAG:Command Excitation to Remote control | R(W) | 1 | 0=Off;1=On
1803 | FREQS:f atm. Display (when not measurable is 0Hz) | R | 2 | FLOAT [0...75] (Hi-16bits)
1804 |  |  |  | HR1803 (Lo-16bits)
1805 | GMAG:Command Excitation to Remote control Received | R | 1 | 0=No;1=Yes
1806 | GMAG:Command AVR (remote) Received | R | 1 | 0=No;1=Yes
1807 | GMAG:Command FCR (remote) Received | R | 1 | 0=No;1=Yes
1808 | GMAG:Command MVAR (remote) Received | R | 1 | 0=No;1=Yes
1809 | GMAG:Command PF (remote) Received | R | 1 | 0=No;1=Yes
1810 | GMAG:Reset remote Received indications | R(W) | 1 | 0=-;1=Reset
1811 | GMAG:GMAG FCR Mode | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1812 |  |  |  | HR1811 (Lo-16bits)
1813 | GMAG:GMAG AVR Mode | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1814 |  |  |  | HR1813 (Lo-16bits)
1815 | GMAG:Unload Q (remote) Received | R | 1 | 0=No;1=Yes
1816 | GMAG:Reset (remote) Received | R | 1 | 0=No;1=Yes
1817 | GMAG:AVR Ref execute (remote) Received | R | 1 | 0=No;1=Yes
1818 | GMAG:AVR Ref value (remote) Received | R | 2 | FLOAT [0...450000] (Hi-16bits)
1819 |  |  |  | HR1818 (Lo-16bits)
1820 | GMAG:FCR Ref execute (remote) Received | R | 1 | 0=No;1=Yes
1821 | GMAG:FCR Ref value (remote) Received | R | 2 | FLOAT [0...100] (Hi-16bits)
1822 |  |  |  | HR1821 (Lo-16bits)
1823 | GMAG:MVar Ref execute (remote) Received | R | 1 | 0=No;1=Yes
1824 | GMAG:MVar Ref value (remote) Received | R | 2 | FLOAT [-1000...1000] (Hi-16bits)
1825 |  |  |  | HR1824 (Lo-16bits)
1826 | GMAG:PF Ref execute (remote) Received | R | 1 | 0=No;1=Yes
1827 | GMAG:PF Ref value (remote) Received | R | 2 | FLOAT [-1...1] (Hi-16bits)
1828 |  |  |  | HR1827 (Lo-16bits)
1829 | GMAG:Open FB command (remote) Received | R | 1 | 0=No;1=Yes
1830 | GMAG:Close FB command (remote) Received | R | 1 | 0=No;1=Yes
1831 | GMAG:AVR speed 90 (remote) Received | R | 1 | 0=No;1=Yes
1832 | GMAG:Ind GB closed (remote) Received | R | 1 | 0=No;1=Yes
1833 | GMAG:Island mode (remote) Received | R | 1 | 0=No;1=Yes
1834 | GMAG:Command voltage matching (remote) Received | R | 1 | 0=No;1=Yes
1835 | GMAG:Grid voltage (remote) Received | R | 2 | FLOAT [0...500] (Hi-16bits)
1836 |  |  |  | HR1835 (Lo-16bits)
1837 | GMAG:AVR Ref start (remote) Received | R | 1 | 0=No;1=Yes
1838 | IAE1:I>U< I.A.E. condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1839 | GSYN:Synchronizer mode | R(W) | 1 | 0=Disabled;1=Activated
1840 | GSYN:Magnitude difference | R | 2 | FLOAT [-200...200] (Hi-16bits)
1841 |  |  |  | HR1840 (Lo-16bits)
1842 | GSYN:Frequency difference | R | 2 | FLOAT [-100...100] (Hi-16bits)
1843 |  |  |  | HR1842 (Lo-16bits)
1844 | GSYN:Angle difference | R | 2 | FLOAT [-360...360] (Hi-16bits)
1845 |  |  |  | HR1844 (Lo-16bits)
1846 | GSYN:Start Synchronizer | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
1847 |  |  |  | HR1846 (Lo-16bits)
1848 | GSYN:Stop Synchronizer | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
1849 |  |  |  | HR1848 (Lo-16bits)
1850 | GSYN:Block and Interrupt Synchronizing | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
1851 |  |  |  | HR1850 (Lo-16bits)
1852 | GSYN:Breaker Closed | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
1853 |  |  |  | HR1852 (Lo-16bits)
1854 | GSYN:GSYN Running | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1855 |  |  |  | HR1854 (Lo-16bits)
1856 | GSYN:GSYN Increase Voltage | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1857 |  |  |  | HR1856 (Lo-16bits)
1858 | GSYN:GSYN Decrease Voltage | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1859 |  |  |  | HR1858 (Lo-16bits)
1860 | GSYN:GSYN Increase Frequency | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1861 |  |  |  | HR1860 (Lo-16bits)
1862 | GSYN:GSYN Decrease Frequency | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1863 |  |  |  | HR1862 (Lo-16bits)
1864 | GSYN:GSYN Breaker Close Pulse | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1865 |  |  |  | HR1864 (Lo-16bits)
1866 | GSYN:GSYN Long Sync Time | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1867 |  |  |  | HR1866 (Lo-16bits)
1868 | GSYN:Magnitude difference fine tune | R(W) | 2 | FLOAT [-200...200] (Hi-16bits)
1869 |  |  |  | HR1868 (Lo-16bits)
1870 | GSYN:Frequency difference fine tune | R(W) | 2 | FLOAT [-100...100] (Hi-16bits)
1871 |  |  |  | HR1870 (Lo-16bits)
1872 | GSYN:Angle difference fine tune | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
1873 |  |  |  | HR1872 (Lo-16bits)
1874 | GSYN:GSYN Blocked | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1875 |  |  |  | HR1874 (Lo-16bits)
1876 | GSYN:GSYN Voltage Mag.Difference Ok | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1877 |  |  |  | HR1876 (Lo-16bits)
1878 | GSYN:GSYN Voltage Freq.Difference Ok | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1879 |  |  |  | HR1878 (Lo-16bits)
1880 | GSYN:GSYN Voltage Ang.Difference Ok | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1881 |  |  |  | HR1880 (Lo-16bits)
1882 | GSYN:Magnitude difference on closing BRK | R | 2 | FLOAT [-200...200] (Hi-16bits)
1883 |  |  |  | HR1882 (Lo-16bits)
1884 | GSYN:Frequency difference on closing BRK | R | 2 | FLOAT [-100...100] (Hi-16bits)
1885 |  |  |  | HR1884 (Lo-16bits)
1886 | GSYN:Angle difference on closing BRK | R | 2 | FLOAT [-360...360] (Hi-16bits)
1887 |  |  |  | HR1886 (Lo-16bits)
1888 | GSYN:Synchronizing time left | R | 2 | FLOAT [0...1800] (Hi-16bits)
1889 |  |  |  | HR1888 (Lo-16bits)
1890 | VREC:Fault register mode | R(W) | 1 | 0=Disabled;1=Activated
1891 | VREC:Scale current values to primary | R(W) | 1 | 0=No;1=Yes
1892 | VREC:Fault register trigger | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
1893 |  |  |  | HR1892 (Lo-16bits)
1894 | VREC:Record fault types (Overcurrrent & Voltage Over/Under) faults | R(W) | 1 | 0=No;1=Yes
1895 | VREC:VREC Magnitude 1 | R | 2 | FLOAT [0...1800] (Hi-16bits)
1896 |  |  |  | HR1895 (Lo-16bits)
1897 | VREC:VREC Magnitude 2 | R | 2 | FLOAT [0...1800] (Hi-16bits)
1898 |  |  |  | HR1897 (Lo-16bits)
1899 | VREC:VREC Magnitude 3 | R | 2 | FLOAT [0...1800] (Hi-16bits)
1900 |  |  |  | HR1899 (Lo-16bits)
1901 | VREC:VREC Magnitude 4 | R | 2 | FLOAT [0...1800] (Hi-16bits)
1902 |  |  |  | HR1901 (Lo-16bits)
1903 | VREC:VREC Magnitude 5 | R | 2 | FLOAT [0...1800] (Hi-16bits)
1904 |  |  |  | HR1903 (Lo-16bits)
1905 | VREC:VREC Magnitude 6 | R | 2 | FLOAT [0...1800] (Hi-16bits)
1906 |  |  |  | HR1905 (Lo-16bits)
1907 | VREC:VREC Magnitude 7 | R | 2 | FLOAT [0...1800] (Hi-16bits)
1908 |  |  |  | HR1907 (Lo-16bits)
1909 | VREC:VREC Magnitude 8 | R | 2 | FLOAT [0...1800] (Hi-16bits)
1910 |  |  |  | HR1909 (Lo-16bits)
1911 | RTB:Real time bus measurements | R(W) | 1 | 0=Disabled;1=Activated
1912 | RTB:Scale current values to primary | R(W) | 1 | 0=No;1=Yes
1913 | RTB:Magnitude 1 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1914 |  |  |  | HR1913 (Lo-16bits)
1915 | RTB:Magnitude 2 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1916 |  |  |  | HR1915 (Lo-16bits)
1917 | RTB:Magnitude 3 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1918 |  |  |  | HR1917 (Lo-16bits)
1919 | RTB:Magnitude 4 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1920 |  |  |  | HR1919 (Lo-16bits)
1921 | RTB:Magnitude 5 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1922 |  |  |  | HR1921 (Lo-16bits)
1923 | RTB:Magnitude 6 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1924 |  |  |  | HR1923 (Lo-16bits)
1925 | RTB:Magnitude 7 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1926 |  |  |  | HR1925 (Lo-16bits)
1927 | RTB:Magnitude 8 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1928 |  |  |  | HR1927 (Lo-16bits)
1929 | AOUT:mA In (I option 1) | R | 2 | FLOAT [0...24] (Hi-16bits)
1930 |  |  |  | HR1929 (Lo-16bits)
1931 | AOUT:mA In (I option 2) | R | 2 | FLOAT [0...24] (Hi-16bits)
1932 |  |  |  | HR1931 (Lo-16bits)
1933 | AOUT:mA Out Channel 1 Input Magnitude now (I option 1) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1934 |  |  |  | HR1933 (Lo-16bits)
1935 | AOUT:mA Out Channel 1 Outputs now (I option 1) | R | 2 | FLOAT [0...24] (Hi-16bits)
1936 |  |  |  | HR1935 (Lo-16bits)
1937 | AOUT:mA Out Channel 2 Input Magnitude now (I option 1) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1938 |  |  |  | HR1937 (Lo-16bits)
1939 | AOUT:mA Out Channel 2 Outputs now (I option 1) | R | 2 | FLOAT [0...24] (Hi-16bits)
1940 |  |  |  | HR1939 (Lo-16bits)
1941 | AOUT:mA Out Channel 3 Input Magnitude now (I option 1) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1942 |  |  |  | HR1941 (Lo-16bits)
1943 | AOUT:mA Out Channel 3 Outputs now (I option 1) | R | 2 | FLOAT [0...24] (Hi-16bits)
1944 |  |  |  | HR1943 (Lo-16bits)
1945 | AOUT:mA Out Channel 4 Input Magnitude now (I option 1) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1946 |  |  |  | HR1945 (Lo-16bits)
1947 | AOUT:mA Out Channel 4 Outputs now (I option 1) | R | 2 | FLOAT [0...24] (Hi-16bits)
1948 |  |  |  | HR1947 (Lo-16bits)
1949 | AOUT:mA Out Channel 5 Input Magnitude now (I option 2) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1950 |  |  |  | HR1949 (Lo-16bits)
1951 | AOUT:mA Out Channel 5 Outputs now (I option 2) | R | 2 | FLOAT [0...24] (Hi-16bits)
1952 |  |  |  | HR1951 (Lo-16bits)
1953 | AOUT:mA Out Channel 6 Input Magnitude now (I option 2) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1954 |  |  |  | HR1953 (Lo-16bits)
1955 | AOUT:mA Out Channel 6 Outputs now (I option 2) | R | 2 | FLOAT [0...24] (Hi-16bits)
1956 |  |  |  | HR1955 (Lo-16bits)
1957 | AOUT:mA Out Channel 7 Input Magnitude now (I option 2) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1958 |  |  |  | HR1957 (Lo-16bits)
1959 | AOUT:mA Out Channel 7 Outputs now (I option 2) | R | 2 | FLOAT [0...24] (Hi-16bits)
1960 |  |  |  | HR1959 (Lo-16bits)
1961 | AOUT:mA Out Channel 8 Input Magnitude now (I option 2) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
1962 |  |  |  | HR1961 (Lo-16bits)
1963 | AOUT:mA Out Channel 8 Outputs now (I option 2) | R | 2 | FLOAT [0...24] (Hi-16bits)
1964 |  |  |  | HR1963 (Lo-16bits)
1965 | RTD1:S13 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1966 |  |  |  | HR1965 (Lo-16bits)
1967 | RTD1:S14 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1968 |  |  |  | HR1967 (Lo-16bits)
1969 | RTD1:S15 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1970 |  |  |  | HR1969 (Lo-16bits)
1971 | RTD1:S16 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
1972 |  |  |  | HR1971 (Lo-16bits)
1973 | RTD1:S13 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1974 |  |  |  | HR1973 (Lo-16bits)
1975 | RTD1:S13 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1976 |  |  |  | HR1975 (Lo-16bits)
1977 | RTD1:S13 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1978 |  |  |  | HR1977 (Lo-16bits)
1979 | RTD1:S14 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1980 |  |  |  | HR1979 (Lo-16bits)
1981 | RTD1:S14 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1982 |  |  |  | HR1981 (Lo-16bits)
1983 | RTD1:S14 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1984 |  |  |  | HR1983 (Lo-16bits)
1985 | RTD1:S15 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1986 |  |  |  | HR1985 (Lo-16bits)
1987 | RTD1:S15 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1988 |  |  |  | HR1987 (Lo-16bits)
1989 | RTD1:S15 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1990 |  |  |  | HR1989 (Lo-16bits)
1991 | RTD1:S16 Alarm1 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1992 |  |  |  | HR1991 (Lo-16bits)
1993 | RTD1:S16 Alarm2 On | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1994 |  |  |  | HR1993 (Lo-16bits)
1995 | RTD1:S16 Meas Invalid | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1996 |  |  |  | HR1995 (Lo-16bits)
1997 | RTDIN:S1 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
1998 |  |  |  | HR1997 (Lo-16bits)
1999 | RTDIN:S2 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2000 |  |  |  | HR1999 (Lo-16bits)
2001 | RTDIN:S3 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2002 |  |  |  | HR2001 (Lo-16bits)
2003 | RTDIN:S4 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2004 |  |  |  | HR2003 (Lo-16bits)
2005 | RTDIN:S5 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2006 |  |  |  | HR2005 (Lo-16bits)
2007 | RTDIN:S6 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2008 |  |  |  | HR2007 (Lo-16bits)
2009 | RTDIN:S7 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2010 |  |  |  | HR2009 (Lo-16bits)
2011 | RTDIN:S8 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2012 |  |  |  | HR2011 (Lo-16bits)
2013 | RTDIN:S9 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2014 |  |  |  | HR2013 (Lo-16bits)
2015 | RTDIN:S10 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2016 |  |  |  | HR2015 (Lo-16bits)
2017 | RTDIN:S11 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2018 |  |  |  | HR2017 (Lo-16bits)
2019 | RTDIN:S12 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2020 |  |  |  | HR2019 (Lo-16bits)
2021 | RTDIN:S13 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2022 |  |  |  | HR2021 (Lo-16bits)
2023 | RTDIN:S14 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2024 |  |  |  | HR2023 (Lo-16bits)
2025 | RTDIN:S15 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2026 |  |  |  | HR2025 (Lo-16bits)
2027 | RTDIN:S16 Resistance | R | 2 | FLOAT [0...4000] (Hi-16bits)
2028 |  |  |  | HR2027 (Lo-16bits)
2029 | GSYN:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
2030 |  |  |  | HR2029 (Lo-16bits)
2031 | GSYN:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
2032 |  |  |  | HR2031 (Lo-16bits)
2033 | GSYN:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
2034 |  |  |  | HR2033 (Lo-16bits)
2035 | GMAG:Read MVar Ref from | R(W) | 1 | 0=Value from comm Bus;1=Value from AI
2036 | GMAG:MVar Ref selection | R(W) | 1 | 0=Scaled input 1;1=Scaled input 2;2=Scaled input 3;3=Scaled input 4
2037 | GMAG:MVar Ref change threshold (AI) | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
2038 |  |  |  | HR2037 (Lo-16bits)
2039 | GMAG:Update MVar Ref automatically when threshold exceeds | R(W) | 1 | 0=No;1=Yes
2040 | PWR1:PQS>/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2041 | PWR2:PQS>>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2042 | PWR3:PQS>>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2043 | PWR4:PQS>>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2044 | CIN6:Ind.6 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2045 | CIN7:Ind.7 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2046 | CIN8:Ind.8 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2047 | CIN9:Ind.9 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2048 | CIN10:Ind.10 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2049 | CIN11:Ind.11 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2050 | CIN12:Ind.12 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2051 | CIN13:Ind.13 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2052 | CIN14:Ind.14 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2053 | CIN15:Ind.15 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2054 | CIN16:Ind.16 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2055 | CIN17:Ind.17 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2056 | CIN18:Ind.18 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2057 | CIN19:Ind.19 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2058 | CIN20:Ind.20 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
2059 | RHC1:Counter is now | R | 1 | 0=Idle;1=Counting
2060 | RHC1:Running hours | R(W) | 2 | UINT32 [0...4294967295] (Hi-16bits)
2061 |  |  |  | HR2060 (Lo-16bits)
2062 | GST1:Generating time (Running hours) | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
2063 |  |  |  | HR2062 (Lo-16bits)
2064 | NOC1:I> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2065 | NOC1:I> Latest fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2066 | NOC1:I> Latest fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2067 |  |  |  | HR2066 (Lo-16bits)
2068 | NOC1:I> Latest fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2069 |  |  |  | HR2068 (Lo-16bits)
2070 | NOC1:I> Latest fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2071 |  |  |  | HR2070 (Lo-16bits)
2072 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2073 |  |  |  | HR2072 (Lo-16bits)
2074 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2075 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2076 |  |  |  | HR2075 (Lo-16bits)
2077 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2078 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2079 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2080 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2081 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2082 |  |  |  | HR2081 (Lo-16bits)
2083 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2084 |  |  |  | HR2083 (Lo-16bits)
2085 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2086 |  |  |  | HR2085 (Lo-16bits)
2087 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2088 |  |  |  | HR2087 (Lo-16bits)
2089 | NOC1:Select setting group | R(W) | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2090 | NOC1:Write settings to selected SG | R(W) | 1 | 0=-;1=Write (autoreset)
2091 | NOC2:I>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2092 | NOC2:I>> Latest fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2093 | NOC2:I>> Latest fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2094 |  |  |  | HR2093 (Lo-16bits)
2095 | NOC2:I>> Latest fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2096 |  |  |  | HR2095 (Lo-16bits)
2097 | NOC2:I>> Latest fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2098 |  |  |  | HR2097 (Lo-16bits)
2099 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2100 |  |  |  | HR2099 (Lo-16bits)
2101 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2102 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2103 |  |  |  | HR2102 (Lo-16bits)
2104 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2105 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2106 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2107 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2108 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2109 |  |  |  | HR2108 (Lo-16bits)
2110 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2111 |  |  |  | HR2110 (Lo-16bits)
2112 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2113 |  |  |  | HR2112 (Lo-16bits)
2114 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2115 |  |  |  | HR2114 (Lo-16bits)
2116 | NOC2:Select setting group | R(W) | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2117 | NOC2:Write settings to selected SG | R(W) | 1 | 0=-;1=Write (autoreset)
2118 | NOC3:I>>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2119 | NOC3:I>>> Latest fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2120 | NOC3:I>>> Latest fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2121 |  |  |  | HR2120 (Lo-16bits)
2122 | NOC3:I>>> Latest fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2123 |  |  |  | HR2122 (Lo-16bits)
2124 | NOC3:I>>> Latest fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2125 |  |  |  | HR2124 (Lo-16bits)
2126 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2127 |  |  |  | HR2126 (Lo-16bits)
2128 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2129 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2130 |  |  |  | HR2129 (Lo-16bits)
2131 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2132 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2133 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2134 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2135 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2136 |  |  |  | HR2135 (Lo-16bits)
2137 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2138 |  |  |  | HR2137 (Lo-16bits)
2139 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2140 |  |  |  | HR2139 (Lo-16bits)
2141 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2142 |  |  |  | HR2141 (Lo-16bits)
2143 | NOC3:Select setting group | R(W) | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2144 | NOC3:Write settings to selected SG | R(W) | 1 | 0=-;1=Write (autoreset)
2145 | NOC4:I>>>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2146 | NOC4:I>>>> Latest fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2147 | NOC4:I>>>> Latest fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2148 |  |  |  | HR2147 (Lo-16bits)
2149 | NOC4:I>>>> Latest fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2150 |  |  |  | HR2149 (Lo-16bits)
2151 | NOC4:I>>>> Latest fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2152 |  |  |  | HR2151 (Lo-16bits)
2153 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2154 |  |  |  | HR2153 (Lo-16bits)
2155 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2156 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2157 |  |  |  | HR2156 (Lo-16bits)
2158 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2159 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2160 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2161 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2162 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2163 |  |  |  | HR2162 (Lo-16bits)
2164 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2165 |  |  |  | HR2164 (Lo-16bits)
2166 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2167 |  |  |  | HR2166 (Lo-16bits)
2168 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2169 |  |  |  | HR2168 (Lo-16bits)
2170 | NOC4:Select setting group | R(W) | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2171 | NOC4:Write settings to selected SG | R(W) | 1 | 0=-;1=Write (autoreset)
2172 | DOC1:Idir> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2173 | DOC1:Idir> Latest fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2174 | DOC1:Idir> Latest fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
2175 |  |  |  | HR2174 (Lo-16bits)
2176 | DOC1:Idir> Latest fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2177 |  |  |  | HR2176 (Lo-16bits)
2178 | DOC1:Idir> Latest fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2179 |  |  |  | HR2178 (Lo-16bits)
2180 | DOC1:Idir> Latest fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2181 |  |  |  | HR2180 (Lo-16bits)
2182 | DOC2:Idir>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2183 | DOC2:Idir>> Latest fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2184 | DOC2:Idir>> Latest fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
2185 |  |  |  | HR2184 (Lo-16bits)
2186 | DOC2:Idir>> Latest fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2187 |  |  |  | HR2186 (Lo-16bits)
2188 | DOC2:Idir>> Latest fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2189 |  |  |  | HR2188 (Lo-16bits)
2190 | DOC2:Idir>> Latest fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2191 |  |  |  | HR2190 (Lo-16bits)
2192 | DOC3:Idir>>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2193 | DOC3:Idir>>> Latest fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2194 | DOC3:Idir>>> Latest fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
2195 |  |  |  | HR2194 (Lo-16bits)
2196 | DOC3:Idir>>> Latest fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2197 |  |  |  | HR2196 (Lo-16bits)
2198 | DOC3:Idir>>> Latest fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2199 |  |  |  | HR2198 (Lo-16bits)
2200 | DOC3:Idir>>> Latest fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2201 |  |  |  | HR2200 (Lo-16bits)
2202 | DOC4:Idir>>>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2203 | DOC4:Idir>>>> Latest fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2204 | DOC4:Idir>>>> Latest fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
2205 |  |  |  | HR2204 (Lo-16bits)
2206 | DOC4:Idir>>>> Latest fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2207 |  |  |  | HR2206 (Lo-16bits)
2208 | DOC4:Idir>>>> Latest fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2209 |  |  |  | HR2208 (Lo-16bits)
2210 | DOC4:Idir>>>> Latest fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2211 |  |  |  | HR2210 (Lo-16bits)
2212 | NEF1:I0> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2213 | NEF1:I0> Latest fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2214 |  |  |  | HR2213 (Lo-16bits)
2215 | NEF1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2216 |  |  |  | HR2215 (Lo-16bits)
2217 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2218 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2219 |  |  |  | HR2218 (Lo-16bits)
2220 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2221 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2222 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2223 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2224 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2225 |  |  |  | HR2224 (Lo-16bits)
2226 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2227 |  |  |  | HR2226 (Lo-16bits)
2228 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2229 |  |  |  | HR2228 (Lo-16bits)
2230 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2231 |  |  |  | HR2230 (Lo-16bits)
2232 | NEF1:Select setting group | R(W) | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2233 | NEF1:Write settings to selected SG | R(W) | 1 | 0=-;1=Write (autoreset)
2234 | NEF2:I0>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2235 | NEF2:I0>> Latest fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2236 |  |  |  | HR2235 (Lo-16bits)
2237 | NEF2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2238 |  |  |  | HR2237 (Lo-16bits)
2239 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2240 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2241 |  |  |  | HR2240 (Lo-16bits)
2242 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2243 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2244 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2245 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2246 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2247 |  |  |  | HR2246 (Lo-16bits)
2248 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2249 |  |  |  | HR2248 (Lo-16bits)
2250 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2251 |  |  |  | HR2250 (Lo-16bits)
2252 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2253 |  |  |  | HR2252 (Lo-16bits)
2254 | NEF2:Select setting group | R(W) | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2255 | NEF2:Write settings to selected SG | R(W) | 1 | 0=-;1=Write (autoreset)
2256 | NEF3:I0>>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2257 | NEF3:I0>>> Latest fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2258 |  |  |  | HR2257 (Lo-16bits)
2259 | NEF3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2260 |  |  |  | HR2259 (Lo-16bits)
2261 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2262 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2263 |  |  |  | HR2262 (Lo-16bits)
2264 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2265 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2266 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2267 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2268 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2269 |  |  |  | HR2268 (Lo-16bits)
2270 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2271 |  |  |  | HR2270 (Lo-16bits)
2272 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2273 |  |  |  | HR2272 (Lo-16bits)
2274 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2275 |  |  |  | HR2274 (Lo-16bits)
2276 | NEF3:Select setting group | R(W) | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2277 | NEF3:Write settings to selected SG | R(W) | 1 | 0=-;1=Write (autoreset)
2278 | NEF4:I0>>>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2279 | NEF4:I0>>>> Latest fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2280 |  |  |  | HR2279 (Lo-16bits)
2281 | NEF4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2282 |  |  |  | HR2281 (Lo-16bits)
2283 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2284 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2285 |  |  |  | HR2284 (Lo-16bits)
2286 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2287 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2288 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2289 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2290 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2291 |  |  |  | HR2290 (Lo-16bits)
2292 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2293 |  |  |  | HR2292 (Lo-16bits)
2294 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2295 |  |  |  | HR2294 (Lo-16bits)
2296 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2297 |  |  |  | HR2296 (Lo-16bits)
2298 | NEF4:Select setting group | R(W) | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2299 | NEF4:Write settings to selected SG | R(W) | 1 | 0=-;1=Write (autoreset)
2300 | DEF1:I0dir> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2301 | DEF1:I0dir> Latest fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
2302 |  |  |  | HR2301 (Lo-16bits)
2303 | DEF1:I0dir> Latest fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2304 |  |  |  | HR2303 (Lo-16bits)
2305 | DEF1:I0dir> Latest fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2306 |  |  |  | HR2305 (Lo-16bits)
2307 | DEF2:I0dir>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2308 | DEF2:I0dir>> Latest fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
2309 |  |  |  | HR2308 (Lo-16bits)
2310 | DEF2:I0dir>> Latest fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2311 |  |  |  | HR2310 (Lo-16bits)
2312 | DEF2:I0dir>> Latest fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2313 |  |  |  | HR2312 (Lo-16bits)
2314 | DEF3:I0dir>>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2315 | DEF3:I0dir>>> Latest fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
2316 |  |  |  | HR2315 (Lo-16bits)
2317 | DEF3:I0dir>>> Latest fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2318 |  |  |  | HR2317 (Lo-16bits)
2319 | DEF3:I0dir>>> Latest fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2320 |  |  |  | HR2319 (Lo-16bits)
2321 | DEF4:I0dir>>>> Latest fault ended with | R | 1 | 0=No Faults;1=Start;2=Trip
2322 | DEF4:I0dir>>>> Latest fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
2323 |  |  |  | HR2322 (Lo-16bits)
2324 | DEF4:I0dir>>>> Latest fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2325 |  |  |  | HR2324 (Lo-16bits)
2326 | DEF4:I0dir>>>> Latest fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2327 |  |  |  | HR2326 (Lo-16bits)
2328 | GMAG:MVar Ref value (kVar) (remote) | R(W) | 2 | FLOAT [-1000...1000] (Hi-16bits)
2329 |  |  |  | HR2328 (Lo-16bits)
2330 | GMAG:Mode FCR (remote) | R | 1 | 0=Off;1=On
2331 | GMAG:Mode AVR (remote) | R | 1 | 0=Off;1=On
2332 | ALARM:Alarms 65-96 | R | 2 | 0b=A65;1b=A66;2b=A67;3b=A68;4b=A69;5b=A70;6b=A71;7b=A72;8b=A73;9b=A74;10b=A75;11b=A76;12b=A77;13b=A78;14b=A79;15b=A80;16b=A81;17b=A82;18b=A83;19b=A84;20b=A85;21b=A86;22b=A87;23b=A88;24b=A89;25b=A90;26b=A91;27b=A92;28b=A93;29b=A94;30b=A95;31b=A96 (Hi-16bits)
2333 |  |  |  | HR2332 (Lo-16bits)
2334 | ALARM:Alarms 97-128 | R | 2 | 0b=A97;1b=A98;2b=A99;3b=A100;4b=A101;5b=A102;6b=A103;7b=A104;8b=A105;9b=A106;10b=A107;11b=A108;12b=A109;13b=A110;14b=A111;15b=A112;16b=A113;17b=A114;18b=A115;19b=A116;20b=A117;21b=A118;22b=A119;23b=A120;24b=A121;25b=A122;26b=A123;27b=A124;28b=A125;29b=A126;30b=A127;31b=A128 (Hi-16bits)
2335 |  |  |  | HR2334 (Lo-16bits)
2336 | VUB1:U1/2 >/< Measurement condition | R | 1 | 0=Seq Volt available;1=No Seq volts available
2337 | VUB2:U1/2 >>/<< Measurement condition | R | 1 | 0=Seq Volt available;1=No Seq volts available
2338 | VUB3:U1/2 >>>/<<< Measurement condition | R | 1 | 0=Seq Volt available;1=No Seq volts available
2339 | VUB4:U1/2 >>>>/<<<< Measurement condition | R | 1 | 0=Seq Volt available;1=No Seq volts available
2340 | VREC:Reset last fault values from memory | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
2341 |  |  |  | HR2340 (Lo-16bits)
2342 | NOC1:I> phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Trip AB;11=Trip BC;12=Trip CA;13=Start ABC;14=Trip ABC
2343 | NOC2:I>> phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Trip AB;11=Trip BC;12=Trip CA;13=Start ABC;14=Trip ABC
2344 | NOC3:I>>> phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Trip AB;11=Trip BC;12=Trip CA;13=Start ABC;14=Trip ABC
2345 | NOC4:I>>>> phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Trip AB;11=Trip BC;12=Trip CA;13=Start ABC;14=Trip ABC
2346 | VRG1:Target voltage (UTGT) | R(W) | 2 | FLOAT [70...140] (Hi-16bits)
2347 |  |  |  | HR2346 (Lo-16bits)
2348 | VRG1:Target voltage (UTGT) | R(W) | 2 | FLOAT [70...140] (Hi-16bits)
2349 |  |  |  | HR2348 (Lo-16bits)
2350 | VRG1:Target voltage (UTGT) | R(W) | 2 | FLOAT [70...140] (Hi-16bits)
2351 |  |  |  | HR2350 (Lo-16bits)
2352 | VRG1:Target voltage (UTGT) | R(W) | 2 | FLOAT [70...140] (Hi-16bits)
2353 |  |  |  | HR2352 (Lo-16bits)
2354 | VRG1:Target voltage (UTGT) | R(W) | 2 | FLOAT [70...140] (Hi-16bits)
2355 |  |  |  | HR2354 (Lo-16bits)
2356 | VRG1:Target voltage (UTGT) | R(W) | 2 | FLOAT [70...140] (Hi-16bits)
2357 |  |  |  | HR2356 (Lo-16bits)
2358 | VRG1:Target voltage (UTGT) | R(W) | 2 | FLOAT [70...140] (Hi-16bits)
2359 |  |  |  | HR2358 (Lo-16bits)
2360 | VRG1:Target voltage (UTGT) | R(W) | 2 | FLOAT [70...140] (Hi-16bits)
2361 |  |  |  | HR2360 (Lo-16bits)
2362 | VRG1:U> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2363 |  |  |  | HR2362 (Lo-16bits)
2364 | VRG1:U> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2365 |  |  |  | HR2364 (Lo-16bits)
2366 | VRG1:U> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2367 |  |  |  | HR2366 (Lo-16bits)
2368 | VRG1:U> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2369 |  |  |  | HR2368 (Lo-16bits)
2370 | VRG1:U> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2371 |  |  |  | HR2370 (Lo-16bits)
2372 | VRG1:U> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2373 |  |  |  | HR2372 (Lo-16bits)
2374 | VRG1:U> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2375 |  |  |  | HR2374 (Lo-16bits)
2376 | VRG1:U> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2377 |  |  |  | HR2376 (Lo-16bits)
2378 | VRG1:U< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2379 |  |  |  | HR2378 (Lo-16bits)
2380 | VRG1:U< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2381 |  |  |  | HR2380 (Lo-16bits)
2382 | VRG1:U< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2383 |  |  |  | HR2382 (Lo-16bits)
2384 | VRG1:U< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2385 |  |  |  | HR2384 (Lo-16bits)
2386 | VRG1:U< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2387 |  |  |  | HR2386 (Lo-16bits)
2388 | VRG1:U< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2389 |  |  |  | HR2388 (Lo-16bits)
2390 | VRG1:U< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2391 |  |  |  | HR2390 (Lo-16bits)
2392 | VRG1:U< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2393 |  |  |  | HR2392 (Lo-16bits)
2394 | VRG1:U>/< T1 time delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2395 |  |  |  | HR2394 (Lo-16bits)
2396 | VRG1:U>/< T1 time delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2397 |  |  |  | HR2396 (Lo-16bits)
2398 | VRG1:U>/< T1 time delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2399 |  |  |  | HR2398 (Lo-16bits)
2400 | VRG1:U>/< T1 time delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2401 |  |  |  | HR2400 (Lo-16bits)
2402 | VRG1:U>/< T1 time delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2403 |  |  |  | HR2402 (Lo-16bits)
2404 | VRG1:U>/< T1 time delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2405 |  |  |  | HR2404 (Lo-16bits)
2406 | VRG1:U>/< T1 time delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2407 |  |  |  | HR2406 (Lo-16bits)
2408 | VRG1:U>/< T1 time delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2409 |  |  |  | HR2408 (Lo-16bits)
2410 | VRG1:U>> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2411 |  |  |  | HR2410 (Lo-16bits)
2412 | VRG1:U>> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2413 |  |  |  | HR2412 (Lo-16bits)
2414 | VRG1:U>> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2415 |  |  |  | HR2414 (Lo-16bits)
2416 | VRG1:U>> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2417 |  |  |  | HR2416 (Lo-16bits)
2418 | VRG1:U>> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2419 |  |  |  | HR2418 (Lo-16bits)
2420 | VRG1:U>> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2421 |  |  |  | HR2420 (Lo-16bits)
2422 | VRG1:U>> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2423 |  |  |  | HR2422 (Lo-16bits)
2424 | VRG1:U>> setting (+UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2425 |  |  |  | HR2424 (Lo-16bits)
2426 | VRG1:U<< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2427 |  |  |  | HR2426 (Lo-16bits)
2428 | VRG1:U<< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2429 |  |  |  | HR2428 (Lo-16bits)
2430 | VRG1:U<< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2431 |  |  |  | HR2430 (Lo-16bits)
2432 | VRG1:U<< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2433 |  |  |  | HR2432 (Lo-16bits)
2434 | VRG1:U<< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2435 |  |  |  | HR2434 (Lo-16bits)
2436 | VRG1:U<< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2437 |  |  |  | HR2436 (Lo-16bits)
2438 | VRG1:U<< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2439 |  |  |  | HR2438 (Lo-16bits)
2440 | VRG1:U<< setting (-UTGT) | R(W) | 2 | FLOAT [0.1...30] (Hi-16bits)
2441 |  |  |  | HR2440 (Lo-16bits)
2442 | MEAS2:MEAS2 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
2443 |  |  |  | HR2442 (Lo-16bits)
2444 | IMERX:IL1 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2445 |  |  |  | HR2444 (Lo-16bits)
2446 | IMERX:IL1 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2447 |  |  |  | HR2446 (Lo-16bits)
2448 | IMERX:IL2 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2449 |  |  |  | HR2448 (Lo-16bits)
2450 | IMERX:IL2 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2451 |  |  |  | HR2450 (Lo-16bits)
2452 | IMERX:IL3 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2453 |  |  |  | HR2452 (Lo-16bits)
2454 | IMERX:IL3 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2455 |  |  |  | HR2454 (Lo-16bits)
2456 | IMERX:Positive sequence Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2457 |  |  |  | HR2456 (Lo-16bits)
2458 | IMERX:Positive sequence Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2459 |  |  |  | HR2458 (Lo-16bits)
2460 | IMERX:I01 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2461 |  |  |  | HR2460 (Lo-16bits)
2462 | IMERX:I01 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2463 |  |  |  | HR2462 (Lo-16bits)
2464 | IMERX:I02 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2465 |  |  |  | HR2464 (Lo-16bits)
2466 | IMERX:I02 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2467 |  |  |  | HR2466 (Lo-16bits)
2468 | IMERX:I01 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2469 |  |  |  | HR2468 (Lo-16bits)
2470 | IMERX:I01 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2471 |  |  |  | HR2470 (Lo-16bits)
2472 | IMERX:I02 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2473 |  |  |  | HR2472 (Lo-16bits)
2474 | IMERX:I02 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
2475 |  |  |  | HR2474 (Lo-16bits)
2476 | POW1:3PH Power factor | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2477 |  |  |  | HR2476 (Lo-16bits)
2478 | POW2:Export Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2479 |  |  |  | HR2478 (Lo-16bits)
2480 | POW2:Export Active Energy (P) kWh | R(W) | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2481 |  |  |  | HR2480 (Lo-16bits)
2482 | POW2:Import Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2483 |  |  |  | HR2482 (Lo-16bits)
2484 | POW2:Import Active Energy (P) kWh | R(W) | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2485 |  |  |  | HR2484 (Lo-16bits)
2486 | POW2:Active Energy (P) Export/Import balance MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2487 |  |  |  | HR2486 (Lo-16bits)
2488 | POW2:Active Energy (P) Export/Import balance kWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2489 |  |  |  | HR2488 (Lo-16bits)
2490 | POW2:Imported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2491 |  |  |  | HR2490 (Lo-16bits)
2492 | POW2:Imported (Q) while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2493 |  |  |  | HR2492 (Lo-16bits)
2494 | POW2:Imported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2495 |  |  |  | HR2494 (Lo-16bits)
2496 | POW2:Imported (Q) while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2497 |  |  |  | HR2496 (Lo-16bits)
2498 | POW2:Reactive Energy (Q) balance while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2499 |  |  |  | HR2498 (Lo-16bits)
2500 | POW2:Reactive Energy (Q) balance while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2501 |  |  |  | HR2500 (Lo-16bits)
2502 | POW2:Exported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2503 |  |  |  | HR2502 (Lo-16bits)
2504 | POW2:Exported (Q) while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2505 |  |  |  | HR2504 (Lo-16bits)
2506 | POW2:Exported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2507 |  |  |  | HR2506 (Lo-16bits)
2508 | POW2:Exported (Q) while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2509 |  |  |  | HR2508 (Lo-16bits)
2510 | POW2:Reactive Energy (Q) balance while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2511 |  |  |  | HR2510 (Lo-16bits)
2512 | POW2:Reactive Energy (Q) balance while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
2513 |  |  |  | HR2512 (Lo-16bits)
2514 | POW2:Reset 3ph energies | R(W) | 1 | 0=-;1=Reset
2515 | POW2:POW2 3PH Apparent power (S) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2516 |  |  |  | HR2515 (Lo-16bits)
2517 | POW2:POW2 3PH Apparent power (S MVA) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2518 |  |  |  | HR2517 (Lo-16bits)
2519 | POW2:POW2 3PH Active power (P) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2520 |  |  |  | HR2519 (Lo-16bits)
2521 | POW2:POW2 3PH Active power (P MW) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2522 |  |  |  | HR2521 (Lo-16bits)
2523 | POW2:POW2 3PH Reactive power (Q) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2524 |  |  |  | HR2523 (Lo-16bits)
2525 | POW2:POW2 3PH Reactive power (QMVar) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2526 |  |  |  | HR2525 (Lo-16bits)
2527 | POW2:POW2 3PH Tan(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2528 |  |  |  | HR2527 (Lo-16bits)
2529 | POW2:POW2 3PH Cos(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2530 |  |  |  | HR2529 (Lo-16bits)
2531 | POW2:3PH Power factor | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
2532 |  |  |  | HR2531 (Lo-16bits)
2533 | LOGIC1:Logic out 33-64 | R(W) | 2 | UINT32 [0...4294967295] (Hi-16bits)
2534 |  |  |  | HR2533 (Lo-16bits)
2535 | RTDIN:S1 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2536 |  |  |  | HR2535 (Lo-16bits)
2537 | RTDIN:S2 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2538 |  |  |  | HR2537 (Lo-16bits)
2539 | RTDIN:S3 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2540 |  |  |  | HR2539 (Lo-16bits)
2541 | RTDIN:S4 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2542 |  |  |  | HR2541 (Lo-16bits)
2543 | RTDIN:S5 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2544 |  |  |  | HR2543 (Lo-16bits)
2545 | RTDIN:S6 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2546 |  |  |  | HR2545 (Lo-16bits)
2547 | RTDIN:S7 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2548 |  |  |  | HR2547 (Lo-16bits)
2549 | RTDIN:S8 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2550 |  |  |  | HR2549 (Lo-16bits)
2551 | RTDIN:S9 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2552 |  |  |  | HR2551 (Lo-16bits)
2553 | RTDIN:S10 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2554 |  |  |  | HR2553 (Lo-16bits)
2555 | RTDIN:S11 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2556 |  |  |  | HR2555 (Lo-16bits)
2557 | RTDIN:S12 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2558 |  |  |  | HR2557 (Lo-16bits)
2559 | RTDIN:S13 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2560 |  |  |  | HR2559 (Lo-16bits)
2561 | RTDIN:S14 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2562 |  |  |  | HR2561 (Lo-16bits)
2563 | RTDIN:S15 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2564 |  |  |  | HR2563 (Lo-16bits)
2565 | RTDIN:S16 Filtered measurement | R | 2 | FLOAT [-200...2000] (Hi-16bits)
2566 |  |  |  | HR2565 (Lo-16bits)
2567 | SYN1:SYN1 Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
2568 |  |  |  | HR2567 (Lo-16bits)
2569 | SYN1:SYN1 Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
2570 |  |  |  | HR2569 (Lo-16bits)
2571 | SYN1:SYN1 Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
2572 |  |  |  | HR2571 (Lo-16bits)
2573 | GSYN:GSYN Nets Standstill | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
2574 |  |  |  | HR2573 (Lo-16bits)
2575 | GSYN:GSYN Nets Departing | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
2576 |  |  |  | HR2575 (Lo-16bits)
2577 | GSYN:GSYN Nets Enclosing | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
2578 |  |  |  | HR2577 (Lo-16bits)
2579 | PCS1:PCS1 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
2580 |  |  |  | HR2579 (Lo-16bits)
2581 | PCS2:PCS2 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
2582 |  |  |  | HR2581 (Lo-16bits)
2583 | PCS3:PCS3 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
2584 |  |  |  | HR2583 (Lo-16bits)
2585 | PCS4:PCS4 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
2586 |  |  |  | HR2585 (Lo-16bits)
2587 | PCS5:PCS5 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
2588 |  |  |  | HR2587 (Lo-16bits)
2589 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2590 |  |  |  | HR2589 (Lo-16bits)
2591 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2592 |  |  |  | HR2591 (Lo-16bits)
2593 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2594 |  |  |  | HR2593 (Lo-16bits)
2595 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2596 |  |  |  | HR2595 (Lo-16bits)
2597 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2598 |  |  |  | HR2597 (Lo-16bits)
2599 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2600 |  |  |  | HR2599 (Lo-16bits)
2601 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2602 |  |  |  | HR2601 (Lo-16bits)
2603 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2604 |  |  |  | HR2603 (Lo-16bits)
2605 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2606 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2607 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2608 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2609 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2610 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2611 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2612 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2613 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2614 |  |  |  | HR2613 (Lo-16bits)
2615 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2616 |  |  |  | HR2615 (Lo-16bits)
2617 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2618 |  |  |  | HR2617 (Lo-16bits)
2619 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2620 |  |  |  | HR2619 (Lo-16bits)
2621 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2622 |  |  |  | HR2621 (Lo-16bits)
2623 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2624 |  |  |  | HR2623 (Lo-16bits)
2625 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2626 |  |  |  | HR2625 (Lo-16bits)
2627 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2628 |  |  |  | HR2627 (Lo-16bits)
2629 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2630 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2631 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2632 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2633 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2634 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2635 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2636 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2637 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2638 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2639 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2640 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2641 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2642 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2643 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2644 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2645 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2646 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2647 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2648 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2649 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2650 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2651 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2652 | NOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2653 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2654 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2655 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2656 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2657 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2658 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2659 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2660 | NOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2661 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2662 |  |  |  | HR2661 (Lo-16bits)
2663 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2664 |  |  |  | HR2663 (Lo-16bits)
2665 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2666 |  |  |  | HR2665 (Lo-16bits)
2667 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2668 |  |  |  | HR2667 (Lo-16bits)
2669 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2670 |  |  |  | HR2669 (Lo-16bits)
2671 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2672 |  |  |  | HR2671 (Lo-16bits)
2673 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2674 |  |  |  | HR2673 (Lo-16bits)
2675 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2676 |  |  |  | HR2675 (Lo-16bits)
2677 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2678 |  |  |  | HR2677 (Lo-16bits)
2679 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2680 |  |  |  | HR2679 (Lo-16bits)
2681 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2682 |  |  |  | HR2681 (Lo-16bits)
2683 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2684 |  |  |  | HR2683 (Lo-16bits)
2685 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2686 |  |  |  | HR2685 (Lo-16bits)
2687 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2688 |  |  |  | HR2687 (Lo-16bits)
2689 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2690 |  |  |  | HR2689 (Lo-16bits)
2691 | NOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2692 |  |  |  | HR2691 (Lo-16bits)
2693 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2694 |  |  |  | HR2693 (Lo-16bits)
2695 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2696 |  |  |  | HR2695 (Lo-16bits)
2697 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2698 |  |  |  | HR2697 (Lo-16bits)
2699 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2700 |  |  |  | HR2699 (Lo-16bits)
2701 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2702 |  |  |  | HR2701 (Lo-16bits)
2703 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2704 |  |  |  | HR2703 (Lo-16bits)
2705 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2706 |  |  |  | HR2705 (Lo-16bits)
2707 | NOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2708 |  |  |  | HR2707 (Lo-16bits)
2709 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2710 |  |  |  | HR2709 (Lo-16bits)
2711 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2712 |  |  |  | HR2711 (Lo-16bits)
2713 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2714 |  |  |  | HR2713 (Lo-16bits)
2715 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2716 |  |  |  | HR2715 (Lo-16bits)
2717 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2718 |  |  |  | HR2717 (Lo-16bits)
2719 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2720 |  |  |  | HR2719 (Lo-16bits)
2721 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2722 |  |  |  | HR2721 (Lo-16bits)
2723 | NOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2724 |  |  |  | HR2723 (Lo-16bits)
2725 | NOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2726 | NOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2727 | NOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2728 | NOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2729 | NOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2730 | NOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2731 | NOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2732 | NOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2733 | NOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2734 |  |  |  | HR2733 (Lo-16bits)
2735 | NOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2736 |  |  |  | HR2735 (Lo-16bits)
2737 | NOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2738 |  |  |  | HR2737 (Lo-16bits)
2739 | NOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2740 |  |  |  | HR2739 (Lo-16bits)
2741 | NOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2742 |  |  |  | HR2741 (Lo-16bits)
2743 | NOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2744 |  |  |  | HR2743 (Lo-16bits)
2745 | NOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2746 |  |  |  | HR2745 (Lo-16bits)
2747 | NOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2748 |  |  |  | HR2747 (Lo-16bits)
2749 | NOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2750 | NOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2751 | NOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2752 | NOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2753 | NOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2754 | NOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2755 | NOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2756 | NOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2757 | NOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2758 |  |  |  | HR2757 (Lo-16bits)
2759 | NOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2760 |  |  |  | HR2759 (Lo-16bits)
2761 | NOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2762 |  |  |  | HR2761 (Lo-16bits)
2763 | NOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2764 |  |  |  | HR2763 (Lo-16bits)
2765 | NOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2766 |  |  |  | HR2765 (Lo-16bits)
2767 | NOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2768 |  |  |  | HR2767 (Lo-16bits)
2769 | NOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2770 |  |  |  | HR2769 (Lo-16bits)
2771 | NOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2772 |  |  |  | HR2771 (Lo-16bits)
2773 | NOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2774 | NOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2775 | NOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2776 | NOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2777 | NOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2778 | NOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2779 | NOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2780 | NOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2781 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2782 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2783 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2784 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2785 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2786 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2787 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2788 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2789 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2790 |  |  |  | HR2789 (Lo-16bits)
2791 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2792 |  |  |  | HR2791 (Lo-16bits)
2793 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2794 |  |  |  | HR2793 (Lo-16bits)
2795 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2796 |  |  |  | HR2795 (Lo-16bits)
2797 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2798 |  |  |  | HR2797 (Lo-16bits)
2799 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2800 |  |  |  | HR2799 (Lo-16bits)
2801 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2802 |  |  |  | HR2801 (Lo-16bits)
2803 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2804 |  |  |  | HR2803 (Lo-16bits)
2805 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2806 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2807 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2808 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2809 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2810 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2811 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2812 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2813 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2814 |  |  |  | HR2813 (Lo-16bits)
2815 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2816 |  |  |  | HR2815 (Lo-16bits)
2817 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2818 |  |  |  | HR2817 (Lo-16bits)
2819 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2820 |  |  |  | HR2819 (Lo-16bits)
2821 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2822 |  |  |  | HR2821 (Lo-16bits)
2823 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2824 |  |  |  | HR2823 (Lo-16bits)
2825 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2826 |  |  |  | HR2825 (Lo-16bits)
2827 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2828 |  |  |  | HR2827 (Lo-16bits)
2829 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2830 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2831 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2832 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2833 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2834 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2835 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2836 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2837 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2838 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2839 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2840 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2841 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2842 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2843 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2844 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2845 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2846 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2847 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2848 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2849 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2850 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2851 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2852 | NOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2853 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2854 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2855 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2856 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2857 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2858 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2859 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2860 | NOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
2861 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2862 |  |  |  | HR2861 (Lo-16bits)
2863 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2864 |  |  |  | HR2863 (Lo-16bits)
2865 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2866 |  |  |  | HR2865 (Lo-16bits)
2867 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2868 |  |  |  | HR2867 (Lo-16bits)
2869 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2870 |  |  |  | HR2869 (Lo-16bits)
2871 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2872 |  |  |  | HR2871 (Lo-16bits)
2873 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2874 |  |  |  | HR2873 (Lo-16bits)
2875 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2876 |  |  |  | HR2875 (Lo-16bits)
2877 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2878 |  |  |  | HR2877 (Lo-16bits)
2879 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2880 |  |  |  | HR2879 (Lo-16bits)
2881 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2882 |  |  |  | HR2881 (Lo-16bits)
2883 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2884 |  |  |  | HR2883 (Lo-16bits)
2885 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2886 |  |  |  | HR2885 (Lo-16bits)
2887 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2888 |  |  |  | HR2887 (Lo-16bits)
2889 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2890 |  |  |  | HR2889 (Lo-16bits)
2891 | NOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2892 |  |  |  | HR2891 (Lo-16bits)
2893 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2894 |  |  |  | HR2893 (Lo-16bits)
2895 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2896 |  |  |  | HR2895 (Lo-16bits)
2897 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2898 |  |  |  | HR2897 (Lo-16bits)
2899 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2900 |  |  |  | HR2899 (Lo-16bits)
2901 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2902 |  |  |  | HR2901 (Lo-16bits)
2903 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2904 |  |  |  | HR2903 (Lo-16bits)
2905 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2906 |  |  |  | HR2905 (Lo-16bits)
2907 | NOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
2908 |  |  |  | HR2907 (Lo-16bits)
2909 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2910 |  |  |  | HR2909 (Lo-16bits)
2911 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2912 |  |  |  | HR2911 (Lo-16bits)
2913 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2914 |  |  |  | HR2913 (Lo-16bits)
2915 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2916 |  |  |  | HR2915 (Lo-16bits)
2917 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2918 |  |  |  | HR2917 (Lo-16bits)
2919 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2920 |  |  |  | HR2919 (Lo-16bits)
2921 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2922 |  |  |  | HR2921 (Lo-16bits)
2923 | NOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2924 |  |  |  | HR2923 (Lo-16bits)
2925 | NOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2926 | NOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2927 | NOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2928 | NOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2929 | NOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2930 | NOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2931 | NOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2932 | NOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2933 | NOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2934 |  |  |  | HR2933 (Lo-16bits)
2935 | NOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2936 |  |  |  | HR2935 (Lo-16bits)
2937 | NOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2938 |  |  |  | HR2937 (Lo-16bits)
2939 | NOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2940 |  |  |  | HR2939 (Lo-16bits)
2941 | NOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2942 |  |  |  | HR2941 (Lo-16bits)
2943 | NOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2944 |  |  |  | HR2943 (Lo-16bits)
2945 | NOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2946 |  |  |  | HR2945 (Lo-16bits)
2947 | NOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2948 |  |  |  | HR2947 (Lo-16bits)
2949 | NOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2950 | NOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2951 | NOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2952 | NOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2953 | NOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2954 | NOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2955 | NOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2956 | NOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
2957 | NOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2958 |  |  |  | HR2957 (Lo-16bits)
2959 | NOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2960 |  |  |  | HR2959 (Lo-16bits)
2961 | NOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2962 |  |  |  | HR2961 (Lo-16bits)
2963 | NOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2964 |  |  |  | HR2963 (Lo-16bits)
2965 | NOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2966 |  |  |  | HR2965 (Lo-16bits)
2967 | NOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2968 |  |  |  | HR2967 (Lo-16bits)
2969 | NOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2970 |  |  |  | HR2969 (Lo-16bits)
2971 | NOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2972 |  |  |  | HR2971 (Lo-16bits)
2973 | NOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2974 | NOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2975 | NOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2976 | NOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2977 | NOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2978 | NOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2979 | NOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2980 | NOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
2981 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2982 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2983 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2984 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2985 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2986 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2987 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2988 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2989 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2990 |  |  |  | HR2989 (Lo-16bits)
2991 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2992 |  |  |  | HR2991 (Lo-16bits)
2993 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2994 |  |  |  | HR2993 (Lo-16bits)
2995 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2996 |  |  |  | HR2995 (Lo-16bits)
2997 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2998 |  |  |  | HR2997 (Lo-16bits)
2999 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3000 |  |  |  | HR2999 (Lo-16bits)
3001 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3002 |  |  |  | HR3001 (Lo-16bits)
3003 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3004 |  |  |  | HR3003 (Lo-16bits)
3005 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3006 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3007 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3008 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3009 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3010 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3011 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3012 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3013 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3014 |  |  |  | HR3013 (Lo-16bits)
3015 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3016 |  |  |  | HR3015 (Lo-16bits)
3017 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3018 |  |  |  | HR3017 (Lo-16bits)
3019 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3020 |  |  |  | HR3019 (Lo-16bits)
3021 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3022 |  |  |  | HR3021 (Lo-16bits)
3023 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3024 |  |  |  | HR3023 (Lo-16bits)
3025 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3026 |  |  |  | HR3025 (Lo-16bits)
3027 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3028 |  |  |  | HR3027 (Lo-16bits)
3029 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3030 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3031 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3032 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3033 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3034 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3035 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3036 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3037 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3038 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3039 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3040 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3041 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3042 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3043 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3044 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3045 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3046 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3047 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3048 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3049 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3050 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3051 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3052 | NOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3053 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3054 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3055 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3056 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3057 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3058 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3059 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3060 | NOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3061 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3062 |  |  |  | HR3061 (Lo-16bits)
3063 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3064 |  |  |  | HR3063 (Lo-16bits)
3065 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3066 |  |  |  | HR3065 (Lo-16bits)
3067 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3068 |  |  |  | HR3067 (Lo-16bits)
3069 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3070 |  |  |  | HR3069 (Lo-16bits)
3071 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3072 |  |  |  | HR3071 (Lo-16bits)
3073 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3074 |  |  |  | HR3073 (Lo-16bits)
3075 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3076 |  |  |  | HR3075 (Lo-16bits)
3077 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3078 |  |  |  | HR3077 (Lo-16bits)
3079 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3080 |  |  |  | HR3079 (Lo-16bits)
3081 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3082 |  |  |  | HR3081 (Lo-16bits)
3083 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3084 |  |  |  | HR3083 (Lo-16bits)
3085 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3086 |  |  |  | HR3085 (Lo-16bits)
3087 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3088 |  |  |  | HR3087 (Lo-16bits)
3089 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3090 |  |  |  | HR3089 (Lo-16bits)
3091 | NOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3092 |  |  |  | HR3091 (Lo-16bits)
3093 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3094 |  |  |  | HR3093 (Lo-16bits)
3095 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3096 |  |  |  | HR3095 (Lo-16bits)
3097 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3098 |  |  |  | HR3097 (Lo-16bits)
3099 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3100 |  |  |  | HR3099 (Lo-16bits)
3101 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3102 |  |  |  | HR3101 (Lo-16bits)
3103 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3104 |  |  |  | HR3103 (Lo-16bits)
3105 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3106 |  |  |  | HR3105 (Lo-16bits)
3107 | NOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3108 |  |  |  | HR3107 (Lo-16bits)
3109 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3110 |  |  |  | HR3109 (Lo-16bits)
3111 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3112 |  |  |  | HR3111 (Lo-16bits)
3113 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3114 |  |  |  | HR3113 (Lo-16bits)
3115 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3116 |  |  |  | HR3115 (Lo-16bits)
3117 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3118 |  |  |  | HR3117 (Lo-16bits)
3119 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3120 |  |  |  | HR3119 (Lo-16bits)
3121 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3122 |  |  |  | HR3121 (Lo-16bits)
3123 | NOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3124 |  |  |  | HR3123 (Lo-16bits)
3125 | NOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3126 | NOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3127 | NOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3128 | NOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3129 | NOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3130 | NOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3131 | NOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3132 | NOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3133 | NOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3134 |  |  |  | HR3133 (Lo-16bits)
3135 | NOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3136 |  |  |  | HR3135 (Lo-16bits)
3137 | NOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3138 |  |  |  | HR3137 (Lo-16bits)
3139 | NOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3140 |  |  |  | HR3139 (Lo-16bits)
3141 | NOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3142 |  |  |  | HR3141 (Lo-16bits)
3143 | NOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3144 |  |  |  | HR3143 (Lo-16bits)
3145 | NOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3146 |  |  |  | HR3145 (Lo-16bits)
3147 | NOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3148 |  |  |  | HR3147 (Lo-16bits)
3149 | NOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3150 | NOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3151 | NOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3152 | NOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3153 | NOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3154 | NOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3155 | NOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3156 | NOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3157 | NOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3158 |  |  |  | HR3157 (Lo-16bits)
3159 | NOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3160 |  |  |  | HR3159 (Lo-16bits)
3161 | NOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3162 |  |  |  | HR3161 (Lo-16bits)
3163 | NOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3164 |  |  |  | HR3163 (Lo-16bits)
3165 | NOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3166 |  |  |  | HR3165 (Lo-16bits)
3167 | NOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3168 |  |  |  | HR3167 (Lo-16bits)
3169 | NOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3170 |  |  |  | HR3169 (Lo-16bits)
3171 | NOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3172 |  |  |  | HR3171 (Lo-16bits)
3173 | NOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3174 | NOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3175 | NOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3176 | NOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3177 | NOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3178 | NOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3179 | NOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3180 | NOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3181 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3182 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3183 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3184 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3185 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3186 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3187 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3188 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3189 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3190 |  |  |  | HR3189 (Lo-16bits)
3191 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3192 |  |  |  | HR3191 (Lo-16bits)
3193 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3194 |  |  |  | HR3193 (Lo-16bits)
3195 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3196 |  |  |  | HR3195 (Lo-16bits)
3197 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3198 |  |  |  | HR3197 (Lo-16bits)
3199 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3200 |  |  |  | HR3199 (Lo-16bits)
3201 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3202 |  |  |  | HR3201 (Lo-16bits)
3203 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3204 |  |  |  | HR3203 (Lo-16bits)
3205 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3206 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3207 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3208 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3209 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3210 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3211 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3212 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3213 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3214 |  |  |  | HR3213 (Lo-16bits)
3215 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3216 |  |  |  | HR3215 (Lo-16bits)
3217 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3218 |  |  |  | HR3217 (Lo-16bits)
3219 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3220 |  |  |  | HR3219 (Lo-16bits)
3221 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3222 |  |  |  | HR3221 (Lo-16bits)
3223 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3224 |  |  |  | HR3223 (Lo-16bits)
3225 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3226 |  |  |  | HR3225 (Lo-16bits)
3227 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3228 |  |  |  | HR3227 (Lo-16bits)
3229 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3230 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3231 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3232 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3233 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3234 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3235 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3236 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3237 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3238 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3239 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3240 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3241 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3242 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3243 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3244 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3245 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3246 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3247 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3248 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3249 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3250 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3251 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3252 | NOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3253 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3254 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3255 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3256 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3257 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3258 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3259 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3260 | NOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3261 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3262 |  |  |  | HR3261 (Lo-16bits)
3263 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3264 |  |  |  | HR3263 (Lo-16bits)
3265 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3266 |  |  |  | HR3265 (Lo-16bits)
3267 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3268 |  |  |  | HR3267 (Lo-16bits)
3269 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3270 |  |  |  | HR3269 (Lo-16bits)
3271 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3272 |  |  |  | HR3271 (Lo-16bits)
3273 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3274 |  |  |  | HR3273 (Lo-16bits)
3275 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3276 |  |  |  | HR3275 (Lo-16bits)
3277 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3278 |  |  |  | HR3277 (Lo-16bits)
3279 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3280 |  |  |  | HR3279 (Lo-16bits)
3281 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3282 |  |  |  | HR3281 (Lo-16bits)
3283 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3284 |  |  |  | HR3283 (Lo-16bits)
3285 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3286 |  |  |  | HR3285 (Lo-16bits)
3287 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3288 |  |  |  | HR3287 (Lo-16bits)
3289 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3290 |  |  |  | HR3289 (Lo-16bits)
3291 | NOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3292 |  |  |  | HR3291 (Lo-16bits)
3293 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3294 |  |  |  | HR3293 (Lo-16bits)
3295 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3296 |  |  |  | HR3295 (Lo-16bits)
3297 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3298 |  |  |  | HR3297 (Lo-16bits)
3299 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3300 |  |  |  | HR3299 (Lo-16bits)
3301 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3302 |  |  |  | HR3301 (Lo-16bits)
3303 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3304 |  |  |  | HR3303 (Lo-16bits)
3305 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3306 |  |  |  | HR3305 (Lo-16bits)
3307 | NOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3308 |  |  |  | HR3307 (Lo-16bits)
3309 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3310 |  |  |  | HR3309 (Lo-16bits)
3311 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3312 |  |  |  | HR3311 (Lo-16bits)
3313 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3314 |  |  |  | HR3313 (Lo-16bits)
3315 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3316 |  |  |  | HR3315 (Lo-16bits)
3317 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3318 |  |  |  | HR3317 (Lo-16bits)
3319 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3320 |  |  |  | HR3319 (Lo-16bits)
3321 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3322 |  |  |  | HR3321 (Lo-16bits)
3323 | NOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3324 |  |  |  | HR3323 (Lo-16bits)
3325 | NOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3326 | NOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3327 | NOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3328 | NOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3329 | NOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3330 | NOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3331 | NOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3332 | NOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3333 | NOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3334 |  |  |  | HR3333 (Lo-16bits)
3335 | NOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3336 |  |  |  | HR3335 (Lo-16bits)
3337 | NOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3338 |  |  |  | HR3337 (Lo-16bits)
3339 | NOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3340 |  |  |  | HR3339 (Lo-16bits)
3341 | NOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3342 |  |  |  | HR3341 (Lo-16bits)
3343 | NOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3344 |  |  |  | HR3343 (Lo-16bits)
3345 | NOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3346 |  |  |  | HR3345 (Lo-16bits)
3347 | NOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3348 |  |  |  | HR3347 (Lo-16bits)
3349 | NOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3350 | NOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3351 | NOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3352 | NOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3353 | NOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3354 | NOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3355 | NOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3356 | NOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3357 | NOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3358 |  |  |  | HR3357 (Lo-16bits)
3359 | NOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3360 |  |  |  | HR3359 (Lo-16bits)
3361 | NOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3362 |  |  |  | HR3361 (Lo-16bits)
3363 | NOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3364 |  |  |  | HR3363 (Lo-16bits)
3365 | NOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3366 |  |  |  | HR3365 (Lo-16bits)
3367 | NOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3368 |  |  |  | HR3367 (Lo-16bits)
3369 | NOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3370 |  |  |  | HR3369 (Lo-16bits)
3371 | NOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3372 |  |  |  | HR3371 (Lo-16bits)
3373 | NOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3374 | NOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3375 | NOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3376 | NOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3377 | NOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3378 | NOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3379 | NOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3380 | NOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3381 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3382 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3383 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3384 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3385 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3386 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3387 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3388 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3389 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3390 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3391 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3392 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3393 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3394 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3395 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3396 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3397 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3398 |  |  |  | HR3397 (Lo-16bits)
3399 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3400 |  |  |  | HR3399 (Lo-16bits)
3401 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3402 |  |  |  | HR3401 (Lo-16bits)
3403 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3404 |  |  |  | HR3403 (Lo-16bits)
3405 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3406 |  |  |  | HR3405 (Lo-16bits)
3407 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3408 |  |  |  | HR3407 (Lo-16bits)
3409 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3410 |  |  |  | HR3409 (Lo-16bits)
3411 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3412 |  |  |  | HR3411 (Lo-16bits)
3413 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3414 |  |  |  | HR3413 (Lo-16bits)
3415 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3416 |  |  |  | HR3415 (Lo-16bits)
3417 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3418 |  |  |  | HR3417 (Lo-16bits)
3419 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3420 |  |  |  | HR3419 (Lo-16bits)
3421 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3422 |  |  |  | HR3421 (Lo-16bits)
3423 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3424 |  |  |  | HR3423 (Lo-16bits)
3425 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3426 |  |  |  | HR3425 (Lo-16bits)
3427 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3428 |  |  |  | HR3427 (Lo-16bits)
3429 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3430 |  |  |  | HR3429 (Lo-16bits)
3431 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3432 |  |  |  | HR3431 (Lo-16bits)
3433 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3434 |  |  |  | HR3433 (Lo-16bits)
3435 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3436 |  |  |  | HR3435 (Lo-16bits)
3437 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3438 |  |  |  | HR3437 (Lo-16bits)
3439 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3440 |  |  |  | HR3439 (Lo-16bits)
3441 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3442 |  |  |  | HR3441 (Lo-16bits)
3443 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3444 |  |  |  | HR3443 (Lo-16bits)
3445 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3446 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3447 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3448 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3449 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3450 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3451 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3452 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3453 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3454 |  |  |  | HR3453 (Lo-16bits)
3455 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3456 |  |  |  | HR3455 (Lo-16bits)
3457 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3458 |  |  |  | HR3457 (Lo-16bits)
3459 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3460 |  |  |  | HR3459 (Lo-16bits)
3461 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3462 |  |  |  | HR3461 (Lo-16bits)
3463 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3464 |  |  |  | HR3463 (Lo-16bits)
3465 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3466 |  |  |  | HR3465 (Lo-16bits)
3467 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3468 |  |  |  | HR3467 (Lo-16bits)
3469 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3470 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3471 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3472 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3473 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3474 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3475 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3476 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3477 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3478 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3479 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3480 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3481 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3482 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3483 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3484 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3485 | DOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3486 | DOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3487 | DOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3488 | DOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3489 | DOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3490 | DOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3491 | DOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3492 | DOC1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3493 | DOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3494 | DOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3495 | DOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3496 | DOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3497 | DOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3498 | DOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3499 | DOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3500 | DOC1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3501 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3502 |  |  |  | HR3501 (Lo-16bits)
3503 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3504 |  |  |  | HR3503 (Lo-16bits)
3505 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3506 |  |  |  | HR3505 (Lo-16bits)
3507 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3508 |  |  |  | HR3507 (Lo-16bits)
3509 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3510 |  |  |  | HR3509 (Lo-16bits)
3511 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3512 |  |  |  | HR3511 (Lo-16bits)
3513 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3514 |  |  |  | HR3513 (Lo-16bits)
3515 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3516 |  |  |  | HR3515 (Lo-16bits)
3517 | DOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3518 |  |  |  | HR3517 (Lo-16bits)
3519 | DOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3520 |  |  |  | HR3519 (Lo-16bits)
3521 | DOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3522 |  |  |  | HR3521 (Lo-16bits)
3523 | DOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3524 |  |  |  | HR3523 (Lo-16bits)
3525 | DOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3526 |  |  |  | HR3525 (Lo-16bits)
3527 | DOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3528 |  |  |  | HR3527 (Lo-16bits)
3529 | DOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3530 |  |  |  | HR3529 (Lo-16bits)
3531 | DOC1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3532 |  |  |  | HR3531 (Lo-16bits)
3533 | DOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3534 |  |  |  | HR3533 (Lo-16bits)
3535 | DOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3536 |  |  |  | HR3535 (Lo-16bits)
3537 | DOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3538 |  |  |  | HR3537 (Lo-16bits)
3539 | DOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3540 |  |  |  | HR3539 (Lo-16bits)
3541 | DOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3542 |  |  |  | HR3541 (Lo-16bits)
3543 | DOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3544 |  |  |  | HR3543 (Lo-16bits)
3545 | DOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3546 |  |  |  | HR3545 (Lo-16bits)
3547 | DOC1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3548 |  |  |  | HR3547 (Lo-16bits)
3549 | DOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3550 |  |  |  | HR3549 (Lo-16bits)
3551 | DOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3552 |  |  |  | HR3551 (Lo-16bits)
3553 | DOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3554 |  |  |  | HR3553 (Lo-16bits)
3555 | DOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3556 |  |  |  | HR3555 (Lo-16bits)
3557 | DOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3558 |  |  |  | HR3557 (Lo-16bits)
3559 | DOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3560 |  |  |  | HR3559 (Lo-16bits)
3561 | DOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3562 |  |  |  | HR3561 (Lo-16bits)
3563 | DOC1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3564 |  |  |  | HR3563 (Lo-16bits)
3565 | DOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3566 | DOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3567 | DOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3568 | DOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3569 | DOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3570 | DOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3571 | DOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3572 | DOC1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3573 | DOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3574 |  |  |  | HR3573 (Lo-16bits)
3575 | DOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3576 |  |  |  | HR3575 (Lo-16bits)
3577 | DOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3578 |  |  |  | HR3577 (Lo-16bits)
3579 | DOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3580 |  |  |  | HR3579 (Lo-16bits)
3581 | DOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3582 |  |  |  | HR3581 (Lo-16bits)
3583 | DOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3584 |  |  |  | HR3583 (Lo-16bits)
3585 | DOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3586 |  |  |  | HR3585 (Lo-16bits)
3587 | DOC1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3588 |  |  |  | HR3587 (Lo-16bits)
3589 | DOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3590 | DOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3591 | DOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3592 | DOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3593 | DOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3594 | DOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3595 | DOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3596 | DOC1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3597 | DOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3598 |  |  |  | HR3597 (Lo-16bits)
3599 | DOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3600 |  |  |  | HR3599 (Lo-16bits)
3601 | DOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3602 |  |  |  | HR3601 (Lo-16bits)
3603 | DOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3604 |  |  |  | HR3603 (Lo-16bits)
3605 | DOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3606 |  |  |  | HR3605 (Lo-16bits)
3607 | DOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3608 |  |  |  | HR3607 (Lo-16bits)
3609 | DOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3610 |  |  |  | HR3609 (Lo-16bits)
3611 | DOC1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3612 |  |  |  | HR3611 (Lo-16bits)
3613 | DOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3614 | DOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3615 | DOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3616 | DOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3617 | DOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3618 | DOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3619 | DOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3620 | DOC1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3621 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3622 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3623 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3624 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3625 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3626 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3627 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3628 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3629 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3630 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3631 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3632 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3633 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3634 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3635 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3636 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3637 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3638 |  |  |  | HR3637 (Lo-16bits)
3639 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3640 |  |  |  | HR3639 (Lo-16bits)
3641 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3642 |  |  |  | HR3641 (Lo-16bits)
3643 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3644 |  |  |  | HR3643 (Lo-16bits)
3645 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3646 |  |  |  | HR3645 (Lo-16bits)
3647 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3648 |  |  |  | HR3647 (Lo-16bits)
3649 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3650 |  |  |  | HR3649 (Lo-16bits)
3651 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3652 |  |  |  | HR3651 (Lo-16bits)
3653 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3654 |  |  |  | HR3653 (Lo-16bits)
3655 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3656 |  |  |  | HR3655 (Lo-16bits)
3657 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3658 |  |  |  | HR3657 (Lo-16bits)
3659 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3660 |  |  |  | HR3659 (Lo-16bits)
3661 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3662 |  |  |  | HR3661 (Lo-16bits)
3663 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3664 |  |  |  | HR3663 (Lo-16bits)
3665 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3666 |  |  |  | HR3665 (Lo-16bits)
3667 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3668 |  |  |  | HR3667 (Lo-16bits)
3669 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3670 |  |  |  | HR3669 (Lo-16bits)
3671 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3672 |  |  |  | HR3671 (Lo-16bits)
3673 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3674 |  |  |  | HR3673 (Lo-16bits)
3675 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3676 |  |  |  | HR3675 (Lo-16bits)
3677 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3678 |  |  |  | HR3677 (Lo-16bits)
3679 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3680 |  |  |  | HR3679 (Lo-16bits)
3681 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3682 |  |  |  | HR3681 (Lo-16bits)
3683 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3684 |  |  |  | HR3683 (Lo-16bits)
3685 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3686 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3687 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3688 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3689 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3690 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3691 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3692 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3693 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3694 |  |  |  | HR3693 (Lo-16bits)
3695 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3696 |  |  |  | HR3695 (Lo-16bits)
3697 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3698 |  |  |  | HR3697 (Lo-16bits)
3699 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3700 |  |  |  | HR3699 (Lo-16bits)
3701 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3702 |  |  |  | HR3701 (Lo-16bits)
3703 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3704 |  |  |  | HR3703 (Lo-16bits)
3705 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3706 |  |  |  | HR3705 (Lo-16bits)
3707 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3708 |  |  |  | HR3707 (Lo-16bits)
3709 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3710 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3711 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3712 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3713 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3714 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3715 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3716 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3717 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3718 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3719 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3720 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3721 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3722 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3723 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3724 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3725 | DOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3726 | DOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3727 | DOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3728 | DOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3729 | DOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3730 | DOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3731 | DOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3732 | DOC2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3733 | DOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3734 | DOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3735 | DOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3736 | DOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3737 | DOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3738 | DOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3739 | DOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3740 | DOC2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3741 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3742 |  |  |  | HR3741 (Lo-16bits)
3743 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3744 |  |  |  | HR3743 (Lo-16bits)
3745 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3746 |  |  |  | HR3745 (Lo-16bits)
3747 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3748 |  |  |  | HR3747 (Lo-16bits)
3749 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3750 |  |  |  | HR3749 (Lo-16bits)
3751 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3752 |  |  |  | HR3751 (Lo-16bits)
3753 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3754 |  |  |  | HR3753 (Lo-16bits)
3755 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3756 |  |  |  | HR3755 (Lo-16bits)
3757 | DOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3758 |  |  |  | HR3757 (Lo-16bits)
3759 | DOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3760 |  |  |  | HR3759 (Lo-16bits)
3761 | DOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3762 |  |  |  | HR3761 (Lo-16bits)
3763 | DOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3764 |  |  |  | HR3763 (Lo-16bits)
3765 | DOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3766 |  |  |  | HR3765 (Lo-16bits)
3767 | DOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3768 |  |  |  | HR3767 (Lo-16bits)
3769 | DOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3770 |  |  |  | HR3769 (Lo-16bits)
3771 | DOC2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3772 |  |  |  | HR3771 (Lo-16bits)
3773 | DOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3774 |  |  |  | HR3773 (Lo-16bits)
3775 | DOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3776 |  |  |  | HR3775 (Lo-16bits)
3777 | DOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3778 |  |  |  | HR3777 (Lo-16bits)
3779 | DOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3780 |  |  |  | HR3779 (Lo-16bits)
3781 | DOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3782 |  |  |  | HR3781 (Lo-16bits)
3783 | DOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3784 |  |  |  | HR3783 (Lo-16bits)
3785 | DOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3786 |  |  |  | HR3785 (Lo-16bits)
3787 | DOC2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
3788 |  |  |  | HR3787 (Lo-16bits)
3789 | DOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3790 |  |  |  | HR3789 (Lo-16bits)
3791 | DOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3792 |  |  |  | HR3791 (Lo-16bits)
3793 | DOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3794 |  |  |  | HR3793 (Lo-16bits)
3795 | DOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3796 |  |  |  | HR3795 (Lo-16bits)
3797 | DOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3798 |  |  |  | HR3797 (Lo-16bits)
3799 | DOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3800 |  |  |  | HR3799 (Lo-16bits)
3801 | DOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3802 |  |  |  | HR3801 (Lo-16bits)
3803 | DOC2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3804 |  |  |  | HR3803 (Lo-16bits)
3805 | DOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3806 | DOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3807 | DOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3808 | DOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3809 | DOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3810 | DOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3811 | DOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3812 | DOC2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3813 | DOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3814 |  |  |  | HR3813 (Lo-16bits)
3815 | DOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3816 |  |  |  | HR3815 (Lo-16bits)
3817 | DOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3818 |  |  |  | HR3817 (Lo-16bits)
3819 | DOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3820 |  |  |  | HR3819 (Lo-16bits)
3821 | DOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3822 |  |  |  | HR3821 (Lo-16bits)
3823 | DOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3824 |  |  |  | HR3823 (Lo-16bits)
3825 | DOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3826 |  |  |  | HR3825 (Lo-16bits)
3827 | DOC2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3828 |  |  |  | HR3827 (Lo-16bits)
3829 | DOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3830 | DOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3831 | DOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3832 | DOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3833 | DOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3834 | DOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3835 | DOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3836 | DOC2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
3837 | DOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3838 |  |  |  | HR3837 (Lo-16bits)
3839 | DOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3840 |  |  |  | HR3839 (Lo-16bits)
3841 | DOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3842 |  |  |  | HR3841 (Lo-16bits)
3843 | DOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3844 |  |  |  | HR3843 (Lo-16bits)
3845 | DOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3846 |  |  |  | HR3845 (Lo-16bits)
3847 | DOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3848 |  |  |  | HR3847 (Lo-16bits)
3849 | DOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3850 |  |  |  | HR3849 (Lo-16bits)
3851 | DOC2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3852 |  |  |  | HR3851 (Lo-16bits)
3853 | DOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3854 | DOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3855 | DOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3856 | DOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3857 | DOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3858 | DOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3859 | DOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3860 | DOC2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
3861 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3862 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3863 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3864 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3865 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3866 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3867 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3868 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3869 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3870 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3871 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3872 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3873 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3874 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3875 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3876 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3877 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3878 |  |  |  | HR3877 (Lo-16bits)
3879 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3880 |  |  |  | HR3879 (Lo-16bits)
3881 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3882 |  |  |  | HR3881 (Lo-16bits)
3883 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3884 |  |  |  | HR3883 (Lo-16bits)
3885 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3886 |  |  |  | HR3885 (Lo-16bits)
3887 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3888 |  |  |  | HR3887 (Lo-16bits)
3889 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3890 |  |  |  | HR3889 (Lo-16bits)
3891 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3892 |  |  |  | HR3891 (Lo-16bits)
3893 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3894 |  |  |  | HR3893 (Lo-16bits)
3895 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3896 |  |  |  | HR3895 (Lo-16bits)
3897 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3898 |  |  |  | HR3897 (Lo-16bits)
3899 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3900 |  |  |  | HR3899 (Lo-16bits)
3901 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3902 |  |  |  | HR3901 (Lo-16bits)
3903 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3904 |  |  |  | HR3903 (Lo-16bits)
3905 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3906 |  |  |  | HR3905 (Lo-16bits)
3907 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3908 |  |  |  | HR3907 (Lo-16bits)
3909 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3910 |  |  |  | HR3909 (Lo-16bits)
3911 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3912 |  |  |  | HR3911 (Lo-16bits)
3913 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3914 |  |  |  | HR3913 (Lo-16bits)
3915 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3916 |  |  |  | HR3915 (Lo-16bits)
3917 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3918 |  |  |  | HR3917 (Lo-16bits)
3919 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3920 |  |  |  | HR3919 (Lo-16bits)
3921 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3922 |  |  |  | HR3921 (Lo-16bits)
3923 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3924 |  |  |  | HR3923 (Lo-16bits)
3925 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3926 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3927 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3928 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3929 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3930 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3931 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3932 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3933 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3934 |  |  |  | HR3933 (Lo-16bits)
3935 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3936 |  |  |  | HR3935 (Lo-16bits)
3937 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3938 |  |  |  | HR3937 (Lo-16bits)
3939 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3940 |  |  |  | HR3939 (Lo-16bits)
3941 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3942 |  |  |  | HR3941 (Lo-16bits)
3943 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3944 |  |  |  | HR3943 (Lo-16bits)
3945 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3946 |  |  |  | HR3945 (Lo-16bits)
3947 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3948 |  |  |  | HR3947 (Lo-16bits)
3949 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3950 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3951 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3952 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3953 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3954 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3955 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3956 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3957 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3958 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3959 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3960 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3961 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3962 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3963 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3964 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3965 | DOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3966 | DOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3967 | DOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3968 | DOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3969 | DOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3970 | DOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3971 | DOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3972 | DOC3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3973 | DOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3974 | DOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3975 | DOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3976 | DOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3977 | DOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3978 | DOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3979 | DOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3980 | DOC3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
3981 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3982 |  |  |  | HR3981 (Lo-16bits)
3983 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3984 |  |  |  | HR3983 (Lo-16bits)
3985 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3986 |  |  |  | HR3985 (Lo-16bits)
3987 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3988 |  |  |  | HR3987 (Lo-16bits)
3989 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3990 |  |  |  | HR3989 (Lo-16bits)
3991 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3992 |  |  |  | HR3991 (Lo-16bits)
3993 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3994 |  |  |  | HR3993 (Lo-16bits)
3995 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3996 |  |  |  | HR3995 (Lo-16bits)
3997 | DOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3998 |  |  |  | HR3997 (Lo-16bits)
3999 | DOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4000 |  |  |  | HR3999 (Lo-16bits)
4001 | DOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4002 |  |  |  | HR4001 (Lo-16bits)
4003 | DOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4004 |  |  |  | HR4003 (Lo-16bits)
4005 | DOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4006 |  |  |  | HR4005 (Lo-16bits)
4007 | DOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4008 |  |  |  | HR4007 (Lo-16bits)
4009 | DOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4010 |  |  |  | HR4009 (Lo-16bits)
4011 | DOC3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4012 |  |  |  | HR4011 (Lo-16bits)
4013 | DOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4014 |  |  |  | HR4013 (Lo-16bits)
4015 | DOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4016 |  |  |  | HR4015 (Lo-16bits)
4017 | DOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4018 |  |  |  | HR4017 (Lo-16bits)
4019 | DOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4020 |  |  |  | HR4019 (Lo-16bits)
4021 | DOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4022 |  |  |  | HR4021 (Lo-16bits)
4023 | DOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4024 |  |  |  | HR4023 (Lo-16bits)
4025 | DOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4026 |  |  |  | HR4025 (Lo-16bits)
4027 | DOC3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4028 |  |  |  | HR4027 (Lo-16bits)
4029 | DOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4030 |  |  |  | HR4029 (Lo-16bits)
4031 | DOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4032 |  |  |  | HR4031 (Lo-16bits)
4033 | DOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4034 |  |  |  | HR4033 (Lo-16bits)
4035 | DOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4036 |  |  |  | HR4035 (Lo-16bits)
4037 | DOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4038 |  |  |  | HR4037 (Lo-16bits)
4039 | DOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4040 |  |  |  | HR4039 (Lo-16bits)
4041 | DOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4042 |  |  |  | HR4041 (Lo-16bits)
4043 | DOC3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4044 |  |  |  | HR4043 (Lo-16bits)
4045 | DOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4046 | DOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4047 | DOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4048 | DOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4049 | DOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4050 | DOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4051 | DOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4052 | DOC3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4053 | DOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4054 |  |  |  | HR4053 (Lo-16bits)
4055 | DOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4056 |  |  |  | HR4055 (Lo-16bits)
4057 | DOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4058 |  |  |  | HR4057 (Lo-16bits)
4059 | DOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4060 |  |  |  | HR4059 (Lo-16bits)
4061 | DOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4062 |  |  |  | HR4061 (Lo-16bits)
4063 | DOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4064 |  |  |  | HR4063 (Lo-16bits)
4065 | DOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4066 |  |  |  | HR4065 (Lo-16bits)
4067 | DOC3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4068 |  |  |  | HR4067 (Lo-16bits)
4069 | DOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4070 | DOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4071 | DOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4072 | DOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4073 | DOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4074 | DOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4075 | DOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4076 | DOC3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4077 | DOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4078 |  |  |  | HR4077 (Lo-16bits)
4079 | DOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4080 |  |  |  | HR4079 (Lo-16bits)
4081 | DOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4082 |  |  |  | HR4081 (Lo-16bits)
4083 | DOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4084 |  |  |  | HR4083 (Lo-16bits)
4085 | DOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4086 |  |  |  | HR4085 (Lo-16bits)
4087 | DOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4088 |  |  |  | HR4087 (Lo-16bits)
4089 | DOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4090 |  |  |  | HR4089 (Lo-16bits)
4091 | DOC3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4092 |  |  |  | HR4091 (Lo-16bits)
4093 | DOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4094 | DOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4095 | DOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4096 | DOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4097 | DOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4098 | DOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4099 | DOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4100 | DOC3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4101 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4102 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4103 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4104 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4105 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4106 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4107 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4108 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4109 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
4110 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
4111 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
4112 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
4113 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
4114 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
4115 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
4116 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
4117 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
4118 |  |  |  | HR4117 (Lo-16bits)
4119 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
4120 |  |  |  | HR4119 (Lo-16bits)
4121 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
4122 |  |  |  | HR4121 (Lo-16bits)
4123 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
4124 |  |  |  | HR4123 (Lo-16bits)
4125 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
4126 |  |  |  | HR4125 (Lo-16bits)
4127 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
4128 |  |  |  | HR4127 (Lo-16bits)
4129 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
4130 |  |  |  | HR4129 (Lo-16bits)
4131 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
4132 |  |  |  | HR4131 (Lo-16bits)
4133 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
4134 |  |  |  | HR4133 (Lo-16bits)
4135 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
4136 |  |  |  | HR4135 (Lo-16bits)
4137 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
4138 |  |  |  | HR4137 (Lo-16bits)
4139 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
4140 |  |  |  | HR4139 (Lo-16bits)
4141 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
4142 |  |  |  | HR4141 (Lo-16bits)
4143 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
4144 |  |  |  | HR4143 (Lo-16bits)
4145 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
4146 |  |  |  | HR4145 (Lo-16bits)
4147 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
4148 |  |  |  | HR4147 (Lo-16bits)
4149 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
4150 |  |  |  | HR4149 (Lo-16bits)
4151 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
4152 |  |  |  | HR4151 (Lo-16bits)
4153 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
4154 |  |  |  | HR4153 (Lo-16bits)
4155 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
4156 |  |  |  | HR4155 (Lo-16bits)
4157 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
4158 |  |  |  | HR4157 (Lo-16bits)
4159 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
4160 |  |  |  | HR4159 (Lo-16bits)
4161 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
4162 |  |  |  | HR4161 (Lo-16bits)
4163 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
4164 |  |  |  | HR4163 (Lo-16bits)
4165 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4166 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4167 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4168 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4169 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4170 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4171 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4172 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4173 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4174 |  |  |  | HR4173 (Lo-16bits)
4175 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4176 |  |  |  | HR4175 (Lo-16bits)
4177 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4178 |  |  |  | HR4177 (Lo-16bits)
4179 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4180 |  |  |  | HR4179 (Lo-16bits)
4181 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4182 |  |  |  | HR4181 (Lo-16bits)
4183 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4184 |  |  |  | HR4183 (Lo-16bits)
4185 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4186 |  |  |  | HR4185 (Lo-16bits)
4187 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4188 |  |  |  | HR4187 (Lo-16bits)
4189 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4190 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4191 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4192 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4193 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4194 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4195 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4196 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4197 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4198 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4199 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4200 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4201 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4202 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4203 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4204 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4205 | DOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4206 | DOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4207 | DOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4208 | DOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4209 | DOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4210 | DOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4211 | DOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4212 | DOC4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4213 | DOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4214 | DOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4215 | DOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4216 | DOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4217 | DOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4218 | DOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4219 | DOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4220 | DOC4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4221 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4222 |  |  |  | HR4221 (Lo-16bits)
4223 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4224 |  |  |  | HR4223 (Lo-16bits)
4225 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4226 |  |  |  | HR4225 (Lo-16bits)
4227 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4228 |  |  |  | HR4227 (Lo-16bits)
4229 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4230 |  |  |  | HR4229 (Lo-16bits)
4231 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4232 |  |  |  | HR4231 (Lo-16bits)
4233 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4234 |  |  |  | HR4233 (Lo-16bits)
4235 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4236 |  |  |  | HR4235 (Lo-16bits)
4237 | DOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4238 |  |  |  | HR4237 (Lo-16bits)
4239 | DOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4240 |  |  |  | HR4239 (Lo-16bits)
4241 | DOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4242 |  |  |  | HR4241 (Lo-16bits)
4243 | DOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4244 |  |  |  | HR4243 (Lo-16bits)
4245 | DOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4246 |  |  |  | HR4245 (Lo-16bits)
4247 | DOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4248 |  |  |  | HR4247 (Lo-16bits)
4249 | DOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4250 |  |  |  | HR4249 (Lo-16bits)
4251 | DOC4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4252 |  |  |  | HR4251 (Lo-16bits)
4253 | DOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4254 |  |  |  | HR4253 (Lo-16bits)
4255 | DOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4256 |  |  |  | HR4255 (Lo-16bits)
4257 | DOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4258 |  |  |  | HR4257 (Lo-16bits)
4259 | DOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4260 |  |  |  | HR4259 (Lo-16bits)
4261 | DOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4262 |  |  |  | HR4261 (Lo-16bits)
4263 | DOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4264 |  |  |  | HR4263 (Lo-16bits)
4265 | DOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4266 |  |  |  | HR4265 (Lo-16bits)
4267 | DOC4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4268 |  |  |  | HR4267 (Lo-16bits)
4269 | DOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4270 |  |  |  | HR4269 (Lo-16bits)
4271 | DOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4272 |  |  |  | HR4271 (Lo-16bits)
4273 | DOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4274 |  |  |  | HR4273 (Lo-16bits)
4275 | DOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4276 |  |  |  | HR4275 (Lo-16bits)
4277 | DOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4278 |  |  |  | HR4277 (Lo-16bits)
4279 | DOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4280 |  |  |  | HR4279 (Lo-16bits)
4281 | DOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4282 |  |  |  | HR4281 (Lo-16bits)
4283 | DOC4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4284 |  |  |  | HR4283 (Lo-16bits)
4285 | DOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4286 | DOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4287 | DOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4288 | DOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4289 | DOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4290 | DOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4291 | DOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4292 | DOC4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4293 | DOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4294 |  |  |  | HR4293 (Lo-16bits)
4295 | DOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4296 |  |  |  | HR4295 (Lo-16bits)
4297 | DOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4298 |  |  |  | HR4297 (Lo-16bits)
4299 | DOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4300 |  |  |  | HR4299 (Lo-16bits)
4301 | DOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4302 |  |  |  | HR4301 (Lo-16bits)
4303 | DOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4304 |  |  |  | HR4303 (Lo-16bits)
4305 | DOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4306 |  |  |  | HR4305 (Lo-16bits)
4307 | DOC4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4308 |  |  |  | HR4307 (Lo-16bits)
4309 | DOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4310 | DOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4311 | DOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4312 | DOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4313 | DOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4314 | DOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4315 | DOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4316 | DOC4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4317 | DOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4318 |  |  |  | HR4317 (Lo-16bits)
4319 | DOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4320 |  |  |  | HR4319 (Lo-16bits)
4321 | DOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4322 |  |  |  | HR4321 (Lo-16bits)
4323 | DOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4324 |  |  |  | HR4323 (Lo-16bits)
4325 | DOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4326 |  |  |  | HR4325 (Lo-16bits)
4327 | DOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4328 |  |  |  | HR4327 (Lo-16bits)
4329 | DOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4330 |  |  |  | HR4329 (Lo-16bits)
4331 | DOC4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4332 |  |  |  | HR4331 (Lo-16bits)
4333 | DOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4334 | DOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4335 | DOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4336 | DOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4337 | DOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4338 | DOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4339 | DOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4340 | DOC4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4341 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4342 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4343 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4344 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4345 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4346 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4347 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4348 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4349 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4350 |  |  |  | HR4349 (Lo-16bits)
4351 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4352 |  |  |  | HR4351 (Lo-16bits)
4353 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4354 |  |  |  | HR4353 (Lo-16bits)
4355 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4356 |  |  |  | HR4355 (Lo-16bits)
4357 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4358 |  |  |  | HR4357 (Lo-16bits)
4359 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4360 |  |  |  | HR4359 (Lo-16bits)
4361 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4362 |  |  |  | HR4361 (Lo-16bits)
4363 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4364 |  |  |  | HR4363 (Lo-16bits)
4365 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4366 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4367 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4368 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4369 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4370 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4371 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4372 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4373 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4374 |  |  |  | HR4373 (Lo-16bits)
4375 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4376 |  |  |  | HR4375 (Lo-16bits)
4377 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4378 |  |  |  | HR4377 (Lo-16bits)
4379 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4380 |  |  |  | HR4379 (Lo-16bits)
4381 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4382 |  |  |  | HR4381 (Lo-16bits)
4383 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4384 |  |  |  | HR4383 (Lo-16bits)
4385 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4386 |  |  |  | HR4385 (Lo-16bits)
4387 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4388 |  |  |  | HR4387 (Lo-16bits)
4389 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4390 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4391 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4392 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4393 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4394 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4395 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4396 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4397 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4398 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4399 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4400 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4401 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4402 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4403 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4404 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4405 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4406 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4407 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4408 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4409 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4410 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4411 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4412 | NEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4413 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4414 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4415 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4416 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4417 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4418 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4419 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4420 | NEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4421 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4422 |  |  |  | HR4421 (Lo-16bits)
4423 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4424 |  |  |  | HR4423 (Lo-16bits)
4425 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4426 |  |  |  | HR4425 (Lo-16bits)
4427 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4428 |  |  |  | HR4427 (Lo-16bits)
4429 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4430 |  |  |  | HR4429 (Lo-16bits)
4431 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4432 |  |  |  | HR4431 (Lo-16bits)
4433 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4434 |  |  |  | HR4433 (Lo-16bits)
4435 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4436 |  |  |  | HR4435 (Lo-16bits)
4437 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4438 |  |  |  | HR4437 (Lo-16bits)
4439 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4440 |  |  |  | HR4439 (Lo-16bits)
4441 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4442 |  |  |  | HR4441 (Lo-16bits)
4443 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4444 |  |  |  | HR4443 (Lo-16bits)
4445 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4446 |  |  |  | HR4445 (Lo-16bits)
4447 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4448 |  |  |  | HR4447 (Lo-16bits)
4449 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4450 |  |  |  | HR4449 (Lo-16bits)
4451 | NEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4452 |  |  |  | HR4451 (Lo-16bits)
4453 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4454 |  |  |  | HR4453 (Lo-16bits)
4455 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4456 |  |  |  | HR4455 (Lo-16bits)
4457 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4458 |  |  |  | HR4457 (Lo-16bits)
4459 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4460 |  |  |  | HR4459 (Lo-16bits)
4461 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4462 |  |  |  | HR4461 (Lo-16bits)
4463 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4464 |  |  |  | HR4463 (Lo-16bits)
4465 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4466 |  |  |  | HR4465 (Lo-16bits)
4467 | NEF1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4468 |  |  |  | HR4467 (Lo-16bits)
4469 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4470 |  |  |  | HR4469 (Lo-16bits)
4471 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4472 |  |  |  | HR4471 (Lo-16bits)
4473 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4474 |  |  |  | HR4473 (Lo-16bits)
4475 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4476 |  |  |  | HR4475 (Lo-16bits)
4477 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4478 |  |  |  | HR4477 (Lo-16bits)
4479 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4480 |  |  |  | HR4479 (Lo-16bits)
4481 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4482 |  |  |  | HR4481 (Lo-16bits)
4483 | NEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4484 |  |  |  | HR4483 (Lo-16bits)
4485 | NEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4486 | NEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4487 | NEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4488 | NEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4489 | NEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4490 | NEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4491 | NEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4492 | NEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4493 | NEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4494 |  |  |  | HR4493 (Lo-16bits)
4495 | NEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4496 |  |  |  | HR4495 (Lo-16bits)
4497 | NEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4498 |  |  |  | HR4497 (Lo-16bits)
4499 | NEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4500 |  |  |  | HR4499 (Lo-16bits)
4501 | NEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4502 |  |  |  | HR4501 (Lo-16bits)
4503 | NEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4504 |  |  |  | HR4503 (Lo-16bits)
4505 | NEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4506 |  |  |  | HR4505 (Lo-16bits)
4507 | NEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4508 |  |  |  | HR4507 (Lo-16bits)
4509 | NEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4510 | NEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4511 | NEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4512 | NEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4513 | NEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4514 | NEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4515 | NEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4516 | NEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4517 | NEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4518 |  |  |  | HR4517 (Lo-16bits)
4519 | NEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4520 |  |  |  | HR4519 (Lo-16bits)
4521 | NEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4522 |  |  |  | HR4521 (Lo-16bits)
4523 | NEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4524 |  |  |  | HR4523 (Lo-16bits)
4525 | NEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4526 |  |  |  | HR4525 (Lo-16bits)
4527 | NEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4528 |  |  |  | HR4527 (Lo-16bits)
4529 | NEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4530 |  |  |  | HR4529 (Lo-16bits)
4531 | NEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4532 |  |  |  | HR4531 (Lo-16bits)
4533 | NEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4534 | NEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4535 | NEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4536 | NEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4537 | NEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4538 | NEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4539 | NEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4540 | NEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4541 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4542 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4543 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4544 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4545 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4546 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4547 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4548 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4549 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4550 |  |  |  | HR4549 (Lo-16bits)
4551 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4552 |  |  |  | HR4551 (Lo-16bits)
4553 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4554 |  |  |  | HR4553 (Lo-16bits)
4555 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4556 |  |  |  | HR4555 (Lo-16bits)
4557 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4558 |  |  |  | HR4557 (Lo-16bits)
4559 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4560 |  |  |  | HR4559 (Lo-16bits)
4561 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4562 |  |  |  | HR4561 (Lo-16bits)
4563 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4564 |  |  |  | HR4563 (Lo-16bits)
4565 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
4566 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
4567 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
4568 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
4569 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
4570 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
4571 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
4572 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
4573 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4574 |  |  |  | HR4573 (Lo-16bits)
4575 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4576 |  |  |  | HR4575 (Lo-16bits)
4577 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4578 |  |  |  | HR4577 (Lo-16bits)
4579 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4580 |  |  |  | HR4579 (Lo-16bits)
4581 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4582 |  |  |  | HR4581 (Lo-16bits)
4583 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4584 |  |  |  | HR4583 (Lo-16bits)
4585 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4586 |  |  |  | HR4585 (Lo-16bits)
4587 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4588 |  |  |  | HR4587 (Lo-16bits)
4589 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4590 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4591 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4592 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4593 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4594 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4595 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4596 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4597 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4598 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4599 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4600 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4601 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4602 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4603 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4604 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4605 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4606 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4607 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4608 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4609 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4610 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4611 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4612 | NEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4613 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4614 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4615 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4616 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4617 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4618 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4619 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4620 | NEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4621 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4622 |  |  |  | HR4621 (Lo-16bits)
4623 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4624 |  |  |  | HR4623 (Lo-16bits)
4625 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4626 |  |  |  | HR4625 (Lo-16bits)
4627 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4628 |  |  |  | HR4627 (Lo-16bits)
4629 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4630 |  |  |  | HR4629 (Lo-16bits)
4631 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4632 |  |  |  | HR4631 (Lo-16bits)
4633 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4634 |  |  |  | HR4633 (Lo-16bits)
4635 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4636 |  |  |  | HR4635 (Lo-16bits)
4637 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4638 |  |  |  | HR4637 (Lo-16bits)
4639 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4640 |  |  |  | HR4639 (Lo-16bits)
4641 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4642 |  |  |  | HR4641 (Lo-16bits)
4643 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4644 |  |  |  | HR4643 (Lo-16bits)
4645 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4646 |  |  |  | HR4645 (Lo-16bits)
4647 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4648 |  |  |  | HR4647 (Lo-16bits)
4649 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4650 |  |  |  | HR4649 (Lo-16bits)
4651 | NEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4652 |  |  |  | HR4651 (Lo-16bits)
4653 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4654 |  |  |  | HR4653 (Lo-16bits)
4655 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4656 |  |  |  | HR4655 (Lo-16bits)
4657 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4658 |  |  |  | HR4657 (Lo-16bits)
4659 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4660 |  |  |  | HR4659 (Lo-16bits)
4661 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4662 |  |  |  | HR4661 (Lo-16bits)
4663 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4664 |  |  |  | HR4663 (Lo-16bits)
4665 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4666 |  |  |  | HR4665 (Lo-16bits)
4667 | NEF2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4668 |  |  |  | HR4667 (Lo-16bits)
4669 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4670 |  |  |  | HR4669 (Lo-16bits)
4671 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4672 |  |  |  | HR4671 (Lo-16bits)
4673 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4674 |  |  |  | HR4673 (Lo-16bits)
4675 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4676 |  |  |  | HR4675 (Lo-16bits)
4677 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4678 |  |  |  | HR4677 (Lo-16bits)
4679 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4680 |  |  |  | HR4679 (Lo-16bits)
4681 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4682 |  |  |  | HR4681 (Lo-16bits)
4683 | NEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4684 |  |  |  | HR4683 (Lo-16bits)
4685 | NEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4686 | NEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4687 | NEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4688 | NEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4689 | NEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4690 | NEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4691 | NEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4692 | NEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4693 | NEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4694 |  |  |  | HR4693 (Lo-16bits)
4695 | NEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4696 |  |  |  | HR4695 (Lo-16bits)
4697 | NEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4698 |  |  |  | HR4697 (Lo-16bits)
4699 | NEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4700 |  |  |  | HR4699 (Lo-16bits)
4701 | NEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4702 |  |  |  | HR4701 (Lo-16bits)
4703 | NEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4704 |  |  |  | HR4703 (Lo-16bits)
4705 | NEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4706 |  |  |  | HR4705 (Lo-16bits)
4707 | NEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4708 |  |  |  | HR4707 (Lo-16bits)
4709 | NEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4710 | NEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4711 | NEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4712 | NEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4713 | NEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4714 | NEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4715 | NEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4716 | NEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4717 | NEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4718 |  |  |  | HR4717 (Lo-16bits)
4719 | NEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4720 |  |  |  | HR4719 (Lo-16bits)
4721 | NEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4722 |  |  |  | HR4721 (Lo-16bits)
4723 | NEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4724 |  |  |  | HR4723 (Lo-16bits)
4725 | NEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4726 |  |  |  | HR4725 (Lo-16bits)
4727 | NEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4728 |  |  |  | HR4727 (Lo-16bits)
4729 | NEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4730 |  |  |  | HR4729 (Lo-16bits)
4731 | NEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4732 |  |  |  | HR4731 (Lo-16bits)
4733 | NEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4734 | NEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4735 | NEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4736 | NEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4737 | NEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4738 | NEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4739 | NEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4740 | NEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4741 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4742 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4743 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4744 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4745 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4746 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4747 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4748 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4749 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4750 |  |  |  | HR4749 (Lo-16bits)
4751 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4752 |  |  |  | HR4751 (Lo-16bits)
4753 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4754 |  |  |  | HR4753 (Lo-16bits)
4755 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4756 |  |  |  | HR4755 (Lo-16bits)
4757 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4758 |  |  |  | HR4757 (Lo-16bits)
4759 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4760 |  |  |  | HR4759 (Lo-16bits)
4761 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4762 |  |  |  | HR4761 (Lo-16bits)
4763 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4764 |  |  |  | HR4763 (Lo-16bits)
4765 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4766 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4767 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4768 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4769 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4770 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4771 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4772 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4773 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4774 |  |  |  | HR4773 (Lo-16bits)
4775 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4776 |  |  |  | HR4775 (Lo-16bits)
4777 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4778 |  |  |  | HR4777 (Lo-16bits)
4779 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4780 |  |  |  | HR4779 (Lo-16bits)
4781 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4782 |  |  |  | HR4781 (Lo-16bits)
4783 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4784 |  |  |  | HR4783 (Lo-16bits)
4785 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4786 |  |  |  | HR4785 (Lo-16bits)
4787 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4788 |  |  |  | HR4787 (Lo-16bits)
4789 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4790 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4791 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4792 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4793 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4794 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4795 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4796 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4797 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4798 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4799 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4800 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4801 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4802 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4803 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4804 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4805 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4806 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4807 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4808 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4809 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4810 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4811 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4812 | NEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4813 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4814 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4815 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4816 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4817 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4818 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4819 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4820 | NEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
4821 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4822 |  |  |  | HR4821 (Lo-16bits)
4823 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4824 |  |  |  | HR4823 (Lo-16bits)
4825 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4826 |  |  |  | HR4825 (Lo-16bits)
4827 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4828 |  |  |  | HR4827 (Lo-16bits)
4829 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4830 |  |  |  | HR4829 (Lo-16bits)
4831 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4832 |  |  |  | HR4831 (Lo-16bits)
4833 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4834 |  |  |  | HR4833 (Lo-16bits)
4835 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4836 |  |  |  | HR4835 (Lo-16bits)
4837 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4838 |  |  |  | HR4837 (Lo-16bits)
4839 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4840 |  |  |  | HR4839 (Lo-16bits)
4841 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4842 |  |  |  | HR4841 (Lo-16bits)
4843 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4844 |  |  |  | HR4843 (Lo-16bits)
4845 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4846 |  |  |  | HR4845 (Lo-16bits)
4847 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4848 |  |  |  | HR4847 (Lo-16bits)
4849 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4850 |  |  |  | HR4849 (Lo-16bits)
4851 | NEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4852 |  |  |  | HR4851 (Lo-16bits)
4853 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4854 |  |  |  | HR4853 (Lo-16bits)
4855 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4856 |  |  |  | HR4855 (Lo-16bits)
4857 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4858 |  |  |  | HR4857 (Lo-16bits)
4859 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4860 |  |  |  | HR4859 (Lo-16bits)
4861 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4862 |  |  |  | HR4861 (Lo-16bits)
4863 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4864 |  |  |  | HR4863 (Lo-16bits)
4865 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4866 |  |  |  | HR4865 (Lo-16bits)
4867 | NEF3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
4868 |  |  |  | HR4867 (Lo-16bits)
4869 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4870 |  |  |  | HR4869 (Lo-16bits)
4871 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4872 |  |  |  | HR4871 (Lo-16bits)
4873 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4874 |  |  |  | HR4873 (Lo-16bits)
4875 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4876 |  |  |  | HR4875 (Lo-16bits)
4877 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4878 |  |  |  | HR4877 (Lo-16bits)
4879 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4880 |  |  |  | HR4879 (Lo-16bits)
4881 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4882 |  |  |  | HR4881 (Lo-16bits)
4883 | NEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4884 |  |  |  | HR4883 (Lo-16bits)
4885 | NEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4886 | NEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4887 | NEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4888 | NEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4889 | NEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4890 | NEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4891 | NEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4892 | NEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4893 | NEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4894 |  |  |  | HR4893 (Lo-16bits)
4895 | NEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4896 |  |  |  | HR4895 (Lo-16bits)
4897 | NEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4898 |  |  |  | HR4897 (Lo-16bits)
4899 | NEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4900 |  |  |  | HR4899 (Lo-16bits)
4901 | NEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4902 |  |  |  | HR4901 (Lo-16bits)
4903 | NEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4904 |  |  |  | HR4903 (Lo-16bits)
4905 | NEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4906 |  |  |  | HR4905 (Lo-16bits)
4907 | NEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4908 |  |  |  | HR4907 (Lo-16bits)
4909 | NEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4910 | NEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4911 | NEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4912 | NEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4913 | NEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4914 | NEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4915 | NEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4916 | NEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
4917 | NEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4918 |  |  |  | HR4917 (Lo-16bits)
4919 | NEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4920 |  |  |  | HR4919 (Lo-16bits)
4921 | NEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4922 |  |  |  | HR4921 (Lo-16bits)
4923 | NEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4924 |  |  |  | HR4923 (Lo-16bits)
4925 | NEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4926 |  |  |  | HR4925 (Lo-16bits)
4927 | NEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4928 |  |  |  | HR4927 (Lo-16bits)
4929 | NEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4930 |  |  |  | HR4929 (Lo-16bits)
4931 | NEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4932 |  |  |  | HR4931 (Lo-16bits)
4933 | NEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4934 | NEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4935 | NEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4936 | NEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4937 | NEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4938 | NEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4939 | NEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4940 | NEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
4941 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4942 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4943 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4944 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4945 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4946 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4947 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4948 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4949 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4950 |  |  |  | HR4949 (Lo-16bits)
4951 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4952 |  |  |  | HR4951 (Lo-16bits)
4953 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4954 |  |  |  | HR4953 (Lo-16bits)
4955 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4956 |  |  |  | HR4955 (Lo-16bits)
4957 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4958 |  |  |  | HR4957 (Lo-16bits)
4959 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4960 |  |  |  | HR4959 (Lo-16bits)
4961 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4962 |  |  |  | HR4961 (Lo-16bits)
4963 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4964 |  |  |  | HR4963 (Lo-16bits)
4965 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4966 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4967 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4968 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4969 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4970 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4971 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4972 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4973 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4974 |  |  |  | HR4973 (Lo-16bits)
4975 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4976 |  |  |  | HR4975 (Lo-16bits)
4977 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4978 |  |  |  | HR4977 (Lo-16bits)
4979 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4980 |  |  |  | HR4979 (Lo-16bits)
4981 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4982 |  |  |  | HR4981 (Lo-16bits)
4983 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4984 |  |  |  | HR4983 (Lo-16bits)
4985 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4986 |  |  |  | HR4985 (Lo-16bits)
4987 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4988 |  |  |  | HR4987 (Lo-16bits)
4989 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4990 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4991 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4992 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4993 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4994 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4995 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4996 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4997 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4998 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4999 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5000 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5001 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5002 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5003 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5004 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5005 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5006 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5007 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5008 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5009 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5010 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5011 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5012 | NEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5013 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5014 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5015 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5016 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5017 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5018 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5019 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5020 | NEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5021 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5022 |  |  |  | HR5021 (Lo-16bits)
5023 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5024 |  |  |  | HR5023 (Lo-16bits)
5025 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5026 |  |  |  | HR5025 (Lo-16bits)
5027 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5028 |  |  |  | HR5027 (Lo-16bits)
5029 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5030 |  |  |  | HR5029 (Lo-16bits)
5031 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5032 |  |  |  | HR5031 (Lo-16bits)
5033 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5034 |  |  |  | HR5033 (Lo-16bits)
5035 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5036 |  |  |  | HR5035 (Lo-16bits)
5037 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5038 |  |  |  | HR5037 (Lo-16bits)
5039 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5040 |  |  |  | HR5039 (Lo-16bits)
5041 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5042 |  |  |  | HR5041 (Lo-16bits)
5043 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5044 |  |  |  | HR5043 (Lo-16bits)
5045 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5046 |  |  |  | HR5045 (Lo-16bits)
5047 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5048 |  |  |  | HR5047 (Lo-16bits)
5049 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5050 |  |  |  | HR5049 (Lo-16bits)
5051 | NEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5052 |  |  |  | HR5051 (Lo-16bits)
5053 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
5054 |  |  |  | HR5053 (Lo-16bits)
5055 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
5056 |  |  |  | HR5055 (Lo-16bits)
5057 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
5058 |  |  |  | HR5057 (Lo-16bits)
5059 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
5060 |  |  |  | HR5059 (Lo-16bits)
5061 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
5062 |  |  |  | HR5061 (Lo-16bits)
5063 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
5064 |  |  |  | HR5063 (Lo-16bits)
5065 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
5066 |  |  |  | HR5065 (Lo-16bits)
5067 | NEF4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
5068 |  |  |  | HR5067 (Lo-16bits)
5069 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5070 |  |  |  | HR5069 (Lo-16bits)
5071 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5072 |  |  |  | HR5071 (Lo-16bits)
5073 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5074 |  |  |  | HR5073 (Lo-16bits)
5075 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5076 |  |  |  | HR5075 (Lo-16bits)
5077 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5078 |  |  |  | HR5077 (Lo-16bits)
5079 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5080 |  |  |  | HR5079 (Lo-16bits)
5081 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5082 |  |  |  | HR5081 (Lo-16bits)
5083 | NEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5084 |  |  |  | HR5083 (Lo-16bits)
5085 | NEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5086 | NEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5087 | NEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5088 | NEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5089 | NEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5090 | NEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5091 | NEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5092 | NEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5093 | NEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5094 |  |  |  | HR5093 (Lo-16bits)
5095 | NEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5096 |  |  |  | HR5095 (Lo-16bits)
5097 | NEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5098 |  |  |  | HR5097 (Lo-16bits)
5099 | NEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5100 |  |  |  | HR5099 (Lo-16bits)
5101 | NEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5102 |  |  |  | HR5101 (Lo-16bits)
5103 | NEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5104 |  |  |  | HR5103 (Lo-16bits)
5105 | NEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5106 |  |  |  | HR5105 (Lo-16bits)
5107 | NEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5108 |  |  |  | HR5107 (Lo-16bits)
5109 | NEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5110 | NEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5111 | NEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5112 | NEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5113 | NEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5114 | NEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5115 | NEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5116 | NEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5117 | NEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5118 |  |  |  | HR5117 (Lo-16bits)
5119 | NEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5120 |  |  |  | HR5119 (Lo-16bits)
5121 | NEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5122 |  |  |  | HR5121 (Lo-16bits)
5123 | NEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5124 |  |  |  | HR5123 (Lo-16bits)
5125 | NEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5126 |  |  |  | HR5125 (Lo-16bits)
5127 | NEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5128 |  |  |  | HR5127 (Lo-16bits)
5129 | NEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5130 |  |  |  | HR5129 (Lo-16bits)
5131 | NEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5132 |  |  |  | HR5131 (Lo-16bits)
5133 | NEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5134 | NEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5135 | NEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5136 | NEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5137 | NEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5138 | NEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5139 | NEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5140 | NEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5141 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5142 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5143 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5144 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5145 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5146 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5147 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5148 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5149 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5150 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5151 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5152 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5153 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5154 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5155 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5156 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5157 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5158 |  |  |  | HR5157 (Lo-16bits)
5159 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5160 |  |  |  | HR5159 (Lo-16bits)
5161 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5162 |  |  |  | HR5161 (Lo-16bits)
5163 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5164 |  |  |  | HR5163 (Lo-16bits)
5165 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5166 |  |  |  | HR5165 (Lo-16bits)
5167 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5168 |  |  |  | HR5167 (Lo-16bits)
5169 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5170 |  |  |  | HR5169 (Lo-16bits)
5171 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5172 |  |  |  | HR5171 (Lo-16bits)
5173 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5174 |  |  |  | HR5173 (Lo-16bits)
5175 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5176 |  |  |  | HR5175 (Lo-16bits)
5177 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5178 |  |  |  | HR5177 (Lo-16bits)
5179 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5180 |  |  |  | HR5179 (Lo-16bits)
5181 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5182 |  |  |  | HR5181 (Lo-16bits)
5183 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5184 |  |  |  | HR5183 (Lo-16bits)
5185 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5186 |  |  |  | HR5185 (Lo-16bits)
5187 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5188 |  |  |  | HR5187 (Lo-16bits)
5189 | DEF1:Comp. pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5190 |  |  |  | HR5189 (Lo-16bits)
5191 | DEF1:Comp. pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5192 |  |  |  | HR5191 (Lo-16bits)
5193 | DEF1:Comp. pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5194 |  |  |  | HR5193 (Lo-16bits)
5195 | DEF1:Comp. pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5196 |  |  |  | HR5195 (Lo-16bits)
5197 | DEF1:Comp. pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5198 |  |  |  | HR5197 (Lo-16bits)
5199 | DEF1:Comp. pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5200 |  |  |  | HR5199 (Lo-16bits)
5201 | DEF1:Comp. pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5202 |  |  |  | HR5201 (Lo-16bits)
5203 | DEF1:Comp. pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5204 |  |  |  | HR5203 (Lo-16bits)
5205 | DEF1:Comp. pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5206 |  |  |  | HR5205 (Lo-16bits)
5207 | DEF1:Comp. pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5208 |  |  |  | HR5207 (Lo-16bits)
5209 | DEF1:Comp. pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5210 |  |  |  | HR5209 (Lo-16bits)
5211 | DEF1:Comp. pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5212 |  |  |  | HR5211 (Lo-16bits)
5213 | DEF1:Comp. pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5214 |  |  |  | HR5213 (Lo-16bits)
5215 | DEF1:Comp. pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5216 |  |  |  | HR5215 (Lo-16bits)
5217 | DEF1:Comp. pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5218 |  |  |  | HR5217 (Lo-16bits)
5219 | DEF1:Comp. pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5220 |  |  |  | HR5219 (Lo-16bits)
5221 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5222 |  |  |  | HR5221 (Lo-16bits)
5223 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5224 |  |  |  | HR5223 (Lo-16bits)
5225 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5226 |  |  |  | HR5225 (Lo-16bits)
5227 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5228 |  |  |  | HR5227 (Lo-16bits)
5229 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5230 |  |  |  | HR5229 (Lo-16bits)
5231 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5232 |  |  |  | HR5231 (Lo-16bits)
5233 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5234 |  |  |  | HR5233 (Lo-16bits)
5235 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5236 |  |  |  | HR5235 (Lo-16bits)
5237 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5238 |  |  |  | HR5237 (Lo-16bits)
5239 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5240 |  |  |  | HR5239 (Lo-16bits)
5241 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5242 |  |  |  | HR5241 (Lo-16bits)
5243 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5244 |  |  |  | HR5243 (Lo-16bits)
5245 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5246 |  |  |  | HR5245 (Lo-16bits)
5247 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5248 |  |  |  | HR5247 (Lo-16bits)
5249 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5250 |  |  |  | HR5249 (Lo-16bits)
5251 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5252 |  |  |  | HR5251 (Lo-16bits)
5253 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5254 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5255 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5256 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5257 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5258 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5259 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5260 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5261 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5262 |  |  |  | HR5261 (Lo-16bits)
5263 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5264 |  |  |  | HR5263 (Lo-16bits)
5265 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5266 |  |  |  | HR5265 (Lo-16bits)
5267 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5268 |  |  |  | HR5267 (Lo-16bits)
5269 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5270 |  |  |  | HR5269 (Lo-16bits)
5271 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5272 |  |  |  | HR5271 (Lo-16bits)
5273 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5274 |  |  |  | HR5273 (Lo-16bits)
5275 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5276 |  |  |  | HR5275 (Lo-16bits)
5277 | DEF1:Unearth. pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5278 |  |  |  | HR5277 (Lo-16bits)
5279 | DEF1:Unearth. pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5280 |  |  |  | HR5279 (Lo-16bits)
5281 | DEF1:Unearth. pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5282 |  |  |  | HR5281 (Lo-16bits)
5283 | DEF1:Unearth. pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5284 |  |  |  | HR5283 (Lo-16bits)
5285 | DEF1:Unearth. pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5286 |  |  |  | HR5285 (Lo-16bits)
5287 | DEF1:Unearth. pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5288 |  |  |  | HR5287 (Lo-16bits)
5289 | DEF1:Unearth. pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5290 |  |  |  | HR5289 (Lo-16bits)
5291 | DEF1:Unearth. pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5292 |  |  |  | HR5291 (Lo-16bits)
5293 | DEF1:Unearth. pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5294 |  |  |  | HR5293 (Lo-16bits)
5295 | DEF1:Unearth. pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5296 |  |  |  | HR5295 (Lo-16bits)
5297 | DEF1:Unearth. pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5298 |  |  |  | HR5297 (Lo-16bits)
5299 | DEF1:Unearth. pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5300 |  |  |  | HR5299 (Lo-16bits)
5301 | DEF1:Unearth. pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5302 |  |  |  | HR5301 (Lo-16bits)
5303 | DEF1:Unearth. pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5304 |  |  |  | HR5303 (Lo-16bits)
5305 | DEF1:Unearth. pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5306 |  |  |  | HR5305 (Lo-16bits)
5307 | DEF1:Unearth. pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5308 |  |  |  | HR5307 (Lo-16bits)
5309 | DEF1:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5310 |  |  |  | HR5309 (Lo-16bits)
5311 | DEF1:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5312 |  |  |  | HR5311 (Lo-16bits)
5313 | DEF1:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5314 |  |  |  | HR5313 (Lo-16bits)
5315 | DEF1:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5316 |  |  |  | HR5315 (Lo-16bits)
5317 | DEF1:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5318 |  |  |  | HR5317 (Lo-16bits)
5319 | DEF1:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5320 |  |  |  | HR5319 (Lo-16bits)
5321 | DEF1:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5322 |  |  |  | HR5321 (Lo-16bits)
5323 | DEF1:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5324 |  |  |  | HR5323 (Lo-16bits)
5325 | DEF1:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5326 |  |  |  | HR5325 (Lo-16bits)
5327 | DEF1:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5328 |  |  |  | HR5327 (Lo-16bits)
5329 | DEF1:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5330 |  |  |  | HR5329 (Lo-16bits)
5331 | DEF1:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5332 |  |  |  | HR5331 (Lo-16bits)
5333 | DEF1:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5334 |  |  |  | HR5333 (Lo-16bits)
5335 | DEF1:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5336 |  |  |  | HR5335 (Lo-16bits)
5337 | DEF1:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5338 |  |  |  | HR5337 (Lo-16bits)
5339 | DEF1:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5340 |  |  |  | HR5339 (Lo-16bits)
5341 | DEF1:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5342 | DEF1:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5343 | DEF1:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5344 | DEF1:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5345 | DEF1:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5346 | DEF1:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5347 | DEF1:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5348 | DEF1:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5349 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
5350 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
5351 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
5352 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
5353 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
5354 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
5355 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
5356 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
5357 | DEF1:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5358 |  |  |  | HR5357 (Lo-16bits)
5359 | DEF1:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5360 |  |  |  | HR5359 (Lo-16bits)
5361 | DEF1:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5362 |  |  |  | HR5361 (Lo-16bits)
5363 | DEF1:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5364 |  |  |  | HR5363 (Lo-16bits)
5365 | DEF1:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5366 |  |  |  | HR5365 (Lo-16bits)
5367 | DEF1:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5368 |  |  |  | HR5367 (Lo-16bits)
5369 | DEF1:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5370 |  |  |  | HR5369 (Lo-16bits)
5371 | DEF1:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5372 |  |  |  | HR5371 (Lo-16bits)
5373 | DEF1:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5374 |  |  |  | HR5373 (Lo-16bits)
5375 | DEF1:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5376 |  |  |  | HR5375 (Lo-16bits)
5377 | DEF1:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5378 |  |  |  | HR5377 (Lo-16bits)
5379 | DEF1:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5380 |  |  |  | HR5379 (Lo-16bits)
5381 | DEF1:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5382 |  |  |  | HR5381 (Lo-16bits)
5383 | DEF1:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5384 |  |  |  | HR5383 (Lo-16bits)
5385 | DEF1:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5386 |  |  |  | HR5385 (Lo-16bits)
5387 | DEF1:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5388 |  |  |  | HR5387 (Lo-16bits)
5389 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5390 |  |  |  | HR5389 (Lo-16bits)
5391 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5392 |  |  |  | HR5391 (Lo-16bits)
5393 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5394 |  |  |  | HR5393 (Lo-16bits)
5395 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5396 |  |  |  | HR5395 (Lo-16bits)
5397 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5398 |  |  |  | HR5397 (Lo-16bits)
5399 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5400 |  |  |  | HR5399 (Lo-16bits)
5401 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5402 |  |  |  | HR5401 (Lo-16bits)
5403 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5404 |  |  |  | HR5403 (Lo-16bits)
5405 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5406 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5407 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5408 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5409 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5410 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5411 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5412 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5413 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5414 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5415 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5416 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5417 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5418 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5419 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5420 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5421 | DEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5422 | DEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5423 | DEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5424 | DEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5425 | DEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5426 | DEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5427 | DEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5428 | DEF1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5429 | DEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5430 | DEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5431 | DEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5432 | DEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5433 | DEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5434 | DEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5435 | DEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5436 | DEF1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5437 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5438 |  |  |  | HR5437 (Lo-16bits)
5439 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5440 |  |  |  | HR5439 (Lo-16bits)
5441 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5442 |  |  |  | HR5441 (Lo-16bits)
5443 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5444 |  |  |  | HR5443 (Lo-16bits)
5445 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5446 |  |  |  | HR5445 (Lo-16bits)
5447 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5448 |  |  |  | HR5447 (Lo-16bits)
5449 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5450 |  |  |  | HR5449 (Lo-16bits)
5451 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5452 |  |  |  | HR5451 (Lo-16bits)
5453 | DEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5454 |  |  |  | HR5453 (Lo-16bits)
5455 | DEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5456 |  |  |  | HR5455 (Lo-16bits)
5457 | DEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5458 |  |  |  | HR5457 (Lo-16bits)
5459 | DEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5460 |  |  |  | HR5459 (Lo-16bits)
5461 | DEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5462 |  |  |  | HR5461 (Lo-16bits)
5463 | DEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5464 |  |  |  | HR5463 (Lo-16bits)
5465 | DEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5466 |  |  |  | HR5465 (Lo-16bits)
5467 | DEF1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5468 |  |  |  | HR5467 (Lo-16bits)
5469 | DEF1:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5470 |  |  |  | HR5469 (Lo-16bits)
5471 | DEF1:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5472 |  |  |  | HR5471 (Lo-16bits)
5473 | DEF1:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5474 |  |  |  | HR5473 (Lo-16bits)
5475 | DEF1:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5476 |  |  |  | HR5475 (Lo-16bits)
5477 | DEF1:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5478 |  |  |  | HR5477 (Lo-16bits)
5479 | DEF1:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5480 |  |  |  | HR5479 (Lo-16bits)
5481 | DEF1:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5482 |  |  |  | HR5481 (Lo-16bits)
5483 | DEF1:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5484 |  |  |  | HR5483 (Lo-16bits)
5485 | DEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5486 |  |  |  | HR5485 (Lo-16bits)
5487 | DEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5488 |  |  |  | HR5487 (Lo-16bits)
5489 | DEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5490 |  |  |  | HR5489 (Lo-16bits)
5491 | DEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5492 |  |  |  | HR5491 (Lo-16bits)
5493 | DEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5494 |  |  |  | HR5493 (Lo-16bits)
5495 | DEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5496 |  |  |  | HR5495 (Lo-16bits)
5497 | DEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5498 |  |  |  | HR5497 (Lo-16bits)
5499 | DEF1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5500 |  |  |  | HR5499 (Lo-16bits)
5501 | DEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5502 | DEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5503 | DEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5504 | DEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5505 | DEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5506 | DEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5507 | DEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5508 | DEF1:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5509 | DEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5510 |  |  |  | HR5509 (Lo-16bits)
5511 | DEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5512 |  |  |  | HR5511 (Lo-16bits)
5513 | DEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5514 |  |  |  | HR5513 (Lo-16bits)
5515 | DEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5516 |  |  |  | HR5515 (Lo-16bits)
5517 | DEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5518 |  |  |  | HR5517 (Lo-16bits)
5519 | DEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5520 |  |  |  | HR5519 (Lo-16bits)
5521 | DEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5522 |  |  |  | HR5521 (Lo-16bits)
5523 | DEF1:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5524 |  |  |  | HR5523 (Lo-16bits)
5525 | DEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5526 | DEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5527 | DEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5528 | DEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5529 | DEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5530 | DEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5531 | DEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5532 | DEF1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5533 | DEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5534 |  |  |  | HR5533 (Lo-16bits)
5535 | DEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5536 |  |  |  | HR5535 (Lo-16bits)
5537 | DEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5538 |  |  |  | HR5537 (Lo-16bits)
5539 | DEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5540 |  |  |  | HR5539 (Lo-16bits)
5541 | DEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5542 |  |  |  | HR5541 (Lo-16bits)
5543 | DEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5544 |  |  |  | HR5543 (Lo-16bits)
5545 | DEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5546 |  |  |  | HR5545 (Lo-16bits)
5547 | DEF1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5548 |  |  |  | HR5547 (Lo-16bits)
5549 | DEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5550 | DEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5551 | DEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5552 | DEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5553 | DEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5554 | DEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5555 | DEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5556 | DEF1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5557 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5558 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5559 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5560 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5561 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5562 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5563 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5564 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5565 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5566 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5567 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5568 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5569 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5570 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5571 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5572 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5573 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5574 |  |  |  | HR5573 (Lo-16bits)
5575 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5576 |  |  |  | HR5575 (Lo-16bits)
5577 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5578 |  |  |  | HR5577 (Lo-16bits)
5579 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5580 |  |  |  | HR5579 (Lo-16bits)
5581 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5582 |  |  |  | HR5581 (Lo-16bits)
5583 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5584 |  |  |  | HR5583 (Lo-16bits)
5585 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5586 |  |  |  | HR5585 (Lo-16bits)
5587 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5588 |  |  |  | HR5587 (Lo-16bits)
5589 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5590 |  |  |  | HR5589 (Lo-16bits)
5591 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5592 |  |  |  | HR5591 (Lo-16bits)
5593 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5594 |  |  |  | HR5593 (Lo-16bits)
5595 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5596 |  |  |  | HR5595 (Lo-16bits)
5597 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5598 |  |  |  | HR5597 (Lo-16bits)
5599 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5600 |  |  |  | HR5599 (Lo-16bits)
5601 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5602 |  |  |  | HR5601 (Lo-16bits)
5603 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5604 |  |  |  | HR5603 (Lo-16bits)
5605 | DEF2:Comp. pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5606 |  |  |  | HR5605 (Lo-16bits)
5607 | DEF2:Comp. pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5608 |  |  |  | HR5607 (Lo-16bits)
5609 | DEF2:Comp. pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5610 |  |  |  | HR5609 (Lo-16bits)
5611 | DEF2:Comp. pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5612 |  |  |  | HR5611 (Lo-16bits)
5613 | DEF2:Comp. pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5614 |  |  |  | HR5613 (Lo-16bits)
5615 | DEF2:Comp. pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5616 |  |  |  | HR5615 (Lo-16bits)
5617 | DEF2:Comp. pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5618 |  |  |  | HR5617 (Lo-16bits)
5619 | DEF2:Comp. pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5620 |  |  |  | HR5619 (Lo-16bits)
5621 | DEF2:Comp. pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5622 |  |  |  | HR5621 (Lo-16bits)
5623 | DEF2:Comp. pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5624 |  |  |  | HR5623 (Lo-16bits)
5625 | DEF2:Comp. pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5626 |  |  |  | HR5625 (Lo-16bits)
5627 | DEF2:Comp. pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5628 |  |  |  | HR5627 (Lo-16bits)
5629 | DEF2:Comp. pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5630 |  |  |  | HR5629 (Lo-16bits)
5631 | DEF2:Comp. pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5632 |  |  |  | HR5631 (Lo-16bits)
5633 | DEF2:Comp. pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5634 |  |  |  | HR5633 (Lo-16bits)
5635 | DEF2:Comp. pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5636 |  |  |  | HR5635 (Lo-16bits)
5637 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5638 |  |  |  | HR5637 (Lo-16bits)
5639 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5640 |  |  |  | HR5639 (Lo-16bits)
5641 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5642 |  |  |  | HR5641 (Lo-16bits)
5643 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5644 |  |  |  | HR5643 (Lo-16bits)
5645 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5646 |  |  |  | HR5645 (Lo-16bits)
5647 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5648 |  |  |  | HR5647 (Lo-16bits)
5649 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5650 |  |  |  | HR5649 (Lo-16bits)
5651 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5652 |  |  |  | HR5651 (Lo-16bits)
5653 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5654 |  |  |  | HR5653 (Lo-16bits)
5655 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5656 |  |  |  | HR5655 (Lo-16bits)
5657 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5658 |  |  |  | HR5657 (Lo-16bits)
5659 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5660 |  |  |  | HR5659 (Lo-16bits)
5661 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5662 |  |  |  | HR5661 (Lo-16bits)
5663 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5664 |  |  |  | HR5663 (Lo-16bits)
5665 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5666 |  |  |  | HR5665 (Lo-16bits)
5667 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5668 |  |  |  | HR5667 (Lo-16bits)
5669 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5670 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5671 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5672 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5673 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5674 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5675 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5676 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5677 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5678 |  |  |  | HR5677 (Lo-16bits)
5679 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5680 |  |  |  | HR5679 (Lo-16bits)
5681 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5682 |  |  |  | HR5681 (Lo-16bits)
5683 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5684 |  |  |  | HR5683 (Lo-16bits)
5685 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5686 |  |  |  | HR5685 (Lo-16bits)
5687 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5688 |  |  |  | HR5687 (Lo-16bits)
5689 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5690 |  |  |  | HR5689 (Lo-16bits)
5691 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5692 |  |  |  | HR5691 (Lo-16bits)
5693 | DEF2:Unearth. pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5694 |  |  |  | HR5693 (Lo-16bits)
5695 | DEF2:Unearth. pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5696 |  |  |  | HR5695 (Lo-16bits)
5697 | DEF2:Unearth. pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5698 |  |  |  | HR5697 (Lo-16bits)
5699 | DEF2:Unearth. pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5700 |  |  |  | HR5699 (Lo-16bits)
5701 | DEF2:Unearth. pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5702 |  |  |  | HR5701 (Lo-16bits)
5703 | DEF2:Unearth. pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5704 |  |  |  | HR5703 (Lo-16bits)
5705 | DEF2:Unearth. pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5706 |  |  |  | HR5705 (Lo-16bits)
5707 | DEF2:Unearth. pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5708 |  |  |  | HR5707 (Lo-16bits)
5709 | DEF2:Unearth. pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5710 |  |  |  | HR5709 (Lo-16bits)
5711 | DEF2:Unearth. pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5712 |  |  |  | HR5711 (Lo-16bits)
5713 | DEF2:Unearth. pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5714 |  |  |  | HR5713 (Lo-16bits)
5715 | DEF2:Unearth. pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5716 |  |  |  | HR5715 (Lo-16bits)
5717 | DEF2:Unearth. pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5718 |  |  |  | HR5717 (Lo-16bits)
5719 | DEF2:Unearth. pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5720 |  |  |  | HR5719 (Lo-16bits)
5721 | DEF2:Unearth. pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5722 |  |  |  | HR5721 (Lo-16bits)
5723 | DEF2:Unearth. pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5724 |  |  |  | HR5723 (Lo-16bits)
5725 | DEF2:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5726 |  |  |  | HR5725 (Lo-16bits)
5727 | DEF2:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5728 |  |  |  | HR5727 (Lo-16bits)
5729 | DEF2:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5730 |  |  |  | HR5729 (Lo-16bits)
5731 | DEF2:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5732 |  |  |  | HR5731 (Lo-16bits)
5733 | DEF2:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5734 |  |  |  | HR5733 (Lo-16bits)
5735 | DEF2:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5736 |  |  |  | HR5735 (Lo-16bits)
5737 | DEF2:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5738 |  |  |  | HR5737 (Lo-16bits)
5739 | DEF2:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5740 |  |  |  | HR5739 (Lo-16bits)
5741 | DEF2:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5742 |  |  |  | HR5741 (Lo-16bits)
5743 | DEF2:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5744 |  |  |  | HR5743 (Lo-16bits)
5745 | DEF2:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5746 |  |  |  | HR5745 (Lo-16bits)
5747 | DEF2:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5748 |  |  |  | HR5747 (Lo-16bits)
5749 | DEF2:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5750 |  |  |  | HR5749 (Lo-16bits)
5751 | DEF2:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5752 |  |  |  | HR5751 (Lo-16bits)
5753 | DEF2:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5754 |  |  |  | HR5753 (Lo-16bits)
5755 | DEF2:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5756 |  |  |  | HR5755 (Lo-16bits)
5757 | DEF2:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5758 | DEF2:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5759 | DEF2:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5760 | DEF2:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5761 | DEF2:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5762 | DEF2:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5763 | DEF2:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5764 | DEF2:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5765 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5766 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5767 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5768 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5769 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5770 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5771 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5772 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5773 | DEF2:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5774 |  |  |  | HR5773 (Lo-16bits)
5775 | DEF2:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5776 |  |  |  | HR5775 (Lo-16bits)
5777 | DEF2:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5778 |  |  |  | HR5777 (Lo-16bits)
5779 | DEF2:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5780 |  |  |  | HR5779 (Lo-16bits)
5781 | DEF2:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5782 |  |  |  | HR5781 (Lo-16bits)
5783 | DEF2:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5784 |  |  |  | HR5783 (Lo-16bits)
5785 | DEF2:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5786 |  |  |  | HR5785 (Lo-16bits)
5787 | DEF2:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5788 |  |  |  | HR5787 (Lo-16bits)
5789 | DEF2:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5790 |  |  |  | HR5789 (Lo-16bits)
5791 | DEF2:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5792 |  |  |  | HR5791 (Lo-16bits)
5793 | DEF2:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5794 |  |  |  | HR5793 (Lo-16bits)
5795 | DEF2:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5796 |  |  |  | HR5795 (Lo-16bits)
5797 | DEF2:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5798 |  |  |  | HR5797 (Lo-16bits)
5799 | DEF2:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5800 |  |  |  | HR5799 (Lo-16bits)
5801 | DEF2:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5802 |  |  |  | HR5801 (Lo-16bits)
5803 | DEF2:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5804 |  |  |  | HR5803 (Lo-16bits)
5805 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5806 |  |  |  | HR5805 (Lo-16bits)
5807 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5808 |  |  |  | HR5807 (Lo-16bits)
5809 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5810 |  |  |  | HR5809 (Lo-16bits)
5811 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5812 |  |  |  | HR5811 (Lo-16bits)
5813 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5814 |  |  |  | HR5813 (Lo-16bits)
5815 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5816 |  |  |  | HR5815 (Lo-16bits)
5817 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5818 |  |  |  | HR5817 (Lo-16bits)
5819 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5820 |  |  |  | HR5819 (Lo-16bits)
5821 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5822 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5823 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5824 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5825 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5826 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5827 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5828 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5829 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5830 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5831 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5832 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5833 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5834 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5835 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5836 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5837 | DEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5838 | DEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5839 | DEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5840 | DEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5841 | DEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5842 | DEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5843 | DEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5844 | DEF2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5845 | DEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5846 | DEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5847 | DEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5848 | DEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5849 | DEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5850 | DEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5851 | DEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5852 | DEF2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
5853 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5854 |  |  |  | HR5853 (Lo-16bits)
5855 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5856 |  |  |  | HR5855 (Lo-16bits)
5857 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5858 |  |  |  | HR5857 (Lo-16bits)
5859 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5860 |  |  |  | HR5859 (Lo-16bits)
5861 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5862 |  |  |  | HR5861 (Lo-16bits)
5863 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5864 |  |  |  | HR5863 (Lo-16bits)
5865 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5866 |  |  |  | HR5865 (Lo-16bits)
5867 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5868 |  |  |  | HR5867 (Lo-16bits)
5869 | DEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5870 |  |  |  | HR5869 (Lo-16bits)
5871 | DEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5872 |  |  |  | HR5871 (Lo-16bits)
5873 | DEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5874 |  |  |  | HR5873 (Lo-16bits)
5875 | DEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5876 |  |  |  | HR5875 (Lo-16bits)
5877 | DEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5878 |  |  |  | HR5877 (Lo-16bits)
5879 | DEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5880 |  |  |  | HR5879 (Lo-16bits)
5881 | DEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5882 |  |  |  | HR5881 (Lo-16bits)
5883 | DEF2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5884 |  |  |  | HR5883 (Lo-16bits)
5885 | DEF2:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5886 |  |  |  | HR5885 (Lo-16bits)
5887 | DEF2:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5888 |  |  |  | HR5887 (Lo-16bits)
5889 | DEF2:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5890 |  |  |  | HR5889 (Lo-16bits)
5891 | DEF2:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5892 |  |  |  | HR5891 (Lo-16bits)
5893 | DEF2:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5894 |  |  |  | HR5893 (Lo-16bits)
5895 | DEF2:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5896 |  |  |  | HR5895 (Lo-16bits)
5897 | DEF2:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5898 |  |  |  | HR5897 (Lo-16bits)
5899 | DEF2:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5900 |  |  |  | HR5899 (Lo-16bits)
5901 | DEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5902 |  |  |  | HR5901 (Lo-16bits)
5903 | DEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5904 |  |  |  | HR5903 (Lo-16bits)
5905 | DEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5906 |  |  |  | HR5905 (Lo-16bits)
5907 | DEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5908 |  |  |  | HR5907 (Lo-16bits)
5909 | DEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5910 |  |  |  | HR5909 (Lo-16bits)
5911 | DEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5912 |  |  |  | HR5911 (Lo-16bits)
5913 | DEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5914 |  |  |  | HR5913 (Lo-16bits)
5915 | DEF2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5916 |  |  |  | HR5915 (Lo-16bits)
5917 | DEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5918 | DEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5919 | DEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5920 | DEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5921 | DEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5922 | DEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5923 | DEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5924 | DEF2:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5925 | DEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5926 |  |  |  | HR5925 (Lo-16bits)
5927 | DEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5928 |  |  |  | HR5927 (Lo-16bits)
5929 | DEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5930 |  |  |  | HR5929 (Lo-16bits)
5931 | DEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5932 |  |  |  | HR5931 (Lo-16bits)
5933 | DEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5934 |  |  |  | HR5933 (Lo-16bits)
5935 | DEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5936 |  |  |  | HR5935 (Lo-16bits)
5937 | DEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5938 |  |  |  | HR5937 (Lo-16bits)
5939 | DEF2:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5940 |  |  |  | HR5939 (Lo-16bits)
5941 | DEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5942 | DEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5943 | DEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5944 | DEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5945 | DEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5946 | DEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5947 | DEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5948 | DEF2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
5949 | DEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5950 |  |  |  | HR5949 (Lo-16bits)
5951 | DEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5952 |  |  |  | HR5951 (Lo-16bits)
5953 | DEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5954 |  |  |  | HR5953 (Lo-16bits)
5955 | DEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5956 |  |  |  | HR5955 (Lo-16bits)
5957 | DEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5958 |  |  |  | HR5957 (Lo-16bits)
5959 | DEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5960 |  |  |  | HR5959 (Lo-16bits)
5961 | DEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5962 |  |  |  | HR5961 (Lo-16bits)
5963 | DEF2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5964 |  |  |  | HR5963 (Lo-16bits)
5965 | DEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5966 | DEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5967 | DEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5968 | DEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5969 | DEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5970 | DEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5971 | DEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5972 | DEF2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
5973 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5974 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5975 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5976 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5977 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5978 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5979 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5980 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5981 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5982 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5983 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5984 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5985 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5986 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5987 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5988 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5989 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5990 |  |  |  | HR5989 (Lo-16bits)
5991 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5992 |  |  |  | HR5991 (Lo-16bits)
5993 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5994 |  |  |  | HR5993 (Lo-16bits)
5995 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5996 |  |  |  | HR5995 (Lo-16bits)
5997 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5998 |  |  |  | HR5997 (Lo-16bits)
5999 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6000 |  |  |  | HR5999 (Lo-16bits)
6001 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6002 |  |  |  | HR6001 (Lo-16bits)
6003 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6004 |  |  |  | HR6003 (Lo-16bits)
6005 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6006 |  |  |  | HR6005 (Lo-16bits)
6007 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6008 |  |  |  | HR6007 (Lo-16bits)
6009 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6010 |  |  |  | HR6009 (Lo-16bits)
6011 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6012 |  |  |  | HR6011 (Lo-16bits)
6013 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6014 |  |  |  | HR6013 (Lo-16bits)
6015 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6016 |  |  |  | HR6015 (Lo-16bits)
6017 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6018 |  |  |  | HR6017 (Lo-16bits)
6019 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6020 |  |  |  | HR6019 (Lo-16bits)
6021 | DEF3:Comp. pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6022 |  |  |  | HR6021 (Lo-16bits)
6023 | DEF3:Comp. pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6024 |  |  |  | HR6023 (Lo-16bits)
6025 | DEF3:Comp. pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6026 |  |  |  | HR6025 (Lo-16bits)
6027 | DEF3:Comp. pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6028 |  |  |  | HR6027 (Lo-16bits)
6029 | DEF3:Comp. pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6030 |  |  |  | HR6029 (Lo-16bits)
6031 | DEF3:Comp. pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6032 |  |  |  | HR6031 (Lo-16bits)
6033 | DEF3:Comp. pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6034 |  |  |  | HR6033 (Lo-16bits)
6035 | DEF3:Comp. pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6036 |  |  |  | HR6035 (Lo-16bits)
6037 | DEF3:Comp. pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6038 |  |  |  | HR6037 (Lo-16bits)
6039 | DEF3:Comp. pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6040 |  |  |  | HR6039 (Lo-16bits)
6041 | DEF3:Comp. pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6042 |  |  |  | HR6041 (Lo-16bits)
6043 | DEF3:Comp. pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6044 |  |  |  | HR6043 (Lo-16bits)
6045 | DEF3:Comp. pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6046 |  |  |  | HR6045 (Lo-16bits)
6047 | DEF3:Comp. pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6048 |  |  |  | HR6047 (Lo-16bits)
6049 | DEF3:Comp. pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6050 |  |  |  | HR6049 (Lo-16bits)
6051 | DEF3:Comp. pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6052 |  |  |  | HR6051 (Lo-16bits)
6053 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6054 |  |  |  | HR6053 (Lo-16bits)
6055 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6056 |  |  |  | HR6055 (Lo-16bits)
6057 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6058 |  |  |  | HR6057 (Lo-16bits)
6059 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6060 |  |  |  | HR6059 (Lo-16bits)
6061 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6062 |  |  |  | HR6061 (Lo-16bits)
6063 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6064 |  |  |  | HR6063 (Lo-16bits)
6065 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6066 |  |  |  | HR6065 (Lo-16bits)
6067 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6068 |  |  |  | HR6067 (Lo-16bits)
6069 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6070 |  |  |  | HR6069 (Lo-16bits)
6071 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6072 |  |  |  | HR6071 (Lo-16bits)
6073 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6074 |  |  |  | HR6073 (Lo-16bits)
6075 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6076 |  |  |  | HR6075 (Lo-16bits)
6077 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6078 |  |  |  | HR6077 (Lo-16bits)
6079 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6080 |  |  |  | HR6079 (Lo-16bits)
6081 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6082 |  |  |  | HR6081 (Lo-16bits)
6083 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6084 |  |  |  | HR6083 (Lo-16bits)
6085 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6086 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6087 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6088 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6089 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6090 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6091 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6092 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6093 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6094 |  |  |  | HR6093 (Lo-16bits)
6095 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6096 |  |  |  | HR6095 (Lo-16bits)
6097 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6098 |  |  |  | HR6097 (Lo-16bits)
6099 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6100 |  |  |  | HR6099 (Lo-16bits)
6101 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6102 |  |  |  | HR6101 (Lo-16bits)
6103 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6104 |  |  |  | HR6103 (Lo-16bits)
6105 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6106 |  |  |  | HR6105 (Lo-16bits)
6107 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6108 |  |  |  | HR6107 (Lo-16bits)
6109 | DEF3:Unearth. pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6110 |  |  |  | HR6109 (Lo-16bits)
6111 | DEF3:Unearth. pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6112 |  |  |  | HR6111 (Lo-16bits)
6113 | DEF3:Unearth. pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6114 |  |  |  | HR6113 (Lo-16bits)
6115 | DEF3:Unearth. pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6116 |  |  |  | HR6115 (Lo-16bits)
6117 | DEF3:Unearth. pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6118 |  |  |  | HR6117 (Lo-16bits)
6119 | DEF3:Unearth. pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6120 |  |  |  | HR6119 (Lo-16bits)
6121 | DEF3:Unearth. pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6122 |  |  |  | HR6121 (Lo-16bits)
6123 | DEF3:Unearth. pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6124 |  |  |  | HR6123 (Lo-16bits)
6125 | DEF3:Unearth. pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6126 |  |  |  | HR6125 (Lo-16bits)
6127 | DEF3:Unearth. pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6128 |  |  |  | HR6127 (Lo-16bits)
6129 | DEF3:Unearth. pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6130 |  |  |  | HR6129 (Lo-16bits)
6131 | DEF3:Unearth. pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6132 |  |  |  | HR6131 (Lo-16bits)
6133 | DEF3:Unearth. pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6134 |  |  |  | HR6133 (Lo-16bits)
6135 | DEF3:Unearth. pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6136 |  |  |  | HR6135 (Lo-16bits)
6137 | DEF3:Unearth. pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6138 |  |  |  | HR6137 (Lo-16bits)
6139 | DEF3:Unearth. pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6140 |  |  |  | HR6139 (Lo-16bits)
6141 | DEF3:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6142 |  |  |  | HR6141 (Lo-16bits)
6143 | DEF3:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6144 |  |  |  | HR6143 (Lo-16bits)
6145 | DEF3:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6146 |  |  |  | HR6145 (Lo-16bits)
6147 | DEF3:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6148 |  |  |  | HR6147 (Lo-16bits)
6149 | DEF3:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6150 |  |  |  | HR6149 (Lo-16bits)
6151 | DEF3:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6152 |  |  |  | HR6151 (Lo-16bits)
6153 | DEF3:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6154 |  |  |  | HR6153 (Lo-16bits)
6155 | DEF3:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6156 |  |  |  | HR6155 (Lo-16bits)
6157 | DEF3:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6158 |  |  |  | HR6157 (Lo-16bits)
6159 | DEF3:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6160 |  |  |  | HR6159 (Lo-16bits)
6161 | DEF3:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6162 |  |  |  | HR6161 (Lo-16bits)
6163 | DEF3:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6164 |  |  |  | HR6163 (Lo-16bits)
6165 | DEF3:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6166 |  |  |  | HR6165 (Lo-16bits)
6167 | DEF3:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6168 |  |  |  | HR6167 (Lo-16bits)
6169 | DEF3:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6170 |  |  |  | HR6169 (Lo-16bits)
6171 | DEF3:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6172 |  |  |  | HR6171 (Lo-16bits)
6173 | DEF3:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6174 | DEF3:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6175 | DEF3:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6176 | DEF3:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6177 | DEF3:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6178 | DEF3:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6179 | DEF3:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6180 | DEF3:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6181 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6182 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6183 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6184 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6185 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6186 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6187 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6188 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6189 | DEF3:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6190 |  |  |  | HR6189 (Lo-16bits)
6191 | DEF3:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6192 |  |  |  | HR6191 (Lo-16bits)
6193 | DEF3:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6194 |  |  |  | HR6193 (Lo-16bits)
6195 | DEF3:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6196 |  |  |  | HR6195 (Lo-16bits)
6197 | DEF3:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6198 |  |  |  | HR6197 (Lo-16bits)
6199 | DEF3:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6200 |  |  |  | HR6199 (Lo-16bits)
6201 | DEF3:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6202 |  |  |  | HR6201 (Lo-16bits)
6203 | DEF3:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6204 |  |  |  | HR6203 (Lo-16bits)
6205 | DEF3:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6206 |  |  |  | HR6205 (Lo-16bits)
6207 | DEF3:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6208 |  |  |  | HR6207 (Lo-16bits)
6209 | DEF3:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6210 |  |  |  | HR6209 (Lo-16bits)
6211 | DEF3:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6212 |  |  |  | HR6211 (Lo-16bits)
6213 | DEF3:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6214 |  |  |  | HR6213 (Lo-16bits)
6215 | DEF3:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6216 |  |  |  | HR6215 (Lo-16bits)
6217 | DEF3:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6218 |  |  |  | HR6217 (Lo-16bits)
6219 | DEF3:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6220 |  |  |  | HR6219 (Lo-16bits)
6221 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6222 |  |  |  | HR6221 (Lo-16bits)
6223 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6224 |  |  |  | HR6223 (Lo-16bits)
6225 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6226 |  |  |  | HR6225 (Lo-16bits)
6227 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6228 |  |  |  | HR6227 (Lo-16bits)
6229 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6230 |  |  |  | HR6229 (Lo-16bits)
6231 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6232 |  |  |  | HR6231 (Lo-16bits)
6233 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6234 |  |  |  | HR6233 (Lo-16bits)
6235 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6236 |  |  |  | HR6235 (Lo-16bits)
6237 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6238 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6239 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6240 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6241 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6242 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6243 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6244 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6245 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6246 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6247 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6248 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6249 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6250 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6251 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6252 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6253 | DEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6254 | DEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6255 | DEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6256 | DEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6257 | DEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6258 | DEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6259 | DEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6260 | DEF3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6261 | DEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6262 | DEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6263 | DEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6264 | DEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6265 | DEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6266 | DEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6267 | DEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6268 | DEF3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6269 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6270 |  |  |  | HR6269 (Lo-16bits)
6271 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6272 |  |  |  | HR6271 (Lo-16bits)
6273 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6274 |  |  |  | HR6273 (Lo-16bits)
6275 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6276 |  |  |  | HR6275 (Lo-16bits)
6277 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6278 |  |  |  | HR6277 (Lo-16bits)
6279 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6280 |  |  |  | HR6279 (Lo-16bits)
6281 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6282 |  |  |  | HR6281 (Lo-16bits)
6283 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6284 |  |  |  | HR6283 (Lo-16bits)
6285 | DEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6286 |  |  |  | HR6285 (Lo-16bits)
6287 | DEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6288 |  |  |  | HR6287 (Lo-16bits)
6289 | DEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6290 |  |  |  | HR6289 (Lo-16bits)
6291 | DEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6292 |  |  |  | HR6291 (Lo-16bits)
6293 | DEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6294 |  |  |  | HR6293 (Lo-16bits)
6295 | DEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6296 |  |  |  | HR6295 (Lo-16bits)
6297 | DEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6298 |  |  |  | HR6297 (Lo-16bits)
6299 | DEF3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6300 |  |  |  | HR6299 (Lo-16bits)
6301 | DEF3:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6302 |  |  |  | HR6301 (Lo-16bits)
6303 | DEF3:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6304 |  |  |  | HR6303 (Lo-16bits)
6305 | DEF3:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6306 |  |  |  | HR6305 (Lo-16bits)
6307 | DEF3:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6308 |  |  |  | HR6307 (Lo-16bits)
6309 | DEF3:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6310 |  |  |  | HR6309 (Lo-16bits)
6311 | DEF3:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6312 |  |  |  | HR6311 (Lo-16bits)
6313 | DEF3:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6314 |  |  |  | HR6313 (Lo-16bits)
6315 | DEF3:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6316 |  |  |  | HR6315 (Lo-16bits)
6317 | DEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6318 |  |  |  | HR6317 (Lo-16bits)
6319 | DEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6320 |  |  |  | HR6319 (Lo-16bits)
6321 | DEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6322 |  |  |  | HR6321 (Lo-16bits)
6323 | DEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6324 |  |  |  | HR6323 (Lo-16bits)
6325 | DEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6326 |  |  |  | HR6325 (Lo-16bits)
6327 | DEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6328 |  |  |  | HR6327 (Lo-16bits)
6329 | DEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6330 |  |  |  | HR6329 (Lo-16bits)
6331 | DEF3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6332 |  |  |  | HR6331 (Lo-16bits)
6333 | DEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6334 | DEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6335 | DEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6336 | DEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6337 | DEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6338 | DEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6339 | DEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6340 | DEF3:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6341 | DEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6342 |  |  |  | HR6341 (Lo-16bits)
6343 | DEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6344 |  |  |  | HR6343 (Lo-16bits)
6345 | DEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6346 |  |  |  | HR6345 (Lo-16bits)
6347 | DEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6348 |  |  |  | HR6347 (Lo-16bits)
6349 | DEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6350 |  |  |  | HR6349 (Lo-16bits)
6351 | DEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6352 |  |  |  | HR6351 (Lo-16bits)
6353 | DEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6354 |  |  |  | HR6353 (Lo-16bits)
6355 | DEF3:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6356 |  |  |  | HR6355 (Lo-16bits)
6357 | DEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6358 | DEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6359 | DEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6360 | DEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6361 | DEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6362 | DEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6363 | DEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6364 | DEF3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6365 | DEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6366 |  |  |  | HR6365 (Lo-16bits)
6367 | DEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6368 |  |  |  | HR6367 (Lo-16bits)
6369 | DEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6370 |  |  |  | HR6369 (Lo-16bits)
6371 | DEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6372 |  |  |  | HR6371 (Lo-16bits)
6373 | DEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6374 |  |  |  | HR6373 (Lo-16bits)
6375 | DEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6376 |  |  |  | HR6375 (Lo-16bits)
6377 | DEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6378 |  |  |  | HR6377 (Lo-16bits)
6379 | DEF3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6380 |  |  |  | HR6379 (Lo-16bits)
6381 | DEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6382 | DEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6383 | DEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6384 | DEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6385 | DEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6386 | DEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6387 | DEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6388 | DEF3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6389 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6390 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6391 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6392 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6393 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6394 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6395 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6396 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6397 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
6398 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
6399 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
6400 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
6401 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
6402 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
6403 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
6404 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
6405 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6406 |  |  |  | HR6405 (Lo-16bits)
6407 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6408 |  |  |  | HR6407 (Lo-16bits)
6409 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6410 |  |  |  | HR6409 (Lo-16bits)
6411 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6412 |  |  |  | HR6411 (Lo-16bits)
6413 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6414 |  |  |  | HR6413 (Lo-16bits)
6415 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6416 |  |  |  | HR6415 (Lo-16bits)
6417 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6418 |  |  |  | HR6417 (Lo-16bits)
6419 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6420 |  |  |  | HR6419 (Lo-16bits)
6421 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6422 |  |  |  | HR6421 (Lo-16bits)
6423 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6424 |  |  |  | HR6423 (Lo-16bits)
6425 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6426 |  |  |  | HR6425 (Lo-16bits)
6427 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6428 |  |  |  | HR6427 (Lo-16bits)
6429 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6430 |  |  |  | HR6429 (Lo-16bits)
6431 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6432 |  |  |  | HR6431 (Lo-16bits)
6433 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6434 |  |  |  | HR6433 (Lo-16bits)
6435 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6436 |  |  |  | HR6435 (Lo-16bits)
6437 | DEF4:Comp. pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6438 |  |  |  | HR6437 (Lo-16bits)
6439 | DEF4:Comp. pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6440 |  |  |  | HR6439 (Lo-16bits)
6441 | DEF4:Comp. pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6442 |  |  |  | HR6441 (Lo-16bits)
6443 | DEF4:Comp. pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6444 |  |  |  | HR6443 (Lo-16bits)
6445 | DEF4:Comp. pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6446 |  |  |  | HR6445 (Lo-16bits)
6447 | DEF4:Comp. pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6448 |  |  |  | HR6447 (Lo-16bits)
6449 | DEF4:Comp. pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6450 |  |  |  | HR6449 (Lo-16bits)
6451 | DEF4:Comp. pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6452 |  |  |  | HR6451 (Lo-16bits)
6453 | DEF4:Comp. pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6454 |  |  |  | HR6453 (Lo-16bits)
6455 | DEF4:Comp. pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6456 |  |  |  | HR6455 (Lo-16bits)
6457 | DEF4:Comp. pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6458 |  |  |  | HR6457 (Lo-16bits)
6459 | DEF4:Comp. pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6460 |  |  |  | HR6459 (Lo-16bits)
6461 | DEF4:Comp. pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6462 |  |  |  | HR6461 (Lo-16bits)
6463 | DEF4:Comp. pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6464 |  |  |  | HR6463 (Lo-16bits)
6465 | DEF4:Comp. pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6466 |  |  |  | HR6465 (Lo-16bits)
6467 | DEF4:Comp. pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6468 |  |  |  | HR6467 (Lo-16bits)
6469 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6470 |  |  |  | HR6469 (Lo-16bits)
6471 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6472 |  |  |  | HR6471 (Lo-16bits)
6473 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6474 |  |  |  | HR6473 (Lo-16bits)
6475 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6476 |  |  |  | HR6475 (Lo-16bits)
6477 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6478 |  |  |  | HR6477 (Lo-16bits)
6479 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6480 |  |  |  | HR6479 (Lo-16bits)
6481 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6482 |  |  |  | HR6481 (Lo-16bits)
6483 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
6484 |  |  |  | HR6483 (Lo-16bits)
6485 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6486 |  |  |  | HR6485 (Lo-16bits)
6487 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6488 |  |  |  | HR6487 (Lo-16bits)
6489 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6490 |  |  |  | HR6489 (Lo-16bits)
6491 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6492 |  |  |  | HR6491 (Lo-16bits)
6493 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6494 |  |  |  | HR6493 (Lo-16bits)
6495 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6496 |  |  |  | HR6495 (Lo-16bits)
6497 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6498 |  |  |  | HR6497 (Lo-16bits)
6499 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
6500 |  |  |  | HR6499 (Lo-16bits)
6501 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6502 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6503 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6504 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6505 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6506 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6507 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6508 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
6509 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6510 |  |  |  | HR6509 (Lo-16bits)
6511 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6512 |  |  |  | HR6511 (Lo-16bits)
6513 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6514 |  |  |  | HR6513 (Lo-16bits)
6515 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6516 |  |  |  | HR6515 (Lo-16bits)
6517 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6518 |  |  |  | HR6517 (Lo-16bits)
6519 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6520 |  |  |  | HR6519 (Lo-16bits)
6521 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6522 |  |  |  | HR6521 (Lo-16bits)
6523 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6524 |  |  |  | HR6523 (Lo-16bits)
6525 | DEF4:Unearth. pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6526 |  |  |  | HR6525 (Lo-16bits)
6527 | DEF4:Unearth. pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6528 |  |  |  | HR6527 (Lo-16bits)
6529 | DEF4:Unearth. pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6530 |  |  |  | HR6529 (Lo-16bits)
6531 | DEF4:Unearth. pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6532 |  |  |  | HR6531 (Lo-16bits)
6533 | DEF4:Unearth. pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6534 |  |  |  | HR6533 (Lo-16bits)
6535 | DEF4:Unearth. pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6536 |  |  |  | HR6535 (Lo-16bits)
6537 | DEF4:Unearth. pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6538 |  |  |  | HR6537 (Lo-16bits)
6539 | DEF4:Unearth. pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6540 |  |  |  | HR6539 (Lo-16bits)
6541 | DEF4:Unearth. pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6542 |  |  |  | HR6541 (Lo-16bits)
6543 | DEF4:Unearth. pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6544 |  |  |  | HR6543 (Lo-16bits)
6545 | DEF4:Unearth. pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6546 |  |  |  | HR6545 (Lo-16bits)
6547 | DEF4:Unearth. pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6548 |  |  |  | HR6547 (Lo-16bits)
6549 | DEF4:Unearth. pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6550 |  |  |  | HR6549 (Lo-16bits)
6551 | DEF4:Unearth. pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6552 |  |  |  | HR6551 (Lo-16bits)
6553 | DEF4:Unearth. pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6554 |  |  |  | HR6553 (Lo-16bits)
6555 | DEF4:Unearth. pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6556 |  |  |  | HR6555 (Lo-16bits)
6557 | DEF4:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6558 |  |  |  | HR6557 (Lo-16bits)
6559 | DEF4:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6560 |  |  |  | HR6559 (Lo-16bits)
6561 | DEF4:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6562 |  |  |  | HR6561 (Lo-16bits)
6563 | DEF4:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6564 |  |  |  | HR6563 (Lo-16bits)
6565 | DEF4:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6566 |  |  |  | HR6565 (Lo-16bits)
6567 | DEF4:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6568 |  |  |  | HR6567 (Lo-16bits)
6569 | DEF4:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6570 |  |  |  | HR6569 (Lo-16bits)
6571 | DEF4:Tripping area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6572 |  |  |  | HR6571 (Lo-16bits)
6573 | DEF4:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6574 |  |  |  | HR6573 (Lo-16bits)
6575 | DEF4:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6576 |  |  |  | HR6575 (Lo-16bits)
6577 | DEF4:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6578 |  |  |  | HR6577 (Lo-16bits)
6579 | DEF4:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6580 |  |  |  | HR6579 (Lo-16bits)
6581 | DEF4:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6582 |  |  |  | HR6581 (Lo-16bits)
6583 | DEF4:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6584 |  |  |  | HR6583 (Lo-16bits)
6585 | DEF4:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6586 |  |  |  | HR6585 (Lo-16bits)
6587 | DEF4:Tripping area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6588 |  |  |  | HR6587 (Lo-16bits)
6589 | DEF4:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6590 | DEF4:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6591 | DEF4:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6592 | DEF4:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6593 | DEF4:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6594 | DEF4:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6595 | DEF4:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6596 | DEF4:Delay type of broad range characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6597 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6598 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6599 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6600 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6601 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6602 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6603 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6604 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6605 | DEF4:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6606 |  |  |  | HR6605 (Lo-16bits)
6607 | DEF4:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6608 |  |  |  | HR6607 (Lo-16bits)
6609 | DEF4:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6610 |  |  |  | HR6609 (Lo-16bits)
6611 | DEF4:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6612 |  |  |  | HR6611 (Lo-16bits)
6613 | DEF4:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6614 |  |  |  | HR6613 (Lo-16bits)
6615 | DEF4:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6616 |  |  |  | HR6615 (Lo-16bits)
6617 | DEF4:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6618 |  |  |  | HR6617 (Lo-16bits)
6619 | DEF4:Definite operating time delay (Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6620 |  |  |  | HR6619 (Lo-16bits)
6621 | DEF4:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6622 |  |  |  | HR6621 (Lo-16bits)
6623 | DEF4:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6624 |  |  |  | HR6623 (Lo-16bits)
6625 | DEF4:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6626 |  |  |  | HR6625 (Lo-16bits)
6627 | DEF4:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6628 |  |  |  | HR6627 (Lo-16bits)
6629 | DEF4:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6630 |  |  |  | HR6629 (Lo-16bits)
6631 | DEF4:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6632 |  |  |  | HR6631 (Lo-16bits)
6633 | DEF4:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6634 |  |  |  | HR6633 (Lo-16bits)
6635 | DEF4:Definite operating time delay (Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6636 |  |  |  | HR6635 (Lo-16bits)
6637 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6638 |  |  |  | HR6637 (Lo-16bits)
6639 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6640 |  |  |  | HR6639 (Lo-16bits)
6641 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6642 |  |  |  | HR6641 (Lo-16bits)
6643 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6644 |  |  |  | HR6643 (Lo-16bits)
6645 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6646 |  |  |  | HR6645 (Lo-16bits)
6647 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6648 |  |  |  | HR6647 (Lo-16bits)
6649 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6650 |  |  |  | HR6649 (Lo-16bits)
6651 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6652 |  |  |  | HR6651 (Lo-16bits)
6653 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6654 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6655 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6656 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6657 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6658 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6659 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6660 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6661 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6662 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6663 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6664 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6665 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6666 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6667 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6668 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6669 | DEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6670 | DEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6671 | DEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6672 | DEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6673 | DEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6674 | DEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6675 | DEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6676 | DEF4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6677 | DEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6678 | DEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6679 | DEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6680 | DEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6681 | DEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6682 | DEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6683 | DEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6684 | DEF4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type
6685 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6686 |  |  |  | HR6685 (Lo-16bits)
6687 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6688 |  |  |  | HR6687 (Lo-16bits)
6689 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6690 |  |  |  | HR6689 (Lo-16bits)
6691 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6692 |  |  |  | HR6691 (Lo-16bits)
6693 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6694 |  |  |  | HR6693 (Lo-16bits)
6695 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6696 |  |  |  | HR6695 (Lo-16bits)
6697 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6698 |  |  |  | HR6697 (Lo-16bits)
6699 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6700 |  |  |  | HR6699 (Lo-16bits)
6701 | DEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6702 |  |  |  | HR6701 (Lo-16bits)
6703 | DEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6704 |  |  |  | HR6703 (Lo-16bits)
6705 | DEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6706 |  |  |  | HR6705 (Lo-16bits)
6707 | DEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6708 |  |  |  | HR6707 (Lo-16bits)
6709 | DEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6710 |  |  |  | HR6709 (Lo-16bits)
6711 | DEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6712 |  |  |  | HR6711 (Lo-16bits)
6713 | DEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6714 |  |  |  | HR6713 (Lo-16bits)
6715 | DEF4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6716 |  |  |  | HR6715 (Lo-16bits)
6717 | DEF4:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6718 |  |  |  | HR6717 (Lo-16bits)
6719 | DEF4:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6720 |  |  |  | HR6719 (Lo-16bits)
6721 | DEF4:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6722 |  |  |  | HR6721 (Lo-16bits)
6723 | DEF4:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6724 |  |  |  | HR6723 (Lo-16bits)
6725 | DEF4:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6726 |  |  |  | HR6725 (Lo-16bits)
6727 | DEF4:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6728 |  |  |  | HR6727 (Lo-16bits)
6729 | DEF4:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6730 |  |  |  | HR6729 (Lo-16bits)
6731 | DEF4:IDMT constant B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6732 |  |  |  | HR6731 (Lo-16bits)
6733 | DEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6734 |  |  |  | HR6733 (Lo-16bits)
6735 | DEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6736 |  |  |  | HR6735 (Lo-16bits)
6737 | DEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6738 |  |  |  | HR6737 (Lo-16bits)
6739 | DEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6740 |  |  |  | HR6739 (Lo-16bits)
6741 | DEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6742 |  |  |  | HR6741 (Lo-16bits)
6743 | DEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6744 |  |  |  | HR6743 (Lo-16bits)
6745 | DEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6746 |  |  |  | HR6745 (Lo-16bits)
6747 | DEF4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6748 |  |  |  | HR6747 (Lo-16bits)
6749 | DEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6750 | DEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6751 | DEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6752 | DEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6753 | DEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6754 | DEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6755 | DEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6756 | DEF4:Inrush harmonic blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6757 | DEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6758 |  |  |  | HR6757 (Lo-16bits)
6759 | DEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6760 |  |  |  | HR6759 (Lo-16bits)
6761 | DEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6762 |  |  |  | HR6761 (Lo-16bits)
6763 | DEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6764 |  |  |  | HR6763 (Lo-16bits)
6765 | DEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6766 |  |  |  | HR6765 (Lo-16bits)
6767 | DEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6768 |  |  |  | HR6767 (Lo-16bits)
6769 | DEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6770 |  |  |  | HR6769 (Lo-16bits)
6771 | DEF4:2nd harmonic blocking limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6772 |  |  |  | HR6771 (Lo-16bits)
6773 | DEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6774 | DEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6775 | DEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6776 | DEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6777 | DEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6778 | DEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6779 | DEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6780 | DEF4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6781 | DEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6782 |  |  |  | HR6781 (Lo-16bits)
6783 | DEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6784 |  |  |  | HR6783 (Lo-16bits)
6785 | DEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6786 |  |  |  | HR6785 (Lo-16bits)
6787 | DEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6788 |  |  |  | HR6787 (Lo-16bits)
6789 | DEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6790 |  |  |  | HR6789 (Lo-16bits)
6791 | DEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6792 |  |  |  | HR6791 (Lo-16bits)
6793 | DEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6794 |  |  |  | HR6793 (Lo-16bits)
6795 | DEF4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6796 |  |  |  | HR6795 (Lo-16bits)
6797 | DEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6798 | DEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6799 | DEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6800 | DEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6801 | DEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6802 | DEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6803 | DEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6804 | DEF4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
6805 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6806 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6807 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6808 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6809 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6810 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6811 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6812 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6813 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6814 |  |  |  | HR6813 (Lo-16bits)
6815 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6816 |  |  |  | HR6815 (Lo-16bits)
6817 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6818 |  |  |  | HR6817 (Lo-16bits)
6819 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6820 |  |  |  | HR6819 (Lo-16bits)
6821 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6822 |  |  |  | HR6821 (Lo-16bits)
6823 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6824 |  |  |  | HR6823 (Lo-16bits)
6825 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6826 |  |  |  | HR6825 (Lo-16bits)
6827 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6828 |  |  |  | HR6827 (Lo-16bits)
6829 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6830 |  |  |  | HR6829 (Lo-16bits)
6831 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6832 |  |  |  | HR6831 (Lo-16bits)
6833 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6834 |  |  |  | HR6833 (Lo-16bits)
6835 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6836 |  |  |  | HR6835 (Lo-16bits)
6837 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6838 |  |  |  | HR6837 (Lo-16bits)
6839 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6840 |  |  |  | HR6839 (Lo-16bits)
6841 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6842 |  |  |  | HR6841 (Lo-16bits)
6843 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6844 |  |  |  | HR6843 (Lo-16bits)
6845 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6846 |  |  |  | HR6845 (Lo-16bits)
6847 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6848 |  |  |  | HR6847 (Lo-16bits)
6849 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6850 |  |  |  | HR6849 (Lo-16bits)
6851 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6852 |  |  |  | HR6851 (Lo-16bits)
6853 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6854 |  |  |  | HR6853 (Lo-16bits)
6855 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6856 |  |  |  | HR6855 (Lo-16bits)
6857 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6858 |  |  |  | HR6857 (Lo-16bits)
6859 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6860 |  |  |  | HR6859 (Lo-16bits)
6861 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6862 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6863 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6864 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6865 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6866 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6867 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6868 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6869 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6870 |  |  |  | HR6869 (Lo-16bits)
6871 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6872 |  |  |  | HR6871 (Lo-16bits)
6873 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6874 |  |  |  | HR6873 (Lo-16bits)
6875 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6876 |  |  |  | HR6875 (Lo-16bits)
6877 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6878 |  |  |  | HR6877 (Lo-16bits)
6879 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6880 |  |  |  | HR6879 (Lo-16bits)
6881 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6882 |  |  |  | HR6881 (Lo-16bits)
6883 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6884 |  |  |  | HR6883 (Lo-16bits)
6885 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6886 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6887 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6888 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6889 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6890 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6891 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6892 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6893 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6894 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6895 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6896 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6897 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6898 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6899 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6900 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6901 | CUB1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6902 | CUB1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6903 | CUB1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6904 | CUB1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6905 | CUB1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6906 | CUB1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6907 | CUB1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6908 | CUB1:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6909 | CUB1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6910 | CUB1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6911 | CUB1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6912 | CUB1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6913 | CUB1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6914 | CUB1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6915 | CUB1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6916 | CUB1:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6917 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6918 |  |  |  | HR6917 (Lo-16bits)
6919 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6920 |  |  |  | HR6919 (Lo-16bits)
6921 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6922 |  |  |  | HR6921 (Lo-16bits)
6923 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6924 |  |  |  | HR6923 (Lo-16bits)
6925 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6926 |  |  |  | HR6925 (Lo-16bits)
6927 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6928 |  |  |  | HR6927 (Lo-16bits)
6929 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6930 |  |  |  | HR6929 (Lo-16bits)
6931 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6932 |  |  |  | HR6931 (Lo-16bits)
6933 | CUB1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6934 |  |  |  | HR6933 (Lo-16bits)
6935 | CUB1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6936 |  |  |  | HR6935 (Lo-16bits)
6937 | CUB1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6938 |  |  |  | HR6937 (Lo-16bits)
6939 | CUB1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6940 |  |  |  | HR6939 (Lo-16bits)
6941 | CUB1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6942 |  |  |  | HR6941 (Lo-16bits)
6943 | CUB1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6944 |  |  |  | HR6943 (Lo-16bits)
6945 | CUB1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6946 |  |  |  | HR6945 (Lo-16bits)
6947 | CUB1:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6948 |  |  |  | HR6947 (Lo-16bits)
6949 | CUB1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
6950 |  |  |  | HR6949 (Lo-16bits)
6951 | CUB1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
6952 |  |  |  | HR6951 (Lo-16bits)
6953 | CUB1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
6954 |  |  |  | HR6953 (Lo-16bits)
6955 | CUB1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
6956 |  |  |  | HR6955 (Lo-16bits)
6957 | CUB1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
6958 |  |  |  | HR6957 (Lo-16bits)
6959 | CUB1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
6960 |  |  |  | HR6959 (Lo-16bits)
6961 | CUB1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
6962 |  |  |  | HR6961 (Lo-16bits)
6963 | CUB1:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
6964 |  |  |  | HR6963 (Lo-16bits)
6965 | CUB1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6966 |  |  |  | HR6965 (Lo-16bits)
6967 | CUB1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6968 |  |  |  | HR6967 (Lo-16bits)
6969 | CUB1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6970 |  |  |  | HR6969 (Lo-16bits)
6971 | CUB1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6972 |  |  |  | HR6971 (Lo-16bits)
6973 | CUB1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6974 |  |  |  | HR6973 (Lo-16bits)
6975 | CUB1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6976 |  |  |  | HR6975 (Lo-16bits)
6977 | CUB1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6978 |  |  |  | HR6977 (Lo-16bits)
6979 | CUB1:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6980 |  |  |  | HR6979 (Lo-16bits)
6981 | CUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6982 | CUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6983 | CUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6984 | CUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6985 | CUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6986 | CUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6987 | CUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6988 | CUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
6989 | CUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6990 |  |  |  | HR6989 (Lo-16bits)
6991 | CUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6992 |  |  |  | HR6991 (Lo-16bits)
6993 | CUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6994 |  |  |  | HR6993 (Lo-16bits)
6995 | CUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6996 |  |  |  | HR6995 (Lo-16bits)
6997 | CUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6998 |  |  |  | HR6997 (Lo-16bits)
6999 | CUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7000 |  |  |  | HR6999 (Lo-16bits)
7001 | CUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7002 |  |  |  | HR7001 (Lo-16bits)
7003 | CUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7004 |  |  |  | HR7003 (Lo-16bits)
7005 | CUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7006 | CUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7007 | CUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7008 | CUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7009 | CUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7010 | CUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7011 | CUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7012 | CUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7013 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7014 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7015 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7016 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7017 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7018 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7019 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7020 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7021 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7022 |  |  |  | HR7021 (Lo-16bits)
7023 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7024 |  |  |  | HR7023 (Lo-16bits)
7025 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7026 |  |  |  | HR7025 (Lo-16bits)
7027 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7028 |  |  |  | HR7027 (Lo-16bits)
7029 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7030 |  |  |  | HR7029 (Lo-16bits)
7031 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7032 |  |  |  | HR7031 (Lo-16bits)
7033 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7034 |  |  |  | HR7033 (Lo-16bits)
7035 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7036 |  |  |  | HR7035 (Lo-16bits)
7037 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7038 |  |  |  | HR7037 (Lo-16bits)
7039 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7040 |  |  |  | HR7039 (Lo-16bits)
7041 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7042 |  |  |  | HR7041 (Lo-16bits)
7043 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7044 |  |  |  | HR7043 (Lo-16bits)
7045 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7046 |  |  |  | HR7045 (Lo-16bits)
7047 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7048 |  |  |  | HR7047 (Lo-16bits)
7049 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7050 |  |  |  | HR7049 (Lo-16bits)
7051 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7052 |  |  |  | HR7051 (Lo-16bits)
7053 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7054 |  |  |  | HR7053 (Lo-16bits)
7055 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7056 |  |  |  | HR7055 (Lo-16bits)
7057 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7058 |  |  |  | HR7057 (Lo-16bits)
7059 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7060 |  |  |  | HR7059 (Lo-16bits)
7061 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7062 |  |  |  | HR7061 (Lo-16bits)
7063 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7064 |  |  |  | HR7063 (Lo-16bits)
7065 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7066 |  |  |  | HR7065 (Lo-16bits)
7067 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7068 |  |  |  | HR7067 (Lo-16bits)
7069 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7070 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7071 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7072 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7073 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7074 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7075 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7076 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7077 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7078 |  |  |  | HR7077 (Lo-16bits)
7079 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7080 |  |  |  | HR7079 (Lo-16bits)
7081 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7082 |  |  |  | HR7081 (Lo-16bits)
7083 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7084 |  |  |  | HR7083 (Lo-16bits)
7085 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7086 |  |  |  | HR7085 (Lo-16bits)
7087 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7088 |  |  |  | HR7087 (Lo-16bits)
7089 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7090 |  |  |  | HR7089 (Lo-16bits)
7091 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7092 |  |  |  | HR7091 (Lo-16bits)
7093 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7094 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7095 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7096 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7097 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7098 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7099 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7100 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7101 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7102 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7103 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7104 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7105 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7106 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7107 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7108 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7109 | CUB2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7110 | CUB2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7111 | CUB2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7112 | CUB2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7113 | CUB2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7114 | CUB2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7115 | CUB2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7116 | CUB2:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7117 | CUB2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7118 | CUB2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7119 | CUB2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7120 | CUB2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7121 | CUB2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7122 | CUB2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7123 | CUB2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7124 | CUB2:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7125 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7126 |  |  |  | HR7125 (Lo-16bits)
7127 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7128 |  |  |  | HR7127 (Lo-16bits)
7129 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7130 |  |  |  | HR7129 (Lo-16bits)
7131 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7132 |  |  |  | HR7131 (Lo-16bits)
7133 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7134 |  |  |  | HR7133 (Lo-16bits)
7135 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7136 |  |  |  | HR7135 (Lo-16bits)
7137 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7138 |  |  |  | HR7137 (Lo-16bits)
7139 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7140 |  |  |  | HR7139 (Lo-16bits)
7141 | CUB2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7142 |  |  |  | HR7141 (Lo-16bits)
7143 | CUB2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7144 |  |  |  | HR7143 (Lo-16bits)
7145 | CUB2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7146 |  |  |  | HR7145 (Lo-16bits)
7147 | CUB2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7148 |  |  |  | HR7147 (Lo-16bits)
7149 | CUB2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7150 |  |  |  | HR7149 (Lo-16bits)
7151 | CUB2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7152 |  |  |  | HR7151 (Lo-16bits)
7153 | CUB2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7154 |  |  |  | HR7153 (Lo-16bits)
7155 | CUB2:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7156 |  |  |  | HR7155 (Lo-16bits)
7157 | CUB2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7158 |  |  |  | HR7157 (Lo-16bits)
7159 | CUB2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7160 |  |  |  | HR7159 (Lo-16bits)
7161 | CUB2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7162 |  |  |  | HR7161 (Lo-16bits)
7163 | CUB2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7164 |  |  |  | HR7163 (Lo-16bits)
7165 | CUB2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7166 |  |  |  | HR7165 (Lo-16bits)
7167 | CUB2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7168 |  |  |  | HR7167 (Lo-16bits)
7169 | CUB2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7170 |  |  |  | HR7169 (Lo-16bits)
7171 | CUB2:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7172 |  |  |  | HR7171 (Lo-16bits)
7173 | CUB2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7174 |  |  |  | HR7173 (Lo-16bits)
7175 | CUB2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7176 |  |  |  | HR7175 (Lo-16bits)
7177 | CUB2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7178 |  |  |  | HR7177 (Lo-16bits)
7179 | CUB2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7180 |  |  |  | HR7179 (Lo-16bits)
7181 | CUB2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7182 |  |  |  | HR7181 (Lo-16bits)
7183 | CUB2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7184 |  |  |  | HR7183 (Lo-16bits)
7185 | CUB2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7186 |  |  |  | HR7185 (Lo-16bits)
7187 | CUB2:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7188 |  |  |  | HR7187 (Lo-16bits)
7189 | CUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7190 | CUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7191 | CUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7192 | CUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7193 | CUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7194 | CUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7195 | CUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7196 | CUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7197 | CUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7198 |  |  |  | HR7197 (Lo-16bits)
7199 | CUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7200 |  |  |  | HR7199 (Lo-16bits)
7201 | CUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7202 |  |  |  | HR7201 (Lo-16bits)
7203 | CUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7204 |  |  |  | HR7203 (Lo-16bits)
7205 | CUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7206 |  |  |  | HR7205 (Lo-16bits)
7207 | CUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7208 |  |  |  | HR7207 (Lo-16bits)
7209 | CUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7210 |  |  |  | HR7209 (Lo-16bits)
7211 | CUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7212 |  |  |  | HR7211 (Lo-16bits)
7213 | CUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7214 | CUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7215 | CUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7216 | CUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7217 | CUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7218 | CUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7219 | CUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7220 | CUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7221 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7222 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7223 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7224 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7225 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7226 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7227 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7228 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7229 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7230 |  |  |  | HR7229 (Lo-16bits)
7231 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7232 |  |  |  | HR7231 (Lo-16bits)
7233 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7234 |  |  |  | HR7233 (Lo-16bits)
7235 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7236 |  |  |  | HR7235 (Lo-16bits)
7237 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7238 |  |  |  | HR7237 (Lo-16bits)
7239 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7240 |  |  |  | HR7239 (Lo-16bits)
7241 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7242 |  |  |  | HR7241 (Lo-16bits)
7243 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7244 |  |  |  | HR7243 (Lo-16bits)
7245 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7246 |  |  |  | HR7245 (Lo-16bits)
7247 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7248 |  |  |  | HR7247 (Lo-16bits)
7249 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7250 |  |  |  | HR7249 (Lo-16bits)
7251 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7252 |  |  |  | HR7251 (Lo-16bits)
7253 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7254 |  |  |  | HR7253 (Lo-16bits)
7255 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7256 |  |  |  | HR7255 (Lo-16bits)
7257 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7258 |  |  |  | HR7257 (Lo-16bits)
7259 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7260 |  |  |  | HR7259 (Lo-16bits)
7261 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7262 |  |  |  | HR7261 (Lo-16bits)
7263 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7264 |  |  |  | HR7263 (Lo-16bits)
7265 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7266 |  |  |  | HR7265 (Lo-16bits)
7267 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7268 |  |  |  | HR7267 (Lo-16bits)
7269 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7270 |  |  |  | HR7269 (Lo-16bits)
7271 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7272 |  |  |  | HR7271 (Lo-16bits)
7273 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7274 |  |  |  | HR7273 (Lo-16bits)
7275 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7276 |  |  |  | HR7275 (Lo-16bits)
7277 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7278 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7279 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7280 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7281 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7282 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7283 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7284 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7285 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7286 |  |  |  | HR7285 (Lo-16bits)
7287 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7288 |  |  |  | HR7287 (Lo-16bits)
7289 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7290 |  |  |  | HR7289 (Lo-16bits)
7291 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7292 |  |  |  | HR7291 (Lo-16bits)
7293 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7294 |  |  |  | HR7293 (Lo-16bits)
7295 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7296 |  |  |  | HR7295 (Lo-16bits)
7297 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7298 |  |  |  | HR7297 (Lo-16bits)
7299 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7300 |  |  |  | HR7299 (Lo-16bits)
7301 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7302 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7303 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7304 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7305 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7306 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7307 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7308 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7309 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7310 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7311 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7312 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7313 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7314 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7315 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7316 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7317 | CUB3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7318 | CUB3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7319 | CUB3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7320 | CUB3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7321 | CUB3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7322 | CUB3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7323 | CUB3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7324 | CUB3:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7325 | CUB3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7326 | CUB3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7327 | CUB3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7328 | CUB3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7329 | CUB3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7330 | CUB3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7331 | CUB3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7332 | CUB3:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7333 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7334 |  |  |  | HR7333 (Lo-16bits)
7335 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7336 |  |  |  | HR7335 (Lo-16bits)
7337 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7338 |  |  |  | HR7337 (Lo-16bits)
7339 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7340 |  |  |  | HR7339 (Lo-16bits)
7341 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7342 |  |  |  | HR7341 (Lo-16bits)
7343 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7344 |  |  |  | HR7343 (Lo-16bits)
7345 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7346 |  |  |  | HR7345 (Lo-16bits)
7347 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7348 |  |  |  | HR7347 (Lo-16bits)
7349 | CUB3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7350 |  |  |  | HR7349 (Lo-16bits)
7351 | CUB3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7352 |  |  |  | HR7351 (Lo-16bits)
7353 | CUB3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7354 |  |  |  | HR7353 (Lo-16bits)
7355 | CUB3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7356 |  |  |  | HR7355 (Lo-16bits)
7357 | CUB3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7358 |  |  |  | HR7357 (Lo-16bits)
7359 | CUB3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7360 |  |  |  | HR7359 (Lo-16bits)
7361 | CUB3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7362 |  |  |  | HR7361 (Lo-16bits)
7363 | CUB3:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7364 |  |  |  | HR7363 (Lo-16bits)
7365 | CUB3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7366 |  |  |  | HR7365 (Lo-16bits)
7367 | CUB3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7368 |  |  |  | HR7367 (Lo-16bits)
7369 | CUB3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7370 |  |  |  | HR7369 (Lo-16bits)
7371 | CUB3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7372 |  |  |  | HR7371 (Lo-16bits)
7373 | CUB3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7374 |  |  |  | HR7373 (Lo-16bits)
7375 | CUB3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7376 |  |  |  | HR7375 (Lo-16bits)
7377 | CUB3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7378 |  |  |  | HR7377 (Lo-16bits)
7379 | CUB3:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7380 |  |  |  | HR7379 (Lo-16bits)
7381 | CUB3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7382 |  |  |  | HR7381 (Lo-16bits)
7383 | CUB3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7384 |  |  |  | HR7383 (Lo-16bits)
7385 | CUB3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7386 |  |  |  | HR7385 (Lo-16bits)
7387 | CUB3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7388 |  |  |  | HR7387 (Lo-16bits)
7389 | CUB3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7390 |  |  |  | HR7389 (Lo-16bits)
7391 | CUB3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7392 |  |  |  | HR7391 (Lo-16bits)
7393 | CUB3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7394 |  |  |  | HR7393 (Lo-16bits)
7395 | CUB3:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7396 |  |  |  | HR7395 (Lo-16bits)
7397 | CUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7398 | CUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7399 | CUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7400 | CUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7401 | CUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7402 | CUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7403 | CUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7404 | CUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7405 | CUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7406 |  |  |  | HR7405 (Lo-16bits)
7407 | CUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7408 |  |  |  | HR7407 (Lo-16bits)
7409 | CUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7410 |  |  |  | HR7409 (Lo-16bits)
7411 | CUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7412 |  |  |  | HR7411 (Lo-16bits)
7413 | CUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7414 |  |  |  | HR7413 (Lo-16bits)
7415 | CUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7416 |  |  |  | HR7415 (Lo-16bits)
7417 | CUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7418 |  |  |  | HR7417 (Lo-16bits)
7419 | CUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7420 |  |  |  | HR7419 (Lo-16bits)
7421 | CUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7422 | CUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7423 | CUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7424 | CUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7425 | CUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7426 | CUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7427 | CUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7428 | CUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7429 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7430 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7431 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7432 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7433 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7434 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7435 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7436 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7437 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7438 |  |  |  | HR7437 (Lo-16bits)
7439 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7440 |  |  |  | HR7439 (Lo-16bits)
7441 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7442 |  |  |  | HR7441 (Lo-16bits)
7443 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7444 |  |  |  | HR7443 (Lo-16bits)
7445 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7446 |  |  |  | HR7445 (Lo-16bits)
7447 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7448 |  |  |  | HR7447 (Lo-16bits)
7449 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7450 |  |  |  | HR7449 (Lo-16bits)
7451 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
7452 |  |  |  | HR7451 (Lo-16bits)
7453 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7454 |  |  |  | HR7453 (Lo-16bits)
7455 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7456 |  |  |  | HR7455 (Lo-16bits)
7457 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7458 |  |  |  | HR7457 (Lo-16bits)
7459 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7460 |  |  |  | HR7459 (Lo-16bits)
7461 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7462 |  |  |  | HR7461 (Lo-16bits)
7463 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7464 |  |  |  | HR7463 (Lo-16bits)
7465 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7466 |  |  |  | HR7465 (Lo-16bits)
7467 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
7468 |  |  |  | HR7467 (Lo-16bits)
7469 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7470 |  |  |  | HR7469 (Lo-16bits)
7471 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7472 |  |  |  | HR7471 (Lo-16bits)
7473 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7474 |  |  |  | HR7473 (Lo-16bits)
7475 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7476 |  |  |  | HR7475 (Lo-16bits)
7477 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7478 |  |  |  | HR7477 (Lo-16bits)
7479 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7480 |  |  |  | HR7479 (Lo-16bits)
7481 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7482 |  |  |  | HR7481 (Lo-16bits)
7483 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
7484 |  |  |  | HR7483 (Lo-16bits)
7485 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7486 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7487 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7488 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7489 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7490 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7491 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7492 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7493 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7494 |  |  |  | HR7493 (Lo-16bits)
7495 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7496 |  |  |  | HR7495 (Lo-16bits)
7497 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7498 |  |  |  | HR7497 (Lo-16bits)
7499 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7500 |  |  |  | HR7499 (Lo-16bits)
7501 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7502 |  |  |  | HR7501 (Lo-16bits)
7503 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7504 |  |  |  | HR7503 (Lo-16bits)
7505 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7506 |  |  |  | HR7505 (Lo-16bits)
7507 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7508 |  |  |  | HR7507 (Lo-16bits)
7509 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7510 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7511 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7512 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7513 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7514 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7515 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7516 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7517 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7518 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7519 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7520 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7521 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7522 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7523 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7524 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7525 | CUB4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7526 | CUB4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7527 | CUB4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7528 | CUB4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7529 | CUB4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7530 | CUB4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7531 | CUB4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7532 | CUB4:Delay characteristics ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7533 | CUB4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7534 | CUB4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7535 | CUB4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7536 | CUB4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7537 | CUB4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7538 | CUB4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7539 | CUB4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7540 | CUB4:Non-standard delay characteristics | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7541 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7542 |  |  |  | HR7541 (Lo-16bits)
7543 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7544 |  |  |  | HR7543 (Lo-16bits)
7545 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7546 |  |  |  | HR7545 (Lo-16bits)
7547 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7548 |  |  |  | HR7547 (Lo-16bits)
7549 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7550 |  |  |  | HR7549 (Lo-16bits)
7551 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7552 |  |  |  | HR7551 (Lo-16bits)
7553 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7554 |  |  |  | HR7553 (Lo-16bits)
7555 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7556 |  |  |  | HR7555 (Lo-16bits)
7557 | CUB4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7558 |  |  |  | HR7557 (Lo-16bits)
7559 | CUB4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7560 |  |  |  | HR7559 (Lo-16bits)
7561 | CUB4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7562 |  |  |  | HR7561 (Lo-16bits)
7563 | CUB4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7564 |  |  |  | HR7563 (Lo-16bits)
7565 | CUB4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7566 |  |  |  | HR7565 (Lo-16bits)
7567 | CUB4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7568 |  |  |  | HR7567 (Lo-16bits)
7569 | CUB4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7570 |  |  |  | HR7569 (Lo-16bits)
7571 | CUB4:IDMT constant A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7572 |  |  |  | HR7571 (Lo-16bits)
7573 | CUB4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7574 |  |  |  | HR7573 (Lo-16bits)
7575 | CUB4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7576 |  |  |  | HR7575 (Lo-16bits)
7577 | CUB4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7578 |  |  |  | HR7577 (Lo-16bits)
7579 | CUB4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7580 |  |  |  | HR7579 (Lo-16bits)
7581 | CUB4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7582 |  |  |  | HR7581 (Lo-16bits)
7583 | CUB4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7584 |  |  |  | HR7583 (Lo-16bits)
7585 | CUB4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7586 |  |  |  | HR7585 (Lo-16bits)
7587 | CUB4:IDMT constant B | R(W) | 2 | FLOAT [0...5] (Hi-16bits)
7588 |  |  |  | HR7587 (Lo-16bits)
7589 | CUB4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7590 |  |  |  | HR7589 (Lo-16bits)
7591 | CUB4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7592 |  |  |  | HR7591 (Lo-16bits)
7593 | CUB4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7594 |  |  |  | HR7593 (Lo-16bits)
7595 | CUB4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7596 |  |  |  | HR7595 (Lo-16bits)
7597 | CUB4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7598 |  |  |  | HR7597 (Lo-16bits)
7599 | CUB4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7600 |  |  |  | HR7599 (Lo-16bits)
7601 | CUB4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7602 |  |  |  | HR7601 (Lo-16bits)
7603 | CUB4:IDMT constant C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7604 |  |  |  | HR7603 (Lo-16bits)
7605 | CUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7606 | CUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7607 | CUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7608 | CUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7609 | CUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7610 | CUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7611 | CUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7612 | CUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7613 | CUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7614 |  |  |  | HR7613 (Lo-16bits)
7615 | CUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7616 |  |  |  | HR7615 (Lo-16bits)
7617 | CUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7618 |  |  |  | HR7617 (Lo-16bits)
7619 | CUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7620 |  |  |  | HR7619 (Lo-16bits)
7621 | CUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7622 |  |  |  | HR7621 (Lo-16bits)
7623 | CUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7624 |  |  |  | HR7623 (Lo-16bits)
7625 | CUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7626 |  |  |  | HR7625 (Lo-16bits)
7627 | CUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7628 |  |  |  | HR7627 (Lo-16bits)
7629 | CUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7630 | CUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7631 | CUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7632 | CUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7633 | CUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7634 | CUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7635 | CUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7636 | CUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7637 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7638 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7639 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7640 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7641 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7642 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7643 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7644 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7645 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7646 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7647 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7648 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7649 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7650 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7651 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7652 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7653 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7654 |  |  |  | HR7653 (Lo-16bits)
7655 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7656 |  |  |  | HR7655 (Lo-16bits)
7657 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7658 |  |  |  | HR7657 (Lo-16bits)
7659 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7660 |  |  |  | HR7659 (Lo-16bits)
7661 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7662 |  |  |  | HR7661 (Lo-16bits)
7663 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7664 |  |  |  | HR7663 (Lo-16bits)
7665 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7666 |  |  |  | HR7665 (Lo-16bits)
7667 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7668 |  |  |  | HR7667 (Lo-16bits)
7669 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7670 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7671 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7672 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7673 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7674 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7675 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7676 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7677 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7678 |  |  |  | HR7677 (Lo-16bits)
7679 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7680 |  |  |  | HR7679 (Lo-16bits)
7681 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7682 |  |  |  | HR7681 (Lo-16bits)
7683 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7684 |  |  |  | HR7683 (Lo-16bits)
7685 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7686 |  |  |  | HR7685 (Lo-16bits)
7687 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7688 |  |  |  | HR7687 (Lo-16bits)
7689 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7690 |  |  |  | HR7689 (Lo-16bits)
7691 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7692 |  |  |  | HR7691 (Lo-16bits)
7693 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7694 |  |  |  | HR7693 (Lo-16bits)
7695 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7696 |  |  |  | HR7695 (Lo-16bits)
7697 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7698 |  |  |  | HR7697 (Lo-16bits)
7699 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7700 |  |  |  | HR7699 (Lo-16bits)
7701 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7702 |  |  |  | HR7701 (Lo-16bits)
7703 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7704 |  |  |  | HR7703 (Lo-16bits)
7705 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7706 |  |  |  | HR7705 (Lo-16bits)
7707 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7708 |  |  |  | HR7707 (Lo-16bits)
7709 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7710 |  |  |  | HR7709 (Lo-16bits)
7711 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7712 |  |  |  | HR7711 (Lo-16bits)
7713 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7714 |  |  |  | HR7713 (Lo-16bits)
7715 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7716 |  |  |  | HR7715 (Lo-16bits)
7717 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7718 |  |  |  | HR7717 (Lo-16bits)
7719 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7720 |  |  |  | HR7719 (Lo-16bits)
7721 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7722 |  |  |  | HR7721 (Lo-16bits)
7723 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7724 |  |  |  | HR7723 (Lo-16bits)
7725 | OV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7726 |  |  |  | HR7725 (Lo-16bits)
7727 | OV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7728 |  |  |  | HR7727 (Lo-16bits)
7729 | OV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7730 |  |  |  | HR7729 (Lo-16bits)
7731 | OV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7732 |  |  |  | HR7731 (Lo-16bits)
7733 | OV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7734 |  |  |  | HR7733 (Lo-16bits)
7735 | OV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7736 |  |  |  | HR7735 (Lo-16bits)
7737 | OV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7738 |  |  |  | HR7737 (Lo-16bits)
7739 | OV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7740 |  |  |  | HR7739 (Lo-16bits)
7741 | OV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7742 | OV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7743 | OV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7744 | OV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7745 | OV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7746 | OV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7747 | OV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7748 | OV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7749 | OV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7750 | OV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7751 | OV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7752 | OV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7753 | OV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7754 | OV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7755 | OV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7756 | OV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7757 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7758 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7759 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7760 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7761 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7762 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7763 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7764 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7765 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7766 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7767 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7768 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7769 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7770 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7771 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7772 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7773 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7774 |  |  |  | HR7773 (Lo-16bits)
7775 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7776 |  |  |  | HR7775 (Lo-16bits)
7777 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7778 |  |  |  | HR7777 (Lo-16bits)
7779 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7780 |  |  |  | HR7779 (Lo-16bits)
7781 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7782 |  |  |  | HR7781 (Lo-16bits)
7783 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7784 |  |  |  | HR7783 (Lo-16bits)
7785 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7786 |  |  |  | HR7785 (Lo-16bits)
7787 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7788 |  |  |  | HR7787 (Lo-16bits)
7789 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7790 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7791 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7792 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7793 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7794 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7795 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7796 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7797 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7798 |  |  |  | HR7797 (Lo-16bits)
7799 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7800 |  |  |  | HR7799 (Lo-16bits)
7801 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7802 |  |  |  | HR7801 (Lo-16bits)
7803 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7804 |  |  |  | HR7803 (Lo-16bits)
7805 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7806 |  |  |  | HR7805 (Lo-16bits)
7807 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7808 |  |  |  | HR7807 (Lo-16bits)
7809 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7810 |  |  |  | HR7809 (Lo-16bits)
7811 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7812 |  |  |  | HR7811 (Lo-16bits)
7813 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7814 |  |  |  | HR7813 (Lo-16bits)
7815 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7816 |  |  |  | HR7815 (Lo-16bits)
7817 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7818 |  |  |  | HR7817 (Lo-16bits)
7819 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7820 |  |  |  | HR7819 (Lo-16bits)
7821 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7822 |  |  |  | HR7821 (Lo-16bits)
7823 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7824 |  |  |  | HR7823 (Lo-16bits)
7825 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7826 |  |  |  | HR7825 (Lo-16bits)
7827 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7828 |  |  |  | HR7827 (Lo-16bits)
7829 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7830 |  |  |  | HR7829 (Lo-16bits)
7831 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7832 |  |  |  | HR7831 (Lo-16bits)
7833 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7834 |  |  |  | HR7833 (Lo-16bits)
7835 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7836 |  |  |  | HR7835 (Lo-16bits)
7837 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7838 |  |  |  | HR7837 (Lo-16bits)
7839 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7840 |  |  |  | HR7839 (Lo-16bits)
7841 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7842 |  |  |  | HR7841 (Lo-16bits)
7843 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7844 |  |  |  | HR7843 (Lo-16bits)
7845 | OV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7846 |  |  |  | HR7845 (Lo-16bits)
7847 | OV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7848 |  |  |  | HR7847 (Lo-16bits)
7849 | OV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7850 |  |  |  | HR7849 (Lo-16bits)
7851 | OV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7852 |  |  |  | HR7851 (Lo-16bits)
7853 | OV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7854 |  |  |  | HR7853 (Lo-16bits)
7855 | OV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7856 |  |  |  | HR7855 (Lo-16bits)
7857 | OV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7858 |  |  |  | HR7857 (Lo-16bits)
7859 | OV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7860 |  |  |  | HR7859 (Lo-16bits)
7861 | OV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7862 | OV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7863 | OV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7864 | OV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7865 | OV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7866 | OV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7867 | OV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7868 | OV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7869 | OV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7870 | OV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7871 | OV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7872 | OV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7873 | OV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7874 | OV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7875 | OV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7876 | OV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7877 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7878 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7879 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7880 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7881 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7882 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7883 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7884 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7885 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7886 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7887 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7888 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7889 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7890 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7891 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7892 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7893 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7894 |  |  |  | HR7893 (Lo-16bits)
7895 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7896 |  |  |  | HR7895 (Lo-16bits)
7897 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7898 |  |  |  | HR7897 (Lo-16bits)
7899 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7900 |  |  |  | HR7899 (Lo-16bits)
7901 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7902 |  |  |  | HR7901 (Lo-16bits)
7903 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7904 |  |  |  | HR7903 (Lo-16bits)
7905 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7906 |  |  |  | HR7905 (Lo-16bits)
7907 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
7908 |  |  |  | HR7907 (Lo-16bits)
7909 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7910 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7911 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7912 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7913 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7914 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7915 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7916 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7917 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7918 |  |  |  | HR7917 (Lo-16bits)
7919 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7920 |  |  |  | HR7919 (Lo-16bits)
7921 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7922 |  |  |  | HR7921 (Lo-16bits)
7923 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7924 |  |  |  | HR7923 (Lo-16bits)
7925 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7926 |  |  |  | HR7925 (Lo-16bits)
7927 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7928 |  |  |  | HR7927 (Lo-16bits)
7929 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7930 |  |  |  | HR7929 (Lo-16bits)
7931 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7932 |  |  |  | HR7931 (Lo-16bits)
7933 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7934 |  |  |  | HR7933 (Lo-16bits)
7935 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7936 |  |  |  | HR7935 (Lo-16bits)
7937 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7938 |  |  |  | HR7937 (Lo-16bits)
7939 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7940 |  |  |  | HR7939 (Lo-16bits)
7941 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7942 |  |  |  | HR7941 (Lo-16bits)
7943 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7944 |  |  |  | HR7943 (Lo-16bits)
7945 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7946 |  |  |  | HR7945 (Lo-16bits)
7947 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7948 |  |  |  | HR7947 (Lo-16bits)
7949 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7950 |  |  |  | HR7949 (Lo-16bits)
7951 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7952 |  |  |  | HR7951 (Lo-16bits)
7953 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7954 |  |  |  | HR7953 (Lo-16bits)
7955 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7956 |  |  |  | HR7955 (Lo-16bits)
7957 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7958 |  |  |  | HR7957 (Lo-16bits)
7959 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7960 |  |  |  | HR7959 (Lo-16bits)
7961 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7962 |  |  |  | HR7961 (Lo-16bits)
7963 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7964 |  |  |  | HR7963 (Lo-16bits)
7965 | OV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7966 |  |  |  | HR7965 (Lo-16bits)
7967 | OV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7968 |  |  |  | HR7967 (Lo-16bits)
7969 | OV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7970 |  |  |  | HR7969 (Lo-16bits)
7971 | OV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7972 |  |  |  | HR7971 (Lo-16bits)
7973 | OV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7974 |  |  |  | HR7973 (Lo-16bits)
7975 | OV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7976 |  |  |  | HR7975 (Lo-16bits)
7977 | OV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7978 |  |  |  | HR7977 (Lo-16bits)
7979 | OV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7980 |  |  |  | HR7979 (Lo-16bits)
7981 | OV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7982 | OV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7983 | OV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7984 | OV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7985 | OV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7986 | OV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7987 | OV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7988 | OV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
7989 | OV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7990 | OV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7991 | OV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7992 | OV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7993 | OV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7994 | OV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7995 | OV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7996 | OV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
7997 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7998 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7999 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8000 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8001 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8002 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8003 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8004 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8005 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8006 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8007 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8008 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8009 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8010 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8011 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8012 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8013 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
8014 |  |  |  | HR8013 (Lo-16bits)
8015 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
8016 |  |  |  | HR8015 (Lo-16bits)
8017 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
8018 |  |  |  | HR8017 (Lo-16bits)
8019 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
8020 |  |  |  | HR8019 (Lo-16bits)
8021 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
8022 |  |  |  | HR8021 (Lo-16bits)
8023 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
8024 |  |  |  | HR8023 (Lo-16bits)
8025 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
8026 |  |  |  | HR8025 (Lo-16bits)
8027 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
8028 |  |  |  | HR8027 (Lo-16bits)
8029 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8030 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8031 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8032 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8033 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8034 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8035 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8036 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8037 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8038 |  |  |  | HR8037 (Lo-16bits)
8039 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8040 |  |  |  | HR8039 (Lo-16bits)
8041 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8042 |  |  |  | HR8041 (Lo-16bits)
8043 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8044 |  |  |  | HR8043 (Lo-16bits)
8045 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8046 |  |  |  | HR8045 (Lo-16bits)
8047 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8048 |  |  |  | HR8047 (Lo-16bits)
8049 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8050 |  |  |  | HR8049 (Lo-16bits)
8051 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8052 |  |  |  | HR8051 (Lo-16bits)
8053 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8054 |  |  |  | HR8053 (Lo-16bits)
8055 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8056 |  |  |  | HR8055 (Lo-16bits)
8057 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8058 |  |  |  | HR8057 (Lo-16bits)
8059 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8060 |  |  |  | HR8059 (Lo-16bits)
8061 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8062 |  |  |  | HR8061 (Lo-16bits)
8063 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8064 |  |  |  | HR8063 (Lo-16bits)
8065 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8066 |  |  |  | HR8065 (Lo-16bits)
8067 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8068 |  |  |  | HR8067 (Lo-16bits)
8069 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8070 |  |  |  | HR8069 (Lo-16bits)
8071 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8072 |  |  |  | HR8071 (Lo-16bits)
8073 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8074 |  |  |  | HR8073 (Lo-16bits)
8075 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8076 |  |  |  | HR8075 (Lo-16bits)
8077 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8078 |  |  |  | HR8077 (Lo-16bits)
8079 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8080 |  |  |  | HR8079 (Lo-16bits)
8081 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8082 |  |  |  | HR8081 (Lo-16bits)
8083 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8084 |  |  |  | HR8083 (Lo-16bits)
8085 | OV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8086 |  |  |  | HR8085 (Lo-16bits)
8087 | OV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8088 |  |  |  | HR8087 (Lo-16bits)
8089 | OV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8090 |  |  |  | HR8089 (Lo-16bits)
8091 | OV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8092 |  |  |  | HR8091 (Lo-16bits)
8093 | OV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8094 |  |  |  | HR8093 (Lo-16bits)
8095 | OV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8096 |  |  |  | HR8095 (Lo-16bits)
8097 | OV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8098 |  |  |  | HR8097 (Lo-16bits)
8099 | OV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8100 |  |  |  | HR8099 (Lo-16bits)
8101 | OV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8102 | OV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8103 | OV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8104 | OV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8105 | OV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8106 | OV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8107 | OV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8108 | OV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8109 | OV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8110 | OV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8111 | OV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8112 | OV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8113 | OV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8114 | OV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8115 | OV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8116 | OV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8117 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8118 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8119 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8120 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8121 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8122 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8123 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8124 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8125 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8126 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8127 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8128 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8129 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8130 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8131 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8132 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8133 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8134 |  |  |  | HR8133 (Lo-16bits)
8135 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8136 |  |  |  | HR8135 (Lo-16bits)
8137 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8138 |  |  |  | HR8137 (Lo-16bits)
8139 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8140 |  |  |  | HR8139 (Lo-16bits)
8141 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8142 |  |  |  | HR8141 (Lo-16bits)
8143 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8144 |  |  |  | HR8143 (Lo-16bits)
8145 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8146 |  |  |  | HR8145 (Lo-16bits)
8147 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8148 |  |  |  | HR8147 (Lo-16bits)
8149 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8150 |  |  |  | HR8149 (Lo-16bits)
8151 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8152 |  |  |  | HR8151 (Lo-16bits)
8153 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8154 |  |  |  | HR8153 (Lo-16bits)
8155 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8156 |  |  |  | HR8155 (Lo-16bits)
8157 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8158 |  |  |  | HR8157 (Lo-16bits)
8159 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8160 |  |  |  | HR8159 (Lo-16bits)
8161 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8162 |  |  |  | HR8161 (Lo-16bits)
8163 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8164 |  |  |  | HR8163 (Lo-16bits)
8165 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8166 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8167 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8168 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8169 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8170 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8171 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8172 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8173 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8174 |  |  |  | HR8173 (Lo-16bits)
8175 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8176 |  |  |  | HR8175 (Lo-16bits)
8177 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8178 |  |  |  | HR8177 (Lo-16bits)
8179 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8180 |  |  |  | HR8179 (Lo-16bits)
8181 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8182 |  |  |  | HR8181 (Lo-16bits)
8183 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8184 |  |  |  | HR8183 (Lo-16bits)
8185 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8186 |  |  |  | HR8185 (Lo-16bits)
8187 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8188 |  |  |  | HR8187 (Lo-16bits)
8189 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8190 |  |  |  | HR8189 (Lo-16bits)
8191 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8192 |  |  |  | HR8191 (Lo-16bits)
8193 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8194 |  |  |  | HR8193 (Lo-16bits)
8195 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8196 |  |  |  | HR8195 (Lo-16bits)
8197 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8198 |  |  |  | HR8197 (Lo-16bits)
8199 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8200 |  |  |  | HR8199 (Lo-16bits)
8201 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8202 |  |  |  | HR8201 (Lo-16bits)
8203 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8204 |  |  |  | HR8203 (Lo-16bits)
8205 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8206 |  |  |  | HR8205 (Lo-16bits)
8207 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8208 |  |  |  | HR8207 (Lo-16bits)
8209 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8210 |  |  |  | HR8209 (Lo-16bits)
8211 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8212 |  |  |  | HR8211 (Lo-16bits)
8213 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8214 |  |  |  | HR8213 (Lo-16bits)
8215 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8216 |  |  |  | HR8215 (Lo-16bits)
8217 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8218 |  |  |  | HR8217 (Lo-16bits)
8219 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8220 |  |  |  | HR8219 (Lo-16bits)
8221 | UV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8222 |  |  |  | HR8221 (Lo-16bits)
8223 | UV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8224 |  |  |  | HR8223 (Lo-16bits)
8225 | UV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8226 |  |  |  | HR8225 (Lo-16bits)
8227 | UV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8228 |  |  |  | HR8227 (Lo-16bits)
8229 | UV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8230 |  |  |  | HR8229 (Lo-16bits)
8231 | UV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8232 |  |  |  | HR8231 (Lo-16bits)
8233 | UV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8234 |  |  |  | HR8233 (Lo-16bits)
8235 | UV1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8236 |  |  |  | HR8235 (Lo-16bits)
8237 | UV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8238 | UV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8239 | UV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8240 | UV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8241 | UV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8242 | UV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8243 | UV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8244 | UV1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8245 | UV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8246 | UV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8247 | UV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8248 | UV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8249 | UV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8250 | UV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8251 | UV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8252 | UV1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8253 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8254 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8255 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8256 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8257 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8258 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8259 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8260 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8261 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8262 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8263 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8264 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8265 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8266 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8267 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8268 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8269 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8270 |  |  |  | HR8269 (Lo-16bits)
8271 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8272 |  |  |  | HR8271 (Lo-16bits)
8273 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8274 |  |  |  | HR8273 (Lo-16bits)
8275 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8276 |  |  |  | HR8275 (Lo-16bits)
8277 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8278 |  |  |  | HR8277 (Lo-16bits)
8279 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8280 |  |  |  | HR8279 (Lo-16bits)
8281 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8282 |  |  |  | HR8281 (Lo-16bits)
8283 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8284 |  |  |  | HR8283 (Lo-16bits)
8285 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8286 |  |  |  | HR8285 (Lo-16bits)
8287 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8288 |  |  |  | HR8287 (Lo-16bits)
8289 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8290 |  |  |  | HR8289 (Lo-16bits)
8291 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8292 |  |  |  | HR8291 (Lo-16bits)
8293 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8294 |  |  |  | HR8293 (Lo-16bits)
8295 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8296 |  |  |  | HR8295 (Lo-16bits)
8297 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8298 |  |  |  | HR8297 (Lo-16bits)
8299 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8300 |  |  |  | HR8299 (Lo-16bits)
8301 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8302 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8303 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8304 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8305 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8306 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8307 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8308 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8309 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8310 |  |  |  | HR8309 (Lo-16bits)
8311 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8312 |  |  |  | HR8311 (Lo-16bits)
8313 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8314 |  |  |  | HR8313 (Lo-16bits)
8315 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8316 |  |  |  | HR8315 (Lo-16bits)
8317 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8318 |  |  |  | HR8317 (Lo-16bits)
8319 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8320 |  |  |  | HR8319 (Lo-16bits)
8321 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8322 |  |  |  | HR8321 (Lo-16bits)
8323 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8324 |  |  |  | HR8323 (Lo-16bits)
8325 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8326 |  |  |  | HR8325 (Lo-16bits)
8327 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8328 |  |  |  | HR8327 (Lo-16bits)
8329 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8330 |  |  |  | HR8329 (Lo-16bits)
8331 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8332 |  |  |  | HR8331 (Lo-16bits)
8333 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8334 |  |  |  | HR8333 (Lo-16bits)
8335 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8336 |  |  |  | HR8335 (Lo-16bits)
8337 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8338 |  |  |  | HR8337 (Lo-16bits)
8339 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8340 |  |  |  | HR8339 (Lo-16bits)
8341 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8342 |  |  |  | HR8341 (Lo-16bits)
8343 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8344 |  |  |  | HR8343 (Lo-16bits)
8345 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8346 |  |  |  | HR8345 (Lo-16bits)
8347 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8348 |  |  |  | HR8347 (Lo-16bits)
8349 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8350 |  |  |  | HR8349 (Lo-16bits)
8351 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8352 |  |  |  | HR8351 (Lo-16bits)
8353 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8354 |  |  |  | HR8353 (Lo-16bits)
8355 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8356 |  |  |  | HR8355 (Lo-16bits)
8357 | UV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8358 |  |  |  | HR8357 (Lo-16bits)
8359 | UV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8360 |  |  |  | HR8359 (Lo-16bits)
8361 | UV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8362 |  |  |  | HR8361 (Lo-16bits)
8363 | UV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8364 |  |  |  | HR8363 (Lo-16bits)
8365 | UV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8366 |  |  |  | HR8365 (Lo-16bits)
8367 | UV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8368 |  |  |  | HR8367 (Lo-16bits)
8369 | UV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8370 |  |  |  | HR8369 (Lo-16bits)
8371 | UV2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8372 |  |  |  | HR8371 (Lo-16bits)
8373 | UV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8374 | UV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8375 | UV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8376 | UV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8377 | UV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8378 | UV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8379 | UV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8380 | UV2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8381 | UV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8382 | UV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8383 | UV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8384 | UV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8385 | UV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8386 | UV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8387 | UV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8388 | UV2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8389 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8390 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8391 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8392 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8393 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8394 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8395 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8396 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8397 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8398 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8399 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8400 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8401 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8402 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8403 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8404 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8405 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8406 |  |  |  | HR8405 (Lo-16bits)
8407 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8408 |  |  |  | HR8407 (Lo-16bits)
8409 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8410 |  |  |  | HR8409 (Lo-16bits)
8411 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8412 |  |  |  | HR8411 (Lo-16bits)
8413 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8414 |  |  |  | HR8413 (Lo-16bits)
8415 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8416 |  |  |  | HR8415 (Lo-16bits)
8417 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8418 |  |  |  | HR8417 (Lo-16bits)
8419 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8420 |  |  |  | HR8419 (Lo-16bits)
8421 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8422 |  |  |  | HR8421 (Lo-16bits)
8423 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8424 |  |  |  | HR8423 (Lo-16bits)
8425 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8426 |  |  |  | HR8425 (Lo-16bits)
8427 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8428 |  |  |  | HR8427 (Lo-16bits)
8429 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8430 |  |  |  | HR8429 (Lo-16bits)
8431 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8432 |  |  |  | HR8431 (Lo-16bits)
8433 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8434 |  |  |  | HR8433 (Lo-16bits)
8435 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8436 |  |  |  | HR8435 (Lo-16bits)
8437 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8438 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8439 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8440 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8441 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8442 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8443 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8444 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8445 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8446 |  |  |  | HR8445 (Lo-16bits)
8447 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8448 |  |  |  | HR8447 (Lo-16bits)
8449 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8450 |  |  |  | HR8449 (Lo-16bits)
8451 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8452 |  |  |  | HR8451 (Lo-16bits)
8453 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8454 |  |  |  | HR8453 (Lo-16bits)
8455 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8456 |  |  |  | HR8455 (Lo-16bits)
8457 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8458 |  |  |  | HR8457 (Lo-16bits)
8459 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8460 |  |  |  | HR8459 (Lo-16bits)
8461 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8462 |  |  |  | HR8461 (Lo-16bits)
8463 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8464 |  |  |  | HR8463 (Lo-16bits)
8465 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8466 |  |  |  | HR8465 (Lo-16bits)
8467 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8468 |  |  |  | HR8467 (Lo-16bits)
8469 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8470 |  |  |  | HR8469 (Lo-16bits)
8471 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8472 |  |  |  | HR8471 (Lo-16bits)
8473 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8474 |  |  |  | HR8473 (Lo-16bits)
8475 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8476 |  |  |  | HR8475 (Lo-16bits)
8477 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8478 |  |  |  | HR8477 (Lo-16bits)
8479 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8480 |  |  |  | HR8479 (Lo-16bits)
8481 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8482 |  |  |  | HR8481 (Lo-16bits)
8483 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8484 |  |  |  | HR8483 (Lo-16bits)
8485 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8486 |  |  |  | HR8485 (Lo-16bits)
8487 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8488 |  |  |  | HR8487 (Lo-16bits)
8489 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8490 |  |  |  | HR8489 (Lo-16bits)
8491 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8492 |  |  |  | HR8491 (Lo-16bits)
8493 | UV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8494 |  |  |  | HR8493 (Lo-16bits)
8495 | UV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8496 |  |  |  | HR8495 (Lo-16bits)
8497 | UV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8498 |  |  |  | HR8497 (Lo-16bits)
8499 | UV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8500 |  |  |  | HR8499 (Lo-16bits)
8501 | UV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8502 |  |  |  | HR8501 (Lo-16bits)
8503 | UV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8504 |  |  |  | HR8503 (Lo-16bits)
8505 | UV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8506 |  |  |  | HR8505 (Lo-16bits)
8507 | UV3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8508 |  |  |  | HR8507 (Lo-16bits)
8509 | UV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8510 | UV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8511 | UV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8512 | UV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8513 | UV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8514 | UV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8515 | UV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8516 | UV3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8517 | UV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8518 | UV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8519 | UV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8520 | UV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8521 | UV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8522 | UV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8523 | UV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8524 | UV3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8525 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8526 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8527 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8528 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8529 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8530 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8531 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8532 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8533 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8534 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8535 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8536 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8537 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8538 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8539 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8540 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8541 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8542 |  |  |  | HR8541 (Lo-16bits)
8543 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8544 |  |  |  | HR8543 (Lo-16bits)
8545 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8546 |  |  |  | HR8545 (Lo-16bits)
8547 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8548 |  |  |  | HR8547 (Lo-16bits)
8549 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8550 |  |  |  | HR8549 (Lo-16bits)
8551 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8552 |  |  |  | HR8551 (Lo-16bits)
8553 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8554 |  |  |  | HR8553 (Lo-16bits)
8555 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8556 |  |  |  | HR8555 (Lo-16bits)
8557 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8558 |  |  |  | HR8557 (Lo-16bits)
8559 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8560 |  |  |  | HR8559 (Lo-16bits)
8561 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8562 |  |  |  | HR8561 (Lo-16bits)
8563 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8564 |  |  |  | HR8563 (Lo-16bits)
8565 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8566 |  |  |  | HR8565 (Lo-16bits)
8567 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8568 |  |  |  | HR8567 (Lo-16bits)
8569 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8570 |  |  |  | HR8569 (Lo-16bits)
8571 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8572 |  |  |  | HR8571 (Lo-16bits)
8573 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8574 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8575 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8576 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8577 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8578 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8579 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8580 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8581 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8582 |  |  |  | HR8581 (Lo-16bits)
8583 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8584 |  |  |  | HR8583 (Lo-16bits)
8585 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8586 |  |  |  | HR8585 (Lo-16bits)
8587 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8588 |  |  |  | HR8587 (Lo-16bits)
8589 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8590 |  |  |  | HR8589 (Lo-16bits)
8591 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8592 |  |  |  | HR8591 (Lo-16bits)
8593 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8594 |  |  |  | HR8593 (Lo-16bits)
8595 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8596 |  |  |  | HR8595 (Lo-16bits)
8597 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8598 |  |  |  | HR8597 (Lo-16bits)
8599 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8600 |  |  |  | HR8599 (Lo-16bits)
8601 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8602 |  |  |  | HR8601 (Lo-16bits)
8603 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8604 |  |  |  | HR8603 (Lo-16bits)
8605 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8606 |  |  |  | HR8605 (Lo-16bits)
8607 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8608 |  |  |  | HR8607 (Lo-16bits)
8609 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8610 |  |  |  | HR8609 (Lo-16bits)
8611 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8612 |  |  |  | HR8611 (Lo-16bits)
8613 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8614 |  |  |  | HR8613 (Lo-16bits)
8615 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8616 |  |  |  | HR8615 (Lo-16bits)
8617 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8618 |  |  |  | HR8617 (Lo-16bits)
8619 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8620 |  |  |  | HR8619 (Lo-16bits)
8621 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8622 |  |  |  | HR8621 (Lo-16bits)
8623 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8624 |  |  |  | HR8623 (Lo-16bits)
8625 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8626 |  |  |  | HR8625 (Lo-16bits)
8627 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8628 |  |  |  | HR8627 (Lo-16bits)
8629 | UV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8630 |  |  |  | HR8629 (Lo-16bits)
8631 | UV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8632 |  |  |  | HR8631 (Lo-16bits)
8633 | UV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8634 |  |  |  | HR8633 (Lo-16bits)
8635 | UV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8636 |  |  |  | HR8635 (Lo-16bits)
8637 | UV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8638 |  |  |  | HR8637 (Lo-16bits)
8639 | UV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8640 |  |  |  | HR8639 (Lo-16bits)
8641 | UV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8642 |  |  |  | HR8641 (Lo-16bits)
8643 | UV4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8644 |  |  |  | HR8643 (Lo-16bits)
8645 | UV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8646 | UV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8647 | UV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8648 | UV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8649 | UV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8650 | UV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8651 | UV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8652 | UV4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8653 | UV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8654 | UV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8655 | UV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8656 | UV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8657 | UV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8658 | UV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8659 | UV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8660 | UV4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8661 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8662 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8663 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8664 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8665 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8666 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8667 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8668 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8669 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8670 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8671 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8672 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8673 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8674 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8675 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8676 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8677 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8678 |  |  |  | HR8677 (Lo-16bits)
8679 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8680 |  |  |  | HR8679 (Lo-16bits)
8681 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8682 |  |  |  | HR8681 (Lo-16bits)
8683 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8684 |  |  |  | HR8683 (Lo-16bits)
8685 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8686 |  |  |  | HR8685 (Lo-16bits)
8687 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8688 |  |  |  | HR8687 (Lo-16bits)
8689 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8690 |  |  |  | HR8689 (Lo-16bits)
8691 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8692 |  |  |  | HR8691 (Lo-16bits)
8693 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8694 |  |  |  | HR8693 (Lo-16bits)
8695 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8696 |  |  |  | HR8695 (Lo-16bits)
8697 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8698 |  |  |  | HR8697 (Lo-16bits)
8699 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8700 |  |  |  | HR8699 (Lo-16bits)
8701 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8702 |  |  |  | HR8701 (Lo-16bits)
8703 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8704 |  |  |  | HR8703 (Lo-16bits)
8705 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8706 |  |  |  | HR8705 (Lo-16bits)
8707 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8708 |  |  |  | HR8707 (Lo-16bits)
8709 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8710 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8711 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8712 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8713 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8714 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8715 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8716 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8717 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8718 |  |  |  | HR8717 (Lo-16bits)
8719 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8720 |  |  |  | HR8719 (Lo-16bits)
8721 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8722 |  |  |  | HR8721 (Lo-16bits)
8723 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8724 |  |  |  | HR8723 (Lo-16bits)
8725 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8726 |  |  |  | HR8725 (Lo-16bits)
8727 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8728 |  |  |  | HR8727 (Lo-16bits)
8729 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8730 |  |  |  | HR8729 (Lo-16bits)
8731 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8732 |  |  |  | HR8731 (Lo-16bits)
8733 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8734 |  |  |  | HR8733 (Lo-16bits)
8735 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8736 |  |  |  | HR8735 (Lo-16bits)
8737 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8738 |  |  |  | HR8737 (Lo-16bits)
8739 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8740 |  |  |  | HR8739 (Lo-16bits)
8741 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8742 |  |  |  | HR8741 (Lo-16bits)
8743 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8744 |  |  |  | HR8743 (Lo-16bits)
8745 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8746 |  |  |  | HR8745 (Lo-16bits)
8747 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8748 |  |  |  | HR8747 (Lo-16bits)
8749 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8750 |  |  |  | HR8749 (Lo-16bits)
8751 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8752 |  |  |  | HR8751 (Lo-16bits)
8753 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8754 |  |  |  | HR8753 (Lo-16bits)
8755 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8756 |  |  |  | HR8755 (Lo-16bits)
8757 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8758 |  |  |  | HR8757 (Lo-16bits)
8759 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8760 |  |  |  | HR8759 (Lo-16bits)
8761 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8762 |  |  |  | HR8761 (Lo-16bits)
8763 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8764 |  |  |  | HR8763 (Lo-16bits)
8765 | VUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8766 |  |  |  | HR8765 (Lo-16bits)
8767 | VUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8768 |  |  |  | HR8767 (Lo-16bits)
8769 | VUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8770 |  |  |  | HR8769 (Lo-16bits)
8771 | VUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8772 |  |  |  | HR8771 (Lo-16bits)
8773 | VUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8774 |  |  |  | HR8773 (Lo-16bits)
8775 | VUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8776 |  |  |  | HR8775 (Lo-16bits)
8777 | VUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8778 |  |  |  | HR8777 (Lo-16bits)
8779 | VUB1:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8780 |  |  |  | HR8779 (Lo-16bits)
8781 | VUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8782 | VUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8783 | VUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8784 | VUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8785 | VUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8786 | VUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8787 | VUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8788 | VUB1:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8789 | VUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8790 | VUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8791 | VUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8792 | VUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8793 | VUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8794 | VUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8795 | VUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8796 | VUB1:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8797 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8798 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8799 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8800 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8801 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8802 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8803 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8804 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8805 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8806 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8807 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8808 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8809 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8810 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8811 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8812 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8813 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8814 |  |  |  | HR8813 (Lo-16bits)
8815 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8816 |  |  |  | HR8815 (Lo-16bits)
8817 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8818 |  |  |  | HR8817 (Lo-16bits)
8819 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8820 |  |  |  | HR8819 (Lo-16bits)
8821 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8822 |  |  |  | HR8821 (Lo-16bits)
8823 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8824 |  |  |  | HR8823 (Lo-16bits)
8825 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8826 |  |  |  | HR8825 (Lo-16bits)
8827 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8828 |  |  |  | HR8827 (Lo-16bits)
8829 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8830 |  |  |  | HR8829 (Lo-16bits)
8831 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8832 |  |  |  | HR8831 (Lo-16bits)
8833 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8834 |  |  |  | HR8833 (Lo-16bits)
8835 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8836 |  |  |  | HR8835 (Lo-16bits)
8837 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8838 |  |  |  | HR8837 (Lo-16bits)
8839 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8840 |  |  |  | HR8839 (Lo-16bits)
8841 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8842 |  |  |  | HR8841 (Lo-16bits)
8843 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8844 |  |  |  | HR8843 (Lo-16bits)
8845 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8846 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8847 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8848 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8849 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8850 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8851 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8852 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8853 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8854 |  |  |  | HR8853 (Lo-16bits)
8855 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8856 |  |  |  | HR8855 (Lo-16bits)
8857 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8858 |  |  |  | HR8857 (Lo-16bits)
8859 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8860 |  |  |  | HR8859 (Lo-16bits)
8861 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8862 |  |  |  | HR8861 (Lo-16bits)
8863 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8864 |  |  |  | HR8863 (Lo-16bits)
8865 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8866 |  |  |  | HR8865 (Lo-16bits)
8867 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8868 |  |  |  | HR8867 (Lo-16bits)
8869 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8870 |  |  |  | HR8869 (Lo-16bits)
8871 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8872 |  |  |  | HR8871 (Lo-16bits)
8873 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8874 |  |  |  | HR8873 (Lo-16bits)
8875 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8876 |  |  |  | HR8875 (Lo-16bits)
8877 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8878 |  |  |  | HR8877 (Lo-16bits)
8879 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8880 |  |  |  | HR8879 (Lo-16bits)
8881 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8882 |  |  |  | HR8881 (Lo-16bits)
8883 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8884 |  |  |  | HR8883 (Lo-16bits)
8885 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8886 |  |  |  | HR8885 (Lo-16bits)
8887 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8888 |  |  |  | HR8887 (Lo-16bits)
8889 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8890 |  |  |  | HR8889 (Lo-16bits)
8891 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8892 |  |  |  | HR8891 (Lo-16bits)
8893 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8894 |  |  |  | HR8893 (Lo-16bits)
8895 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8896 |  |  |  | HR8895 (Lo-16bits)
8897 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8898 |  |  |  | HR8897 (Lo-16bits)
8899 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8900 |  |  |  | HR8899 (Lo-16bits)
8901 | VUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8902 |  |  |  | HR8901 (Lo-16bits)
8903 | VUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8904 |  |  |  | HR8903 (Lo-16bits)
8905 | VUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8906 |  |  |  | HR8905 (Lo-16bits)
8907 | VUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8908 |  |  |  | HR8907 (Lo-16bits)
8909 | VUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8910 |  |  |  | HR8909 (Lo-16bits)
8911 | VUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8912 |  |  |  | HR8911 (Lo-16bits)
8913 | VUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8914 |  |  |  | HR8913 (Lo-16bits)
8915 | VUB2:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8916 |  |  |  | HR8915 (Lo-16bits)
8917 | VUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8918 | VUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8919 | VUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8920 | VUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8921 | VUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8922 | VUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8923 | VUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8924 | VUB2:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
8925 | VUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8926 | VUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8927 | VUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8928 | VUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8929 | VUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8930 | VUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8931 | VUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8932 | VUB2:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
8933 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8934 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8935 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8936 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8937 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8938 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8939 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8940 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8941 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8942 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8943 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8944 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8945 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8946 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8947 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8948 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8949 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8950 |  |  |  | HR8949 (Lo-16bits)
8951 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8952 |  |  |  | HR8951 (Lo-16bits)
8953 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8954 |  |  |  | HR8953 (Lo-16bits)
8955 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8956 |  |  |  | HR8955 (Lo-16bits)
8957 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8958 |  |  |  | HR8957 (Lo-16bits)
8959 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8960 |  |  |  | HR8959 (Lo-16bits)
8961 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8962 |  |  |  | HR8961 (Lo-16bits)
8963 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8964 |  |  |  | HR8963 (Lo-16bits)
8965 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8966 |  |  |  | HR8965 (Lo-16bits)
8967 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8968 |  |  |  | HR8967 (Lo-16bits)
8969 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8970 |  |  |  | HR8969 (Lo-16bits)
8971 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8972 |  |  |  | HR8971 (Lo-16bits)
8973 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8974 |  |  |  | HR8973 (Lo-16bits)
8975 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8976 |  |  |  | HR8975 (Lo-16bits)
8977 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8978 |  |  |  | HR8977 (Lo-16bits)
8979 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8980 |  |  |  | HR8979 (Lo-16bits)
8981 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8982 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8983 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8984 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8985 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8986 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8987 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8988 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8989 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8990 |  |  |  | HR8989 (Lo-16bits)
8991 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8992 |  |  |  | HR8991 (Lo-16bits)
8993 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8994 |  |  |  | HR8993 (Lo-16bits)
8995 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8996 |  |  |  | HR8995 (Lo-16bits)
8997 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8998 |  |  |  | HR8997 (Lo-16bits)
8999 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9000 |  |  |  | HR8999 (Lo-16bits)
9001 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9002 |  |  |  | HR9001 (Lo-16bits)
9003 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9004 |  |  |  | HR9003 (Lo-16bits)
9005 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9006 |  |  |  | HR9005 (Lo-16bits)
9007 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9008 |  |  |  | HR9007 (Lo-16bits)
9009 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9010 |  |  |  | HR9009 (Lo-16bits)
9011 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9012 |  |  |  | HR9011 (Lo-16bits)
9013 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9014 |  |  |  | HR9013 (Lo-16bits)
9015 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9016 |  |  |  | HR9015 (Lo-16bits)
9017 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9018 |  |  |  | HR9017 (Lo-16bits)
9019 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9020 |  |  |  | HR9019 (Lo-16bits)
9021 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9022 |  |  |  | HR9021 (Lo-16bits)
9023 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9024 |  |  |  | HR9023 (Lo-16bits)
9025 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9026 |  |  |  | HR9025 (Lo-16bits)
9027 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9028 |  |  |  | HR9027 (Lo-16bits)
9029 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9030 |  |  |  | HR9029 (Lo-16bits)
9031 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9032 |  |  |  | HR9031 (Lo-16bits)
9033 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9034 |  |  |  | HR9033 (Lo-16bits)
9035 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9036 |  |  |  | HR9035 (Lo-16bits)
9037 | VUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9038 |  |  |  | HR9037 (Lo-16bits)
9039 | VUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9040 |  |  |  | HR9039 (Lo-16bits)
9041 | VUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9042 |  |  |  | HR9041 (Lo-16bits)
9043 | VUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9044 |  |  |  | HR9043 (Lo-16bits)
9045 | VUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9046 |  |  |  | HR9045 (Lo-16bits)
9047 | VUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9048 |  |  |  | HR9047 (Lo-16bits)
9049 | VUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9050 |  |  |  | HR9049 (Lo-16bits)
9051 | VUB3:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9052 |  |  |  | HR9051 (Lo-16bits)
9053 | VUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9054 | VUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9055 | VUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9056 | VUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9057 | VUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9058 | VUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9059 | VUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9060 | VUB3:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9061 | VUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9062 | VUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9063 | VUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9064 | VUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9065 | VUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9066 | VUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9067 | VUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9068 | VUB3:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9069 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9070 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9071 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9072 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9073 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9074 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9075 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9076 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9077 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
9078 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
9079 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
9080 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
9081 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
9082 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
9083 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
9084 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
9085 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
9086 |  |  |  | HR9085 (Lo-16bits)
9087 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
9088 |  |  |  | HR9087 (Lo-16bits)
9089 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
9090 |  |  |  | HR9089 (Lo-16bits)
9091 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
9092 |  |  |  | HR9091 (Lo-16bits)
9093 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
9094 |  |  |  | HR9093 (Lo-16bits)
9095 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
9096 |  |  |  | HR9095 (Lo-16bits)
9097 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
9098 |  |  |  | HR9097 (Lo-16bits)
9099 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
9100 |  |  |  | HR9099 (Lo-16bits)
9101 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
9102 |  |  |  | HR9101 (Lo-16bits)
9103 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
9104 |  |  |  | HR9103 (Lo-16bits)
9105 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
9106 |  |  |  | HR9105 (Lo-16bits)
9107 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
9108 |  |  |  | HR9107 (Lo-16bits)
9109 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
9110 |  |  |  | HR9109 (Lo-16bits)
9111 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
9112 |  |  |  | HR9111 (Lo-16bits)
9113 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
9114 |  |  |  | HR9113 (Lo-16bits)
9115 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
9116 |  |  |  | HR9115 (Lo-16bits)
9117 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
9118 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
9119 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
9120 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
9121 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
9122 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
9123 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
9124 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
9125 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9126 |  |  |  | HR9125 (Lo-16bits)
9127 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9128 |  |  |  | HR9127 (Lo-16bits)
9129 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9130 |  |  |  | HR9129 (Lo-16bits)
9131 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9132 |  |  |  | HR9131 (Lo-16bits)
9133 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9134 |  |  |  | HR9133 (Lo-16bits)
9135 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9136 |  |  |  | HR9135 (Lo-16bits)
9137 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9138 |  |  |  | HR9137 (Lo-16bits)
9139 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9140 |  |  |  | HR9139 (Lo-16bits)
9141 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9142 |  |  |  | HR9141 (Lo-16bits)
9143 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9144 |  |  |  | HR9143 (Lo-16bits)
9145 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9146 |  |  |  | HR9145 (Lo-16bits)
9147 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9148 |  |  |  | HR9147 (Lo-16bits)
9149 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9150 |  |  |  | HR9149 (Lo-16bits)
9151 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9152 |  |  |  | HR9151 (Lo-16bits)
9153 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9154 |  |  |  | HR9153 (Lo-16bits)
9155 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
9156 |  |  |  | HR9155 (Lo-16bits)
9157 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9158 |  |  |  | HR9157 (Lo-16bits)
9159 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9160 |  |  |  | HR9159 (Lo-16bits)
9161 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9162 |  |  |  | HR9161 (Lo-16bits)
9163 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9164 |  |  |  | HR9163 (Lo-16bits)
9165 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9166 |  |  |  | HR9165 (Lo-16bits)
9167 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9168 |  |  |  | HR9167 (Lo-16bits)
9169 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9170 |  |  |  | HR9169 (Lo-16bits)
9171 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
9172 |  |  |  | HR9171 (Lo-16bits)
9173 | VUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9174 |  |  |  | HR9173 (Lo-16bits)
9175 | VUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9176 |  |  |  | HR9175 (Lo-16bits)
9177 | VUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9178 |  |  |  | HR9177 (Lo-16bits)
9179 | VUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9180 |  |  |  | HR9179 (Lo-16bits)
9181 | VUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9182 |  |  |  | HR9181 (Lo-16bits)
9183 | VUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9184 |  |  |  | HR9183 (Lo-16bits)
9185 | VUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9186 |  |  |  | HR9185 (Lo-16bits)
9187 | VUB4:Release time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
9188 |  |  |  | HR9187 (Lo-16bits)
9189 | VUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9190 | VUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9191 | VUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9192 | VUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9193 | VUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9194 | VUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9195 | VUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9196 | VUB4:Delayed pick-up release | R(W) | 1 | 0=No;1=Yes
9197 | VUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9198 | VUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9199 | VUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9200 | VUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9201 | VUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9202 | VUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9203 | VUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9204 | VUB4:Op.Time calculation reset after release time | R(W) | 1 | 0=No;1=Yes
9205 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9206 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9207 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9208 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9209 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9210 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9211 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9212 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
9213 | FRQV1:f> Enable | R(W) | 1 | 0=No;1=Yes
9214 | FRQV1:f>> Enable | R(W) | 1 | 0=No;1=Yes
9215 | FRQV1:f>>> Enable | R(W) | 1 | 0=No;1=Yes
9216 | FRQV1:f>>>> Enable | R(W) | 1 | 0=No;1=Yes
9217 | FRQV1:f< Enable | R(W) | 1 | 0=No;1=Yes
9218 | FRQV1:f<< Enable | R(W) | 1 | 0=No;1=Yes
9219 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
9220 | FRQV1:f<<<< Enable | R(W) | 1 | 0=No;1=Yes
9221 | FRQV1:f> used in setting group | R(W) | 1 | 0=No;1=Yes
9222 | FRQV1:f> used in setting group | R(W) | 1 | 0=No;1=Yes
9223 | FRQV1:f> used in setting group | R(W) | 1 | 0=No;1=Yes
9224 | FRQV1:f> used in setting group | R(W) | 1 | 0=No;1=Yes
9225 | FRQV1:f> used in setting group | R(W) | 1 | 0=No;1=Yes
9226 | FRQV1:f> used in setting group | R(W) | 1 | 0=No;1=Yes
9227 | FRQV1:f> used in setting group | R(W) | 1 | 0=No;1=Yes
9228 | FRQV1:f> used in setting group | R(W) | 1 | 0=No;1=Yes
9229 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9230 |  |  |  | HR9229 (Lo-16bits)
9231 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9232 |  |  |  | HR9231 (Lo-16bits)
9233 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9234 |  |  |  | HR9233 (Lo-16bits)
9235 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9236 |  |  |  | HR9235 (Lo-16bits)
9237 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9238 |  |  |  | HR9237 (Lo-16bits)
9239 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9240 |  |  |  | HR9239 (Lo-16bits)
9241 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9242 |  |  |  | HR9241 (Lo-16bits)
9243 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9244 |  |  |  | HR9243 (Lo-16bits)
9245 | FRQV1:f> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9246 |  |  |  | HR9245 (Lo-16bits)
9247 | FRQV1:f> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9248 |  |  |  | HR9247 (Lo-16bits)
9249 | FRQV1:f> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9250 |  |  |  | HR9249 (Lo-16bits)
9251 | FRQV1:f> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9252 |  |  |  | HR9251 (Lo-16bits)
9253 | FRQV1:f> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9254 |  |  |  | HR9253 (Lo-16bits)
9255 | FRQV1:f> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9256 |  |  |  | HR9255 (Lo-16bits)
9257 | FRQV1:f> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9258 |  |  |  | HR9257 (Lo-16bits)
9259 | FRQV1:f> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9260 |  |  |  | HR9259 (Lo-16bits)
9261 | FRQV1:f>> used in setting group | R(W) | 1 | 0=No;1=Yes
9262 | FRQV1:f>> used in setting group | R(W) | 1 | 0=No;1=Yes
9263 | FRQV1:f>> used in setting group | R(W) | 1 | 0=No;1=Yes
9264 | FRQV1:f>> used in setting group | R(W) | 1 | 0=No;1=Yes
9265 | FRQV1:f>> used in setting group | R(W) | 1 | 0=No;1=Yes
9266 | FRQV1:f>> used in setting group | R(W) | 1 | 0=No;1=Yes
9267 | FRQV1:f>> used in setting group | R(W) | 1 | 0=No;1=Yes
9268 | FRQV1:f>> used in setting group | R(W) | 1 | 0=No;1=Yes
9269 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9270 |  |  |  | HR9269 (Lo-16bits)
9271 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9272 |  |  |  | HR9271 (Lo-16bits)
9273 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9274 |  |  |  | HR9273 (Lo-16bits)
9275 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9276 |  |  |  | HR9275 (Lo-16bits)
9277 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9278 |  |  |  | HR9277 (Lo-16bits)
9279 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9280 |  |  |  | HR9279 (Lo-16bits)
9281 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9282 |  |  |  | HR9281 (Lo-16bits)
9283 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9284 |  |  |  | HR9283 (Lo-16bits)
9285 | FRQV1:f>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9286 |  |  |  | HR9285 (Lo-16bits)
9287 | FRQV1:f>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9288 |  |  |  | HR9287 (Lo-16bits)
9289 | FRQV1:f>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9290 |  |  |  | HR9289 (Lo-16bits)
9291 | FRQV1:f>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9292 |  |  |  | HR9291 (Lo-16bits)
9293 | FRQV1:f>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9294 |  |  |  | HR9293 (Lo-16bits)
9295 | FRQV1:f>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9296 |  |  |  | HR9295 (Lo-16bits)
9297 | FRQV1:f>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9298 |  |  |  | HR9297 (Lo-16bits)
9299 | FRQV1:f>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9300 |  |  |  | HR9299 (Lo-16bits)
9301 | FRQV1:f>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9302 | FRQV1:f>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9303 | FRQV1:f>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9304 | FRQV1:f>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9305 | FRQV1:f>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9306 | FRQV1:f>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9307 | FRQV1:f>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9308 | FRQV1:f>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9309 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9310 |  |  |  | HR9309 (Lo-16bits)
9311 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9312 |  |  |  | HR9311 (Lo-16bits)
9313 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9314 |  |  |  | HR9313 (Lo-16bits)
9315 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9316 |  |  |  | HR9315 (Lo-16bits)
9317 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9318 |  |  |  | HR9317 (Lo-16bits)
9319 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9320 |  |  |  | HR9319 (Lo-16bits)
9321 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9322 |  |  |  | HR9321 (Lo-16bits)
9323 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9324 |  |  |  | HR9323 (Lo-16bits)
9325 | FRQV1:f>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9326 |  |  |  | HR9325 (Lo-16bits)
9327 | FRQV1:f>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9328 |  |  |  | HR9327 (Lo-16bits)
9329 | FRQV1:f>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9330 |  |  |  | HR9329 (Lo-16bits)
9331 | FRQV1:f>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9332 |  |  |  | HR9331 (Lo-16bits)
9333 | FRQV1:f>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9334 |  |  |  | HR9333 (Lo-16bits)
9335 | FRQV1:f>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9336 |  |  |  | HR9335 (Lo-16bits)
9337 | FRQV1:f>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9338 |  |  |  | HR9337 (Lo-16bits)
9339 | FRQV1:f>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9340 |  |  |  | HR9339 (Lo-16bits)
9341 | FRQV1:f>>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9342 | FRQV1:f>>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9343 | FRQV1:f>>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9344 | FRQV1:f>>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9345 | FRQV1:f>>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9346 | FRQV1:f>>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9347 | FRQV1:f>>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9348 | FRQV1:f>>>> used in setting group | R(W) | 1 | 0=No;1=Yes
9349 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9350 |  |  |  | HR9349 (Lo-16bits)
9351 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9352 |  |  |  | HR9351 (Lo-16bits)
9353 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9354 |  |  |  | HR9353 (Lo-16bits)
9355 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9356 |  |  |  | HR9355 (Lo-16bits)
9357 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9358 |  |  |  | HR9357 (Lo-16bits)
9359 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9360 |  |  |  | HR9359 (Lo-16bits)
9361 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9362 |  |  |  | HR9361 (Lo-16bits)
9363 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9364 |  |  |  | HR9363 (Lo-16bits)
9365 | FRQV1:f>>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9366 |  |  |  | HR9365 (Lo-16bits)
9367 | FRQV1:f>>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9368 |  |  |  | HR9367 (Lo-16bits)
9369 | FRQV1:f>>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9370 |  |  |  | HR9369 (Lo-16bits)
9371 | FRQV1:f>>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9372 |  |  |  | HR9371 (Lo-16bits)
9373 | FRQV1:f>>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9374 |  |  |  | HR9373 (Lo-16bits)
9375 | FRQV1:f>>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9376 |  |  |  | HR9375 (Lo-16bits)
9377 | FRQV1:f>>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9378 |  |  |  | HR9377 (Lo-16bits)
9379 | FRQV1:f>>>> operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9380 |  |  |  | HR9379 (Lo-16bits)
9381 | FRQV1:f< used in setting group | R(W) | 1 | 0=No;1=Yes
9382 | FRQV1:f< used in setting group | R(W) | 1 | 0=No;1=Yes
9383 | FRQV1:f< used in setting group | R(W) | 1 | 0=No;1=Yes
9384 | FRQV1:f< used in setting group | R(W) | 1 | 0=No;1=Yes
9385 | FRQV1:f< used in setting group | R(W) | 1 | 0=No;1=Yes
9386 | FRQV1:f< used in setting group | R(W) | 1 | 0=No;1=Yes
9387 | FRQV1:f< used in setting group | R(W) | 1 | 0=No;1=Yes
9388 | FRQV1:f< used in setting group | R(W) | 1 | 0=No;1=Yes
9389 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9390 |  |  |  | HR9389 (Lo-16bits)
9391 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9392 |  |  |  | HR9391 (Lo-16bits)
9393 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9394 |  |  |  | HR9393 (Lo-16bits)
9395 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9396 |  |  |  | HR9395 (Lo-16bits)
9397 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9398 |  |  |  | HR9397 (Lo-16bits)
9399 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9400 |  |  |  | HR9399 (Lo-16bits)
9401 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9402 |  |  |  | HR9401 (Lo-16bits)
9403 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9404 |  |  |  | HR9403 (Lo-16bits)
9405 | FRQV1:f< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9406 |  |  |  | HR9405 (Lo-16bits)
9407 | FRQV1:f< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9408 |  |  |  | HR9407 (Lo-16bits)
9409 | FRQV1:f< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9410 |  |  |  | HR9409 (Lo-16bits)
9411 | FRQV1:f< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9412 |  |  |  | HR9411 (Lo-16bits)
9413 | FRQV1:f< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9414 |  |  |  | HR9413 (Lo-16bits)
9415 | FRQV1:f< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9416 |  |  |  | HR9415 (Lo-16bits)
9417 | FRQV1:f< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9418 |  |  |  | HR9417 (Lo-16bits)
9419 | FRQV1:f< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9420 |  |  |  | HR9419 (Lo-16bits)
9421 | FRQV1:f<< used in setting group | R(W) | 1 | 0=No;1=Yes
9422 | FRQV1:f<< used in setting group | R(W) | 1 | 0=No;1=Yes
9423 | FRQV1:f<< used in setting group | R(W) | 1 | 0=No;1=Yes
9424 | FRQV1:f<< used in setting group | R(W) | 1 | 0=No;1=Yes
9425 | FRQV1:f<< used in setting group | R(W) | 1 | 0=No;1=Yes
9426 | FRQV1:f<< used in setting group | R(W) | 1 | 0=No;1=Yes
9427 | FRQV1:f<< used in setting group | R(W) | 1 | 0=No;1=Yes
9428 | FRQV1:f<< used in setting group | R(W) | 1 | 0=No;1=Yes
9429 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9430 |  |  |  | HR9429 (Lo-16bits)
9431 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9432 |  |  |  | HR9431 (Lo-16bits)
9433 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9434 |  |  |  | HR9433 (Lo-16bits)
9435 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9436 |  |  |  | HR9435 (Lo-16bits)
9437 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9438 |  |  |  | HR9437 (Lo-16bits)
9439 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9440 |  |  |  | HR9439 (Lo-16bits)
9441 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9442 |  |  |  | HR9441 (Lo-16bits)
9443 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9444 |  |  |  | HR9443 (Lo-16bits)
9445 | FRQV1:f<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9446 |  |  |  | HR9445 (Lo-16bits)
9447 | FRQV1:f<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9448 |  |  |  | HR9447 (Lo-16bits)
9449 | FRQV1:f<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9450 |  |  |  | HR9449 (Lo-16bits)
9451 | FRQV1:f<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9452 |  |  |  | HR9451 (Lo-16bits)
9453 | FRQV1:f<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9454 |  |  |  | HR9453 (Lo-16bits)
9455 | FRQV1:f<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9456 |  |  |  | HR9455 (Lo-16bits)
9457 | FRQV1:f<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9458 |  |  |  | HR9457 (Lo-16bits)
9459 | FRQV1:f<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9460 |  |  |  | HR9459 (Lo-16bits)
9461 | FRQV1:f<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9462 | FRQV1:f<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9463 | FRQV1:f<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9464 | FRQV1:f<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9465 | FRQV1:f<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9466 | FRQV1:f<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9467 | FRQV1:f<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9468 | FRQV1:f<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9469 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9470 |  |  |  | HR9469 (Lo-16bits)
9471 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9472 |  |  |  | HR9471 (Lo-16bits)
9473 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9474 |  |  |  | HR9473 (Lo-16bits)
9475 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9476 |  |  |  | HR9475 (Lo-16bits)
9477 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9478 |  |  |  | HR9477 (Lo-16bits)
9479 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9480 |  |  |  | HR9479 (Lo-16bits)
9481 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9482 |  |  |  | HR9481 (Lo-16bits)
9483 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9484 |  |  |  | HR9483 (Lo-16bits)
9485 | FRQV1:f<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9486 |  |  |  | HR9485 (Lo-16bits)
9487 | FRQV1:f<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9488 |  |  |  | HR9487 (Lo-16bits)
9489 | FRQV1:f<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9490 |  |  |  | HR9489 (Lo-16bits)
9491 | FRQV1:f<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9492 |  |  |  | HR9491 (Lo-16bits)
9493 | FRQV1:f<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9494 |  |  |  | HR9493 (Lo-16bits)
9495 | FRQV1:f<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9496 |  |  |  | HR9495 (Lo-16bits)
9497 | FRQV1:f<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9498 |  |  |  | HR9497 (Lo-16bits)
9499 | FRQV1:f<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9500 |  |  |  | HR9499 (Lo-16bits)
9501 | FRQV1:f<<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9502 | FRQV1:f<<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9503 | FRQV1:f<<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9504 | FRQV1:f<<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9505 | FRQV1:f<<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9506 | FRQV1:f<<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9507 | FRQV1:f<<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9508 | FRQV1:f<<<< used in setting group | R(W) | 1 | 0=No;1=Yes
9509 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9510 |  |  |  | HR9509 (Lo-16bits)
9511 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9512 |  |  |  | HR9511 (Lo-16bits)
9513 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9514 |  |  |  | HR9513 (Lo-16bits)
9515 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9516 |  |  |  | HR9515 (Lo-16bits)
9517 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9518 |  |  |  | HR9517 (Lo-16bits)
9519 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9520 |  |  |  | HR9519 (Lo-16bits)
9521 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9522 |  |  |  | HR9521 (Lo-16bits)
9523 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9524 |  |  |  | HR9523 (Lo-16bits)
9525 | FRQV1:f<<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9526 |  |  |  | HR9525 (Lo-16bits)
9527 | FRQV1:f<<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9528 |  |  |  | HR9527 (Lo-16bits)
9529 | FRQV1:f<<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9530 |  |  |  | HR9529 (Lo-16bits)
9531 | FRQV1:f<<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9532 |  |  |  | HR9531 (Lo-16bits)
9533 | FRQV1:f<<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9534 |  |  |  | HR9533 (Lo-16bits)
9535 | FRQV1:f<<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9536 |  |  |  | HR9535 (Lo-16bits)
9537 | FRQV1:f<<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9538 |  |  |  | HR9537 (Lo-16bits)
9539 | FRQV1:f<<<< operating time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9540 |  |  |  | HR9539 (Lo-16bits)
9541 | DEV:Serial number | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
9542 |  |  |  | HR9541 (Lo-16bits)
9543 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9544 |  |  |  | HR9543 (Lo-16bits)
9545 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9546 |  |  |  | HR9545 (Lo-16bits)
9547 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9548 |  |  |  | HR9547 (Lo-16bits)
9549 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9550 |  |  |  | HR9549 (Lo-16bits)
9551 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9552 |  |  |  | HR9551 (Lo-16bits)
9553 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9554 |  |  |  | HR9553 (Lo-16bits)
9555 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9556 |  |  |  | HR9555 (Lo-16bits)
9557 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9558 |  |  |  | HR9557 (Lo-16bits)
9559 | DEV:Firmware version | R | 2 | STRING [...32] (Hi-16bits)
9560 |  |  |  | HR9559 (Lo-16bits)
9561 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9562 |  |  |  | HR9561 (Lo-16bits)
9563 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9564 |  |  |  | HR9563 (Lo-16bits)
9565 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9566 |  |  |  | HR9565 (Lo-16bits)
9567 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9568 |  |  |  | HR9567 (Lo-16bits)
9569 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9570 |  |  |  | HR9569 (Lo-16bits)
9571 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9572 |  |  |  | HR9571 (Lo-16bits)
9573 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9574 |  |  |  | HR9573 (Lo-16bits)
9575 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9576 |  |  |  | HR9575 (Lo-16bits)
9577 | DEV:Hardware configuration | R | 2 | STRING [0...32] (Hi-16bits)
9578 |  |  |  | HR9577 (Lo-16bits)
9579 | MBTCP:Enable mapped setting value modification through Modbus | RW | 1 | 0=Disabled;1=Enabled
9580 | M1CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
9581 |  |  |  | HR9580 (Lo-16bits)
9582 | M1CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...10] (Hi-16bits)
9583 |  |  |  | HR9582 (Lo-16bits)
9584 | M1CT2:I01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
9585 |  |  |  | HR9584 (Lo-16bits)
9586 | M1CT2:I01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
9587 |  |  |  | HR9586 (Lo-16bits)
9588 | M1CT3:I02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
9589 |  |  |  | HR9588 (Lo-16bits)
9590 | M1CT3:I02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
9591 |  |  |  | HR9590 (Lo-16bits)
9592 | M2CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
9593 |  |  |  | HR9592 (Lo-16bits)
9594 | M2CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...10] (Hi-16bits)
9595 |  |  |  | HR9594 (Lo-16bits)
9596 | M2CT2:I''01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
9597 |  |  |  | HR9596 (Lo-16bits)
9598 | M2CT2:I''01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
9599 |  |  |  | HR9598 (Lo-16bits)
9600 | M2CT3:I''02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
9601 |  |  |  | HR9600 (Lo-16bits)
9602 | M2CT3:I''02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
9603 |  |  |  | HR9602 (Lo-16bits)
9604 | M1VT1:VT Primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
9605 |  |  |  | HR9604 (Lo-16bits)
9606 | M1VT1:VT Secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
9607 |  |  |  | HR9606 (Lo-16bits)
9608 | M1VT1:U3 Res/SS VT Primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
9609 |  |  |  | HR9608 (Lo-16bits)
9610 | M1VT1:U3 Res/SS VT Secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
9611 |  |  |  | HR9610 (Lo-16bits)
9612 | M1VT1:U4 Res/SS VT Primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
9613 |  |  |  | HR9612 (Lo-16bits)
9614 | M1VT1:U4 Res/SS VT Secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
9615 |  |  |  | HR9614 (Lo-16bits)
9616 | NOC1:I> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
9617 | NOC2:I>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
9618 | NOC3:I>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
9619 | NOC4:I>>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
9620 | NEF1:I0> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
9621 | NEF2:I0>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
9622 | NEF3:I0>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
9623 | NEF4:I0>>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
9624 | CUB1:I2> [46 46R 46L] mode | R(W) | 1 | 0=Disabled;1=Activated
9625 | CUB2:I2>> [46 46R 46L] mode | R(W) | 1 | 0=Disabled;1=Activated
9626 | CUB3:I2>>> [46 46R 46L] mode | R(W) | 1 | 0=Disabled;1=Activated
9627 | CUB4:I2>>>> [46 46R 46L] mode | R(W) | 1 | 0=Disabled;1=Activated
9628 | OV1:U> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
9629 | OV2:U>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
9630 | OV3:U>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
9631 | OV4:U>>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
9632 | UV1:U< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
9633 | UV2:U<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
9634 | UV3:U<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
9635 | UV4:U<<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
9636 | VUB1:U1/2 >/< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
9637 | VUB2:U1/2 >>/<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
9638 | VUB3:U1/2 >>>/<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
9639 | VUB4:U1/2 >>>>/<<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
9640 | FRQV1:f</> [81O/81U] mode | R(W) | 1 | 0=Disabled;1=Activated
9641 | DOC1:Idir> [67] mode | R(W) | 1 | 0=Disabled;1=Activated
9642 | DOC2:Idir>> [67] mode | R(W) | 1 | 0=Disabled;1=Activated
9643 | DOC3:Idir>>> [67] mode | R(W) | 1 | 0=Disabled;1=Activated
9644 | DOC4:Idir>>>> [67] mode | R(W) | 1 | 0=Disabled;1=Activated
9645 | DEF1:I0dir> [67N/32N] mode | R(W) | 1 | 0=Disabled;1=Activated
9646 | DEF2:I0dir>> [67N/32N] mode | R(W) | 1 | 0=Disabled;1=Activated
9647 | DEF3:I0dir>>> [67N/32N] mode | R(W) | 1 | 0=Disabled;1=Activated
9648 | DEF4:I0dir>>>> [67N/32N] mode | R(W) | 1 | 0=Disabled;1=Activated
9649 | LOGIC:Logical double bit Input 1 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9650 |  |  |  | HR9649 (Lo-16bits)
9651 | LOGIC:State00 for Logical double bit Input 1 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9652 |  |  |  | HR9651 (Lo-16bits)
9653 | LOGIC:State01 for Logical double bit Input 1 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9654 |  |  |  | HR9653 (Lo-16bits)
9655 | LOGIC:State10 for Logical double bit Input 1 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9656 |  |  |  | HR9655 (Lo-16bits)
9657 | LOGIC:State11 for Logical double bit Input 1 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9658 |  |  |  | HR9657 (Lo-16bits)
9659 | LOGIC:Logical double bit Input 2 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9660 |  |  |  | HR9659 (Lo-16bits)
9661 | LOGIC:State00 for Logical double bit Input 2 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9662 |  |  |  | HR9661 (Lo-16bits)
9663 | LOGIC:State01 for Logical double bit Input 2 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9664 |  |  |  | HR9663 (Lo-16bits)
9665 | LOGIC:State10 for Logical double bit Input 2 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9666 |  |  |  | HR9665 (Lo-16bits)
9667 | LOGIC:State11 for Logical double bit Input 2 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9668 |  |  |  | HR9667 (Lo-16bits)
9669 | LOGIC:Logical double bit Input 3 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9670 |  |  |  | HR9669 (Lo-16bits)
9671 | LOGIC:State00 for Logical double bit Input 3 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9672 |  |  |  | HR9671 (Lo-16bits)
9673 | LOGIC:State01 for Logical double bit Input 3 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9674 |  |  |  | HR9673 (Lo-16bits)
9675 | LOGIC:State10 for Logical double bit Input 3 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9676 |  |  |  | HR9675 (Lo-16bits)
9677 | LOGIC:State11 for Logical double bit Input 3 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9678 |  |  |  | HR9677 (Lo-16bits)
9679 | LOGIC:Logical double bit Input 4 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9680 |  |  |  | HR9679 (Lo-16bits)
9681 | LOGIC:State00 for Logical double bit Input 4 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9682 |  |  |  | HR9681 (Lo-16bits)
9683 | LOGIC:State01 for Logical double bit Input 4 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9684 |  |  |  | HR9683 (Lo-16bits)
9685 | LOGIC:State10 for Logical double bit Input 4 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9686 |  |  |  | HR9685 (Lo-16bits)
9687 | LOGIC:State11 for Logical double bit Input 4 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9688 |  |  |  | HR9687 (Lo-16bits)
9689 | LOGIC:Logical double bit Input 5 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9690 |  |  |  | HR9689 (Lo-16bits)
9691 | LOGIC:State00 for Logical double bit Input 5 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9692 |  |  |  | HR9691 (Lo-16bits)
9693 | LOGIC:State01 for Logical double bit Input 5 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9694 |  |  |  | HR9693 (Lo-16bits)
9695 | LOGIC:State10 for Logical double bit Input 5 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9696 |  |  |  | HR9695 (Lo-16bits)
9697 | LOGIC:State11 for Logical double bit Input 5 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9698 |  |  |  | HR9697 (Lo-16bits)
9699 | LOGIC:Logical double bit Input 6 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9700 |  |  |  | HR9699 (Lo-16bits)
9701 | LOGIC:State00 for Logical double bit Input 6 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9702 |  |  |  | HR9701 (Lo-16bits)
9703 | LOGIC:State01 for Logical double bit Input 6 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9704 |  |  |  | HR9703 (Lo-16bits)
9705 | LOGIC:State10 for Logical double bit Input 6 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9706 |  |  |  | HR9705 (Lo-16bits)
9707 | LOGIC:State11 for Logical double bit Input 6 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9708 |  |  |  | HR9707 (Lo-16bits)
9709 | LOGIC:Logical double bit Input 7 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9710 |  |  |  | HR9709 (Lo-16bits)
9711 | LOGIC:State00 for Logical double bit Input 7 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9712 |  |  |  | HR9711 (Lo-16bits)
9713 | LOGIC:State01 for Logical double bit Input 7 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9714 |  |  |  | HR9713 (Lo-16bits)
9715 | LOGIC:State10 for Logical double bit Input 7 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9716 |  |  |  | HR9715 (Lo-16bits)
9717 | LOGIC:State11 for Logical double bit Input 7 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9718 |  |  |  | HR9717 (Lo-16bits)
9719 | LOGIC:Logical double bit Input 8 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9720 |  |  |  | HR9719 (Lo-16bits)
9721 | LOGIC:State00 for Logical double bit Input 8 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9722 |  |  |  | HR9721 (Lo-16bits)
9723 | LOGIC:State01 for Logical double bit Input 8 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9724 |  |  |  | HR9723 (Lo-16bits)
9725 | LOGIC:State10 for Logical double bit Input 8 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9726 |  |  |  | HR9725 (Lo-16bits)
9727 | LOGIC:State11 for Logical double bit Input 8 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9728 |  |  |  | HR9727 (Lo-16bits)
9729 | LOGIC:Logical double bit Input 9 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9730 |  |  |  | HR9729 (Lo-16bits)
9731 | LOGIC:State00 for Logical double bit Input 9 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9732 |  |  |  | HR9731 (Lo-16bits)
9733 | LOGIC:State01 for Logical double bit Input 9 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9734 |  |  |  | HR9733 (Lo-16bits)
9735 | LOGIC:State10 for Logical double bit Input 9 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9736 |  |  |  | HR9735 (Lo-16bits)
9737 | LOGIC:State11 for Logical double bit Input 9 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9738 |  |  |  | HR9737 (Lo-16bits)
9739 | LOGIC:Logical double bit Input 10 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9740 |  |  |  | HR9739 (Lo-16bits)
9741 | LOGIC:State00 for Logical double bit Input 10 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9742 |  |  |  | HR9741 (Lo-16bits)
9743 | LOGIC:State01 for Logical double bit Input 10 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9744 |  |  |  | HR9743 (Lo-16bits)
9745 | LOGIC:State10 for Logical double bit Input 10 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9746 |  |  |  | HR9745 (Lo-16bits)
9747 | LOGIC:State11 for Logical double bit Input 10 | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9748 |  |  |  | HR9747 (Lo-16bits)
9749 | NOCS1:IPW> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=StartL1;5=StartL2;6=StartL3;7=TripL1;8=TripL2;9=TripL3;10=StartL1-2;11=StartL2-3;12=StartL3-1;13=TripL1-2;14=TripL2-3;15=TripL31;16=StartL1-2-3;17=TripL1-2-3
9750 | NOCS2:IPW>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=StartL1;5=StartL2;6=StartL3;7=TripL1;8=TripL2;9=TripL3;10=StartL1-2;11=StartL2-3;12=StartL3-1;13=TripL1-2;14=TripL2-3;15=TripL31;16=StartL1-2-3;17=TripL1-2-3
9751 | OBJS1:Phase-wise object Breaker Status A(L1) | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9752 | OBJS1:Phase-wise object Breaker Status B(L2) | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9753 | OBJS1:Phase-wise object Breaker Status C(L3) | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9754 | OBJS1:Phase-wise object Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
9755 | LOGIC:Logical Input 1 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9756 |  |  |  | HR9755 (Lo-16bits)
9757 | LOGIC:Logical Input 2 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9758 |  |  |  | HR9757 (Lo-16bits)
9759 | LOGIC:Logical Input 3 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9760 |  |  |  | HR9759 (Lo-16bits)
9761 | LOGIC:Logical Input 4 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9762 |  |  |  | HR9761 (Lo-16bits)
9763 | LOGIC:Logical Input 5 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9764 |  |  |  | HR9763 (Lo-16bits)
9765 | LOGIC:Logical Input 6 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9766 |  |  |  | HR9765 (Lo-16bits)
9767 | LOGIC:Logical Input 7 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9768 |  |  |  | HR9767 (Lo-16bits)
9769 | LOGIC:Logical Input 8 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9770 |  |  |  | HR9769 (Lo-16bits)
9771 | LOGIC:Logical Input 9 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9772 |  |  |  | HR9771 (Lo-16bits)
9773 | LOGIC:Logical Input 10 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9774 |  |  |  | HR9773 (Lo-16bits)
9775 | LOGIC:Logical Input 11 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9776 |  |  |  | HR9775 (Lo-16bits)
9777 | LOGIC:Logical Input 12 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9778 |  |  |  | HR9777 (Lo-16bits)
9779 | LOGIC:Logical Input 13 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9780 |  |  |  | HR9779 (Lo-16bits)
9781 | LOGIC:Logical Input 14 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9782 |  |  |  | HR9781 (Lo-16bits)
9783 | LOGIC:Logical Input 15 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9784 |  |  |  | HR9783 (Lo-16bits)
9785 | LOGIC:Logical Input 16 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9786 |  |  |  | HR9785 (Lo-16bits)
9787 | LOGIC:Logical Input 17 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9788 |  |  |  | HR9787 (Lo-16bits)
9789 | LOGIC:Logical Input 18 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9790 |  |  |  | HR9789 (Lo-16bits)
9791 | LOGIC:Logical Input 19 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9792 |  |  |  | HR9791 (Lo-16bits)
9793 | LOGIC:Logical Input 20 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9794 |  |  |  | HR9793 (Lo-16bits)
9795 | LOGIC:Logical Input 21 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9796 |  |  |  | HR9795 (Lo-16bits)
9797 | LOGIC:Logical Input 22 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9798 |  |  |  | HR9797 (Lo-16bits)
9799 | LOGIC:Logical Input 23 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9800 |  |  |  | HR9799 (Lo-16bits)
9801 | LOGIC:Logical Input 24 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9802 |  |  |  | HR9801 (Lo-16bits)
9803 | LOGIC:Logical Input 25 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9804 |  |  |  | HR9803 (Lo-16bits)
9805 | LOGIC:Logical Input 26 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9806 |  |  |  | HR9805 (Lo-16bits)
9807 | LOGIC:Logical Input 27 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9808 |  |  |  | HR9807 (Lo-16bits)
9809 | LOGIC:Logical Input 28 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9810 |  |  |  | HR9809 (Lo-16bits)
9811 | LOGIC:Logical Input 29 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9812 |  |  |  | HR9811 (Lo-16bits)
9813 | MEAS1:IL1 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9814 |  |  |  | HR9813 (Lo-16bits)
9815 | MEAS1:IL1 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9816 |  |  |  | HR9815 (Lo-16bits)
9817 | MEAS1:IL2 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9818 |  |  |  | HR9817 (Lo-16bits)
9819 | MEAS1:IL2 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9820 |  |  |  | HR9819 (Lo-16bits)
9821 | MEAS1:IL3 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9822 |  |  |  | HR9821 (Lo-16bits)
9823 | MEAS1:IL3 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9824 |  |  |  | HR9823 (Lo-16bits)
9825 | MEAS1:I01 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9826 |  |  |  | HR9825 (Lo-16bits)
9827 | MEAS1:I01 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9828 |  |  |  | HR9827 (Lo-16bits)
9829 | MEAS1:I02 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9830 |  |  |  | HR9829 (Lo-16bits)
9831 | MEAS1:I02 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9832 |  |  |  | HR9831 (Lo-16bits)
9833 | MEAS2:I''L1 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9834 |  |  |  | HR9833 (Lo-16bits)
9835 | MEAS2:I''L1 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9836 |  |  |  | HR9835 (Lo-16bits)
9837 | MEAS2:I''L2 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9838 |  |  |  | HR9837 (Lo-16bits)
9839 | MEAS2:I''L2 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9840 |  |  |  | HR9839 (Lo-16bits)
9841 | MEAS2:I''L3 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9842 |  |  |  | HR9841 (Lo-16bits)
9843 | MEAS2:I''L3 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9844 |  |  |  | HR9843 (Lo-16bits)
9845 | MEAS2:I''01 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9846 |  |  |  | HR9845 (Lo-16bits)
9847 | MEAS2:I''01 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9848 |  |  |  | HR9847 (Lo-16bits)
9849 | MEAS2:I''02 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9850 |  |  |  | HR9849 (Lo-16bits)
9851 | MEAS2:I''02 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9852 |  |  |  | HR9851 (Lo-16bits)
9853 | MEAS3:UL1 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9854 |  |  |  | HR9853 (Lo-16bits)
9855 | MEAS3:UL1 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9856 |  |  |  | HR9855 (Lo-16bits)
9857 | MEAS3:UL2 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9858 |  |  |  | HR9857 (Lo-16bits)
9859 | MEAS3:UL2 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9860 |  |  |  | HR9859 (Lo-16bits)
9861 | MEAS3:UL3 Amplitude THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9862 |  |  |  | HR9861 (Lo-16bits)
9863 | MEAS3:UL3 Power THD | R | 2 | FLOAT [0...100000] (Hi-16bits)
9864 |  |  |  | HR9863 (Lo-16bits)
9865 | POW1:Apparent Energy (S) while Export (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9866 |  |  |  | HR9865 (Lo-16bits)
9867 | POW1:Apparent Energy (S) while Export (P) kVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9868 |  |  |  | HR9867 (Lo-16bits)
9869 | POW1:Apparent Energy (S) while Import (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9870 |  |  |  | HR9869 (Lo-16bits)
9871 | POW1:Apparent Energy (S) while Import (P) kVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9872 |  |  |  | HR9871 (Lo-16bits)
9873 | POW1:Apparent Energy (S) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9874 |  |  |  | HR9873 (Lo-16bits)
9875 | POW1:Real Energy (P) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9876 |  |  |  | HR9875 (Lo-16bits)
9877 | POW1:Reactive Energy (Q) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9878 |  |  |  | HR9877 (Lo-16bits)
9879 | POW1:Real Energy (P) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9880 |  |  |  | HR9879 (Lo-16bits)
9881 | POW1:Reactive Energy (Q) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9882 |  |  |  | HR9881 (Lo-16bits)
9883 | POW1:Real Energy (P) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9884 |  |  |  | HR9883 (Lo-16bits)
9885 | POW1:Reactive Energy (Q) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9886 |  |  |  | HR9885 (Lo-16bits)
9887 | POW2:Apparent Energy (S) while Export (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9888 |  |  |  | HR9887 (Lo-16bits)
9889 | POW2:Apparent Energy (S) while Export (P) kVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9890 |  |  |  | HR9889 (Lo-16bits)
9891 | POW2:Apparent Energy (S) while Import (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9892 |  |  |  | HR9891 (Lo-16bits)
9893 | POW2:Apparent Energy (S) while Import (P) kVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9894 |  |  |  | HR9893 (Lo-16bits)
9895 | POW2:Apparent Energy (S) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9896 |  |  |  | HR9895 (Lo-16bits)
9897 | POW2:Real Energy (P) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9898 |  |  |  | HR9897 (Lo-16bits)
9899 | POW2:Reactive Energy (Q) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9900 |  |  |  | HR9899 (Lo-16bits)
9901 | POW2:Real Energy (P) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9902 |  |  |  | HR9901 (Lo-16bits)
9903 | POW2:Reactive Energy (Q) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9904 |  |  |  | HR9903 (Lo-16bits)
9905 | POW2:Real Energy (P) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9906 |  |  |  | HR9905 (Lo-16bits)
9907 | POW2:Reactive Energy (Q) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
9908 |  |  |  | HR9907 (Lo-16bits)
9909 | GNSIG:Common signals condition | R | 1 | 0=Normal;1=Start;2=Trip
9910 | UCP1:IUC> condition | R | 1 | 0=Normal;1=Blocked;2=StartOn(Alarm);3=StartOn(Alarm&Trip);4=StartOn(Trip);5=AlarmOn;6=StartOn(Alarm),TripOn;7=StartOn,AlarmOn;8=TripOn;9=AlarmOn,TripOn;10=MultistatusOn
9911 | CRF1:Cd> (87C) condition | R | 1 | 0=Normal;1=Trip;2=Blocked
9912 | FRQV1:f< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9913 |  |  |  | HR9912 (Lo-16bits)
9914 | FRQV1:f< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9915 |  |  |  | HR9914 (Lo-16bits)
9916 | FRQV1:f< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9917 |  |  |  | HR9916 (Lo-16bits)
9918 | FRQV1:f< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9919 |  |  |  | HR9918 (Lo-16bits)
9920 | FRQV1:f< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9921 |  |  |  | HR9920 (Lo-16bits)
9922 | FRQV1:f< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9923 |  |  |  | HR9922 (Lo-16bits)
9924 | FRQV1:f< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9925 |  |  |  | HR9924 (Lo-16bits)
9926 | FRQV1:f< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9927 |  |  |  | HR9926 (Lo-16bits)
9928 | FRQV1:f<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9929 |  |  |  | HR9928 (Lo-16bits)
9930 | FRQV1:f<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9931 |  |  |  | HR9930 (Lo-16bits)
9932 | FRQV1:f<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9933 |  |  |  | HR9932 (Lo-16bits)
9934 | FRQV1:f<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9935 |  |  |  | HR9934 (Lo-16bits)
9936 | FRQV1:f<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9937 |  |  |  | HR9936 (Lo-16bits)
9938 | FRQV1:f<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9939 |  |  |  | HR9938 (Lo-16bits)
9940 | FRQV1:f<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9941 |  |  |  | HR9940 (Lo-16bits)
9942 | FRQV1:f<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9943 |  |  |  | HR9942 (Lo-16bits)
9944 | FRQV1:f<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9945 |  |  |  | HR9944 (Lo-16bits)
9946 | FRQV1:f<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9947 |  |  |  | HR9946 (Lo-16bits)
9948 | FRQV1:f<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9949 |  |  |  | HR9948 (Lo-16bits)
9950 | FRQV1:f<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9951 |  |  |  | HR9950 (Lo-16bits)
9952 | FRQV1:f<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9953 |  |  |  | HR9952 (Lo-16bits)
9954 | FRQV1:f<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9955 |  |  |  | HR9954 (Lo-16bits)
9956 | FRQV1:f<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9957 |  |  |  | HR9956 (Lo-16bits)
9958 | FRQV1:f<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9959 |  |  |  | HR9958 (Lo-16bits)
9960 | FRQV1:f<<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9961 |  |  |  | HR9960 (Lo-16bits)
9962 | FRQV1:f<<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9963 |  |  |  | HR9962 (Lo-16bits)
9964 | FRQV1:f<<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9965 |  |  |  | HR9964 (Lo-16bits)
9966 | FRQV1:f<<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9967 |  |  |  | HR9966 (Lo-16bits)
9968 | FRQV1:f<<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9969 |  |  |  | HR9968 (Lo-16bits)
9970 | FRQV1:f<<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9971 |  |  |  | HR9970 (Lo-16bits)
9972 | FRQV1:f<<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9973 |  |  |  | HR9972 (Lo-16bits)
9974 | FRQV1:f<<<< Undervoltage block (0% no blocking) | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
9975 |  |  |  | HR9974 (Lo-16bits)
9976 | RHC1:Start count | R(W) | 2 | UINT32 [0...4294967295] (Hi-16bits)
9977 |  |  |  | HR9976 (Lo-16bits)
9978 | RTDIN:S1 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9979 | RTDIN:S2 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9980 | RTDIN:S3 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9981 | RTDIN:S4 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9982 | RTDIN:S5 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9983 | RTDIN:S6 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9984 | RTDIN:S7 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9985 | RTDIN:S8 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9986 | RTDIN:S9 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9987 | RTDIN:S10 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9988 | RTDIN:S11 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9989 | RTDIN:S12 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9990 | RTDIN:S13 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9991 | RTDIN:S14 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9992 | RTDIN:S15 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9993 | RTDIN:S16 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9994 | OOS1:Pole slip condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9995 | OOS1:Configuration status | R | 1 | 0=Ok;1=Incorrect VT set;2=Incorrect char. Set
9996 | OOS1:PoleSlip detection START | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9997 |  |  |  | HR9996 (Lo-16bits)
9998 | OOS1:PoleSlip TRIP | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9999 |  |  |  | HR9998 (Lo-16bits)
10000 | OOS1:PoleSlip detection BLOCKED | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
10001 |  |  |  | HR10000 (Lo-16bits)
10002 | GSYN:Enable on-screen synchronizer view | R(W) | 1 | 0=Disabled;1=Activated
10003 | GSYN:Synchronizing by | R(W) | 1 | 0=Autosynchronizer;1=Manual commands
10004 | GSYN:Manual switching mode | R(W) | 1 | 0=Assisted synchroswitch;1=I know what I am doing
10005 | GSYN:Magnitude side A | R | 2 | FLOAT [0...200] (Hi-16bits)
10006 |  |  |  | HR10005 (Lo-16bits)
10007 | GSYN:Magnitude side B | R | 2 | FLOAT [0...200] (Hi-16bits)
10008 |  |  |  | HR10007 (Lo-16bits)
10009 | GSYN:Frequency side A | R | 2 | FLOAT [0...75] (Hi-16bits)
10010 |  |  |  | HR10009 (Lo-16bits)
10011 | GSYN:Frequency side B | R | 2 | FLOAT [0...75] (Hi-16bits)
10012 |  |  |  | HR10011 (Lo-16bits)
10013 | GSYN:Open synchronizer HMI | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
10014 |  |  |  | HR10013 (Lo-16bits)
10015 | GSYN:Manual increase voltage | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
10016 |  |  |  | HR10015 (Lo-16bits)
10017 | GSYN:Manual decrease voltage | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
10018 |  |  |  | HR10017 (Lo-16bits)
10019 | GSYN:Manual increase frequency | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
10020 |  |  |  | HR10019 (Lo-16bits)
10021 | GSYN:Manual decrease frequency | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
10022 |  |  |  | HR10021 (Lo-16bits)
10023 | GSYN:Manual Close Breaker | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
10024 |  |  |  | HR10023 (Lo-16bits)
10025 | FREQS:SS1.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
10026 |  |  |  | HR10025 (Lo-16bits)
10027 | FREQS:SS2.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
10028 |  |  |  | HR10027 (Lo-16bits)
10029 | HSHC:HSO card inputs | R | 2 | 0b=HSO1 TCS In;1b=HSO2 TCS In;2b=HSO3 TCS In;3b=HSO4 TCS In;4b=HSO5 TCS In;5b=HSO6 TCS In;6b=HSO7 TCS In;7b=HSO8 TCS In;8b=HSO9 TCS In (Hi-16bits)
10030 |  |  |  | HR10029 (Lo-16bits)
10031 | SGS2:SGS2 Active setting group | R | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
10032 | SGS2:SGS2 Force setting group | R(W) | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
10033 | SGS2:SGS2 Force setting group change | R(W) | 1 | 0=Disabled;1=Enabled
10034 | SGS2:SGS2 Used setting groups | R(W) | 1 | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
10035 | SGS2:SGS2 Remote setting group change | R(W) | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
10036 | LOGIC:Logical Input 30 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
10037 |  |  |  | HR10036 (Lo-16bits)
10038 | LOGIC:Logical Input 31 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
10039 |  |  |  | HR10038 (Lo-16bits)
10040 | LOGIC:Logical Input 32 | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
10041 |  |  |  | HR10040 (Lo-16bits)
10042 | LDIF1:IdL> condition | R | 2 | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On (Hi-16bits)
10043 |  |  |  | HR10042 (Lo-16bits)
10044 | TOLT1:TT> setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault.Override to1.0
10045 | TOLT1:TT> setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault.Override to1.0
10046 | TOLT1:TT> setting alarm | R | 1 | 0=Nominalcurrent calc ok;1=Nominalcurrent set fault.Overrideto1.0
10047 | TOLT1:TT> setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
10048 | TOLF1:TF> setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault.Override to1.0
10049 | TOLF1:TF> setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault.Override to1.0
10050 | TOLF1:TF> setting alarm | R | 1 | 0=Nominalcurrent calc ok;1=Nominalcurrent set fault.Overrideto1.0
10051 | TOLF1:TF> setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
10052 | TOLM1:TM>Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault.Override to1.0
10053 | TOLM1:TM>Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault.Override to1.0
10054 | TOLM1:TM>Setting alarm | R | 1 | 0=Nominalcurrent calc ok;1=Nominalcurrent set fault.Overrideto1.0
10055 | TOLM1:TM>Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
10056 | URX1:X< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
10057 | URX2:X<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
10058 | SYN1:SYN1 Mag diff | R | 2 | FLOAT [-120...120] (Hi-16bits)
10059 |  |  |  | HR10058 (Lo-16bits)
10060 | SYN1:SYN1 Ang diff | R | 2 | FLOAT [-360...360] (Hi-16bits)
10061 |  |  |  | HR10060 (Lo-16bits)
10062 | SYN1:SYN1 freq diff | R | 2 | FLOAT [-75...75] (Hi-16bits)
10063 |  |  |  | HR10062 (Lo-16bits)
10064 | COL1:ICOL> [49OL] mode | R(W) | 1 | 0=Disabled;1=Activated
10065 | COL2:ICOL>> [49OL] mode | R(W) | 1 | 0=Disabled;1=Activated
10066 | CNU1:CNU> [50UB] mode | R(W) | 1 | 0=Disabled;1=Activated
10067 | UCP1:IUC> [46C] mode | R(W) | 1 | 0=Disabled;1=Activated
10068 | CRF1:Cd> (87C) mode | R(W) | 1 | 0=Disabled;1=Activated
10069 | NOCS1:IPW> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
10070 | NOCS2:IPW>> mode | R(W) | 1 | 0=Disabled;1=Activated
10071 | EFX1:I0x> [67NX] mode | R(W) | 1 | 0=Disabled;1=Activated
10072 | EFX1:Used U0> reference | R | 1 | 0=VT meas.mode error;1=U3 Input;2=U4 Input
10073 | EFX1:I0x> condition | R | 1 | 0=Normal;1=Start forward;2=Trip forward;3=Blocked;4=Start reverse;5=Trip reverse
10074 | EFX1:I0x> Last fault active residual power | R | 2 | FLOAT [0...1000000] (Hi-16bits)
10075 |  |  |  | HR10074 (Lo-16bits)
10076 | EFX1:I0x> Last fault apparent residual power | R | 2 | FLOAT [0...1000000] (Hi-16bits)
10077 |  |  |  | HR10076 (Lo-16bits)
10078 | EFX1:I0x> Last fault apparent/active residual power | R | 2 | FLOAT [0...1000000] (Hi-16bits)
10079 |  |  |  | HR10078 (Lo-16bits)
10080 | EFX1:I0x> Last fault residual current | R | 2 | FLOAT [0...1000000] (Hi-16bits)
10081 |  |  |  | HR10080 (Lo-16bits)
10082 | EFX1:I0x> Last fault zero sequence voltage | R | 2 | FLOAT [0...1000000] (Hi-16bits)
10083 |  |  |  | HR10082 (Lo-16bits)
10084 | EFX1:Sw (active residual power pickup FWD) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10085 |  |  |  | HR10084 (Lo-16bits)
10086 | EFX1:Sw (active residual power pickup FWD) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10087 |  |  |  | HR10086 (Lo-16bits)
10088 | EFX1:Sw (active residual power pickup FWD) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10089 |  |  |  | HR10088 (Lo-16bits)
10090 | EFX1:Sw (active residual power pickup FWD) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10091 |  |  |  | HR10090 (Lo-16bits)
10092 | EFX1:Sw (active residual power pickup FWD) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10093 |  |  |  | HR10092 (Lo-16bits)
10094 | EFX1:Sw (active residual power pickup FWD) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10095 |  |  |  | HR10094 (Lo-16bits)
10096 | EFX1:Sw (active residual power pickup FWD) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10097 |  |  |  | HR10096 (Lo-16bits)
10098 | EFX1:Sw (active residual power pickup FWD) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10099 |  |  |  | HR10098 (Lo-16bits)
10100 | EFX1:@Sw (active residual power pickup REV) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10101 |  |  |  | HR10100 (Lo-16bits)
10102 | EFX1:@Sw (active residual power pickup REV) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10103 |  |  |  | HR10102 (Lo-16bits)
10104 | EFX1:@Sw (active residual power pickup REV) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10105 |  |  |  | HR10104 (Lo-16bits)
10106 | EFX1:@Sw (active residual power pickup REV) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10107 |  |  |  | HR10106 (Lo-16bits)
10108 | EFX1:@Sw (active residual power pickup REV) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10109 |  |  |  | HR10108 (Lo-16bits)
10110 | EFX1:@Sw (active residual power pickup REV) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10111 |  |  |  | HR10110 (Lo-16bits)
10112 | EFX1:@Sw (active residual power pickup REV) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10113 |  |  |  | HR10112 (Lo-16bits)
10114 | EFX1:@Sw (active residual power pickup REV) | R(W) | 2 | FLOAT [20...120] (Hi-16bits)
10115 |  |  |  | HR10114 (Lo-16bits)
10116 | EFX1:Sw/@Sw hysteresis | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10117 |  |  |  | HR10116 (Lo-16bits)
10118 | EFX1:Sw/@Sw hysteresis | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10119 |  |  |  | HR10118 (Lo-16bits)
10120 | EFX1:Sw/@Sw hysteresis | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10121 |  |  |  | HR10120 (Lo-16bits)
10122 | EFX1:Sw/@Sw hysteresis | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10123 |  |  |  | HR10122 (Lo-16bits)
10124 | EFX1:Sw/@Sw hysteresis | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10125 |  |  |  | HR10124 (Lo-16bits)
10126 | EFX1:Sw/@Sw hysteresis | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10127 |  |  |  | HR10126 (Lo-16bits)
10128 | EFX1:Sw/@Sw hysteresis | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10129 |  |  |  | HR10128 (Lo-16bits)
10130 | EFX1:Sw/@Sw hysteresis | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10131 |  |  |  | HR10130 (Lo-16bits)
10132 | EFX1:S/P (angle pickup) | R(W) | 2 | FLOAT [0...20] (Hi-16bits)
10133 |  |  |  | HR10132 (Lo-16bits)
10134 | EFX1:S/P (angle pickup) | R(W) | 2 | FLOAT [0...20] (Hi-16bits)
10135 |  |  |  | HR10134 (Lo-16bits)
10136 | EFX1:S/P (angle pickup) | R(W) | 2 | FLOAT [0...20] (Hi-16bits)
10137 |  |  |  | HR10136 (Lo-16bits)
10138 | EFX1:S/P (angle pickup) | R(W) | 2 | FLOAT [0...20] (Hi-16bits)
10139 |  |  |  | HR10138 (Lo-16bits)
10140 | EFX1:S/P (angle pickup) | R(W) | 2 | FLOAT [0...20] (Hi-16bits)
10141 |  |  |  | HR10140 (Lo-16bits)
10142 | EFX1:S/P (angle pickup) | R(W) | 2 | FLOAT [0...20] (Hi-16bits)
10143 |  |  |  | HR10142 (Lo-16bits)
10144 | EFX1:S/P (angle pickup) | R(W) | 2 | FLOAT [0...20] (Hi-16bits)
10145 |  |  |  | HR10144 (Lo-16bits)
10146 | EFX1:S/P (angle pickup) | R(W) | 2 | FLOAT [0...20] (Hi-16bits)
10147 |  |  |  | HR10146 (Lo-16bits)
10148 | EFX1:S/P (angle threshold) | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10149 |  |  |  | HR10148 (Lo-16bits)
10150 | EFX1:S/P (angle threshold) | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10151 |  |  |  | HR10150 (Lo-16bits)
10152 | EFX1:S/P (angle threshold) | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10153 |  |  |  | HR10152 (Lo-16bits)
10154 | EFX1:S/P (angle threshold) | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10155 |  |  |  | HR10154 (Lo-16bits)
10156 | EFX1:S/P (angle threshold) | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10157 |  |  |  | HR10156 (Lo-16bits)
10158 | EFX1:S/P (angle threshold) | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10159 |  |  |  | HR10158 (Lo-16bits)
10160 | EFX1:S/P (angle threshold) | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10161 |  |  |  | HR10160 (Lo-16bits)
10162 | EFX1:S/P (angle threshold) | R(W) | 2 | FLOAT [0.85...0.95] (Hi-16bits)
10163 |  |  |  | HR10162 (Lo-16bits)
10164 | EFX1:Operating time | R(W) | 2 | FLOAT [0.02...5] (Hi-16bits)
10165 |  |  |  | HR10164 (Lo-16bits)
10166 | EFX1:Operating time | R(W) | 2 | FLOAT [0.02...5] (Hi-16bits)
10167 |  |  |  | HR10166 (Lo-16bits)
10168 | EFX1:Operating time | R(W) | 2 | FLOAT [0.02...5] (Hi-16bits)
10169 |  |  |  | HR10168 (Lo-16bits)
10170 | EFX1:Operating time | R(W) | 2 | FLOAT [0.02...5] (Hi-16bits)
10171 |  |  |  | HR10170 (Lo-16bits)
10172 | EFX1:Operating time | R(W) | 2 | FLOAT [0.02...5] (Hi-16bits)
10173 |  |  |  | HR10172 (Lo-16bits)
10174 | EFX1:Operating time | R(W) | 2 | FLOAT [0.02...5] (Hi-16bits)
10175 |  |  |  | HR10174 (Lo-16bits)
10176 | EFX1:Operating time | R(W) | 2 | FLOAT [0.02...5] (Hi-16bits)
10177 |  |  |  | HR10176 (Lo-16bits)
10178 | EFX1:Operating time | R(W) | 2 | FLOAT [0.02...5] (Hi-16bits)
10179 |  |  |  | HR10178 (Lo-16bits)
10180 | EFX1:Release delay | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10181 |  |  |  | HR10180 (Lo-16bits)
10182 | EFX1:Release delay | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10183 |  |  |  | HR10182 (Lo-16bits)
10184 | EFX1:Release delay | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10185 |  |  |  | HR10184 (Lo-16bits)
10186 | EFX1:Release delay | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10187 |  |  |  | HR10186 (Lo-16bits)
10188 | EFX1:Release delay | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10189 |  |  |  | HR10188 (Lo-16bits)
10190 | EFX1:Release delay | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10191 |  |  |  | HR10190 (Lo-16bits)
10192 | EFX1:Release delay | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10193 |  |  |  | HR10192 (Lo-16bits)
10194 | EFX1:Release delay | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10195 |  |  |  | HR10194 (Lo-16bits)
10196 | IEF1:I0Int> [67NT] mode | R(W) | 1 | 0=Disabled;1=Activated
10197 | HOC1:Ih> [50H/51H/68H] mode | R(W) | 1 | 0=Disabled;1=Activated
10198 | HOC2:Ih>> [50H/51H/68H] mode | R(W) | 1 | 0=Disabled;1=Activated
10199 | HOC3:Ih>>> [50H/51H/68H] mode | R(W) | 1 | 0=Disabled;1=Activated
10200 | HOC4:Ih>>>> [50H/51H/68H] mode | R(W) | 1 | 0=Disabled;1=Activated
10201 | CLP1:CLP mode | R(W) | 1 | 0=Disabled;1=Activated
10202 | CBF1:CBFP [50BF] mode | R(W) | 1 | 0=Disabled;1=Activated
10203 | DIF1:Idx> [87T/87G/87M/87N] mode | R(W) | 1 | 0=Disabled;1=Activated
10204 | LDIF1:IdL> [87L] mode | R(W) | 1 | 0=Disabled;1=Activated
10205 | REF1:I0d> [87N] mode | R(W) | 1 | 0=Disabled;1=Activated
10206 | TOLT1:TT> [49T] mode | R(W) | 1 | 0=Disabled;1=Activated
10207 | TOLF1:TF> [49F] mode | R(W) | 1 | 0=Disabled;1=Activated
10208 | TOLF1:IN thermal cap current | R(W) | 2 | FLOAT [0...40] (Hi-16bits)
10209 |  |  |  | HR10208 (Lo-16bits)
10210 | TOLF1:Obj.Max.temp (tmax=100%) | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
10211 |  |  |  | HR10210 (Lo-16bits)
10212 | TOLF1:Man.Amb.Temp.Set | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10213 |  |  |  | HR10212 (Lo-16bits)
10214 | TOLF1:RTD Module | R(W) | 1 | 0=ModuleA;1=ModuleB;2=ModuleC;
10215 | TOLF1:RTD Channel | R(W) | 1 | 0=Ch0;1=Ch1;2=Ch2;3=Ch3;4=Ch4;5=Ch5;6=Ch6;7=Ch7
10216 | TOLF1:RTD Deg C / Deg F | R(W) | 1 | 0=Deg C;1=Deg F
10217 | TOLF1:RTD Amb.Temp.Read | R(W) | 2 | FLOAT [-101...2000] (Hi-16bits)
10218 |  |  |  | HR10217 (Lo-16bits)
10219 | TOLF1:tau (t const) | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
10220 |  |  |  | HR10219 (Lo-16bits)
10221 | TOLF1:Max.Perm.OC.Current(norm Ik1s) | R(W) | 2 | FLOAT [1...9999999] (Hi-16bits)
10222 |  |  |  | HR10221 (Lo-16bits)
10223 | TOLF1:Max.OC.Time (norm 1s) | R(W) | 2 | FLOAT [0.1...5] (Hi-16bits)
10224 |  |  |  | HR10223 (Lo-16bits)
10225 | TOLF1:Nominal current | R(W) | 2 | FLOAT [1...9999999] (Hi-16bits)
10226 |  |  |  | HR10225 (Lo-16bits)
10227 | TOLF1:kSF (service factor) | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10228 |  |  |  | HR10227 (Lo-16bits)
10229 | TOLF1:Cold Reset default theta | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
10230 |  |  |  | HR10229 (Lo-16bits)
10231 | TOLF1:Ambient lin or curve | R(W) | 1 | 0=Linear est.;1=Set Curve
10232 | TOLF1:Temp. reference (tref) kamb=1.00 | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
10233 |  |  |  | HR10232 (Lo-16bits)
10234 | TOLF1:Max.ambient temp | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
10235 |  |  |  | HR10234 (Lo-16bits)
10236 | TOLF1:k at max.amb.temp. | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10237 |  |  |  | HR10236 (Lo-16bits)
10238 | TOLF1:Min.ambient temp | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
10239 |  |  |  | HR10238 (Lo-16bits)
10240 | TOLF1:k at min.amb.temp. | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10241 |  |  |  | HR10240 (Lo-16bits)
10242 | TOLF1:Amb.Temp.ref1 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10243 |  |  |  | HR10242 (Lo-16bits)
10244 | TOLF1:Amb.Temp.k1 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10245 |  |  |  | HR10244 (Lo-16bits)
10246 | TOLF1:Amb.Temp.ref2 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10247 |  |  |  | HR10246 (Lo-16bits)
10248 | TOLF1:Amb.Temp.k2 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10249 |  |  |  | HR10248 (Lo-16bits)
10250 | TOLF1:Add curvepoint 3 | R(W) | 1 | 0=Not used;1=Used
10251 | TOLF1:Amb.Temp.ref3 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10252 |  |  |  | HR10251 (Lo-16bits)
10253 | TOLF1:Amb.Temp.k3 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10254 |  |  |  | HR10253 (Lo-16bits)
10255 | TOLF1:Add curvepoint 4 | R(W) | 1 | 0=Not used;1=Used
10256 | TOLF1:Amb.Temp.ref4 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10257 |  |  |  | HR10256 (Lo-16bits)
10258 | TOLF1:Amb.Temp.k4 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10259 |  |  |  | HR10258 (Lo-16bits)
10260 | TOLF1:Add curvepoint 5 | R(W) | 1 | 0=Not used;1=Used
10261 | TOLF1:Amb.Temp.ref5 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10262 |  |  |  | HR10261 (Lo-16bits)
10263 | TOLF1:Amb.Temp.k5 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10264 |  |  |  | HR10263 (Lo-16bits)
10265 | TOLF1:Add curvepoint 6 | R(W) | 1 | 0=Not used;1=Used
10266 | TOLF1:Amb.Temp.ref6 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10267 |  |  |  | HR10266 (Lo-16bits)
10268 | TOLF1:Amb.Temp.k6 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10269 |  |  |  | HR10268 (Lo-16bits)
10270 | TOLF1:Add curvepoint 7 | R(W) | 1 | 0=Not used;1=Used
10271 | TOLF1:Amb.Temp.ref7 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10272 |  |  |  | HR10271 (Lo-16bits)
10273 | TOLF1:Amb.Temp.k7 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10274 |  |  |  | HR10273 (Lo-16bits)
10275 | TOLF1:Add curvepoint 8 | R(W) | 1 | 0=Not used;1=Used
10276 | TOLF1:Amb.Temp.ref8 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10277 |  |  |  | HR10276 (Lo-16bits)
10278 | TOLF1:Amb.Temp.k8 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10279 |  |  |  | HR10278 (Lo-16bits)
10280 | TOLF1:Add curvepoint 9 | R(W) | 1 | 0=Not used;1=Used
10281 | TOLF1:Amb.Temp.ref9 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10282 |  |  |  | HR10281 (Lo-16bits)
10283 | TOLF1:Amb.Temp.k9 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10284 |  |  |  | HR10283 (Lo-16bits)
10285 | TOLF1:Add curvepoint 10 | R(W) | 1 | 0=Not used;1=Used
10286 | TOLF1:Amb.Temp.ref10 | R(W) | 2 | FLOAT [-60...500] (Hi-16bits)
10287 |  |  |  | HR10286 (Lo-16bits)
10288 | TOLF1:Amb.Temp.k10 | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
10289 |  |  |  | HR10288 (Lo-16bits)
10290 | TOLM1:TM> [49M] mode | R(W) | 1 | 0=Disabled;1=Activated
10291 | TOLM1:Curve AI | R(W) | 1 | 0=Disabled;1=Enabled
10292 | LCR1:ISt> [48/14/50LR] mode | R(W) | 1 | 0=Disabled;1=Activated
10293 | FSP1:N> [66/86] mode | R(W) | 1 | 0=Disabled;1=Activated
10294 | NUC1:I< [37] mode | R(W) | 1 | 0=Disabled;1=Activated
10295 | MJP1:Im> [50M/51M] mode | R(W) | 1 | 0=Disabled;1=Activated
10296 | NOV1:U0> [59N] mode | R(W) | 1 | 0=Disabled;1=Activated
10297 | NOV2:U0>> [59N] mode | R(W) | 1 | 0=Disabled;1=Activated
10298 | NOV3:U0>>> [59N] mode | R(W) | 1 | 0=Disabled;1=Activated
10299 | NOV4:U0>>>> [59N] mode | R(W) | 1 | 0=Disabled;1=Activated
10300 | PGS1:PSx >/< [99] mode | R(W) | 1 | 0=Disabled;1=Activated
10301 | FRQC1:f</> [Curr] mode | R(W) | 1 | 0=Disabled;1=Activated
10302 | DFT1:df/dt >/< [81] mode | R(W) | 1 | 0=Disabled;1=Activated
10303 | RHC1:Running Hour Counter mode | R(W) | 1 | 0=Disabled;1=Activated
10304 | PWR1:PQS>/< [32] mode | R(W) | 1 | 0=Disabled;1=Activated
10305 | PWR2:PQS>>/<< [32] mode | R(W) | 1 | 0=Disabled;1=Activated
10306 | PWR3:PQS>>>/<<< [32] mode | R(W) | 1 | 0=Disabled;1=Activated
10307 | PWR4:PQS>>>>/<<<< [32] mode | R(W) | 1 | 0=Disabled;1=Activated
10308 | OPW1:P> [32] mode (OBSOLETE) | R(W) | 1 | 0=Disabled;1=Activated
10309 | UPW1:P< [37] mode (OBSOLETE) | R(W) | 1 | 0=Disabled;1=Activated
10310 | RPW1:Prev> [32] mode (OBSOLETE) | R(W) | 1 | 0=Disabled;1=Activated
10311 | SEF1:U03rd< [64S] mode | R(W) | 1 | 0=Disabled;1=Activated
10312 | UEX1:Q< [40] mode | R(W) | 1 | 0=Disabled;1=Activated
10313 | UIM1:Z< [21U] mode | R(W) | 1 | 0=Disabled;1=Activated
10314 | UIM2:Z<< [21U] mode | R(W) | 1 | 0=Disabled;1=Activated
10315 | URX1:X< [40] mode | R(W) | 1 | 0=Disabled;1=Activated
10316 | URX2:X<< [40] mode | R(W) | 1 | 0=Disabled;1=Activated
10317 | VOC1:Iv> [51V] mode | R(W) | 1 | 0=Disabled;1=Activated
10318 | IAE1:I>U< I.A.E. [50/27] mode | R(W) | 1 | 0=Disabled;1=Activated
10319 | VHZ1:V/Hz > [24] mode | R(W) | 1 | 0=Disabled;1=Activated
10320 | UPF1:PF< [55] mode | R(W) | 1 | 0=Disabled;1=Activated
10321 | RTD1:RTD mode | R(W) | 1 | 0=Disabled;1=Activated
10322 | OOS1:Pole slip [78] mode | R(W) | 1 | 0=Disabled;1=Activated
10323 | ARC1:I/I0 Arc> [50ARC/50NARC] mode | R(W) | 1 | 0=Disabled;1=Activated
10324 | ARC1:I/I0 Arc> Self supervision test pulse on option card 1 | R(W) | 1 | 0=Disabled;1=On
10325 | ARC1:I/I0 Arc> Number of connected arc sub-units on option card 1 | R(W) | 1 | 0=1 AQ-101;1=2 AQ-101;2=3 AQ-101;3=4 AQ-101;4=5 AQ-101;5=6 AQ-101;6=7 AQ-101;7=8 AQ-101
10326 | ARC1:I/I0 Arc> arc sub-unit status on option card 1 | R(W) | 1 | 0=AQ101 unit count match;1=AQ 101 unit count mismatch
10327 | ARC1:Sensor status | R | 2 | 0b=Ph Curr Blocked;1b=Ph Curr Start;2b=Res Curr Blocked;3b=Res Curr Start;4b=Channel1 Light;5b=Channel1 Pressure;6b=Channel2 Light;7b=Channel2 Pressure;8b=Channel3 Light;9b=Channel3 Pressure;10b=Channel4 Light;11b=Channel4 Pressure;12b=Digital input;13b=I/I0 Arc> Sensor 1 Fault;14b=I/I0 Arc> Sensor 2 Fault;15b=I/I0 Arc> Sensor 3 Fault;16b=I/I0 Arc> Sensor 4 Fault;17b=I/I0 Arc> I/O-unit Fault (Hi-16bits)
10328 |  |  |  | HR10327 (Lo-16bits)
10329 | ARC1:Channel 1 sensors | R(W) | 1 | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
10330 | ARC1:Channel 1 sensor status | R | 1 | 0=Sensors Ok;1=Configuration fault
10331 | ARC1:Channel 2 sensors | R(W) | 1 | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
10332 | ARC1:Channel 2 sensor status | R | 1 | 0=Sensors Ok;1=Configuration fault
10333 | ARC1:Channel 3 sensors | R(W) | 1 | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
10334 | ARC1:Channel 3 sensor status | R | 1 | 0=Sensors Ok;1=Configuration fault
10335 | ARC1:Channel 4 sensors | R(W) | 1 | 0=No Sensors;1=1 Sensor;2=2 Sensors;3=3 Sensors
10336 | ARC1:Channel 4 sensor status | R | 1 | 0=Sensors Ok;1=Configuration fault
10337 | ARC1:Phase current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10338 |  |  |  | HR10337 (Lo-16bits)
10339 | ARC1:Phase current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10340 |  |  |  | HR10339 (Lo-16bits)
10341 | ARC1:Phase current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10342 |  |  |  | HR10341 (Lo-16bits)
10343 | ARC1:Phase current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10344 |  |  |  | HR10343 (Lo-16bits)
10345 | ARC1:Phase current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10346 |  |  |  | HR10345 (Lo-16bits)
10347 | ARC1:Phase current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10348 |  |  |  | HR10347 (Lo-16bits)
10349 | ARC1:Phase current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10350 |  |  |  | HR10349 (Lo-16bits)
10351 | ARC1:Phase current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10352 |  |  |  | HR10351 (Lo-16bits)
10353 | ARC1:I0 input selection | R(W) | 1 | 0=None;1=I01;2=I02
10354 | ARC1:I0 input selection | R(W) | 1 | 0=None;1=I01;2=I02
10355 | ARC1:I0 input selection | R(W) | 1 | 0=None;1=I01;2=I02
10356 | ARC1:I0 input selection | R(W) | 1 | 0=None;1=I01;2=I02
10357 | ARC1:I0 input selection | R(W) | 1 | 0=None;1=I01;2=I02
10358 | ARC1:I0 input selection | R(W) | 1 | 0=None;1=I01;2=I02
10359 | ARC1:I0 input selection | R(W) | 1 | 0=None;1=I01;2=I02
10360 | ARC1:I0 input selection | R(W) | 1 | 0=None;1=I01;2=I02
10361 | ARC1:Res. current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10362 |  |  |  | HR10361 (Lo-16bits)
10363 | ARC1:Res. current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10364 |  |  |  | HR10363 (Lo-16bits)
10365 | ARC1:Res. current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10366 |  |  |  | HR10365 (Lo-16bits)
10367 | ARC1:Res. current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10368 |  |  |  | HR10367 (Lo-16bits)
10369 | ARC1:Res. current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10370 |  |  |  | HR10369 (Lo-16bits)
10371 | ARC1:Res. current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10372 |  |  |  | HR10371 (Lo-16bits)
10373 | ARC1:Res. current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10374 |  |  |  | HR10373 (Lo-16bits)
10375 | ARC1:Res. current pick-up | R(W) | 2 | FLOAT [0.05...40] (Hi-16bits)
10376 |  |  |  | HR10375 (Lo-16bits)
10377 | ARC1:Zone1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10378 | ARC1:Zone1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10379 | ARC1:Zone1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10380 | ARC1:Zone1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10381 | ARC1:Zone1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10382 | ARC1:Zone1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10383 | ARC1:Zone1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10384 | ARC1:Zone1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10385 | ARC1:Zone1 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10386 | ARC1:Zone1 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10387 | ARC1:Zone1 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10388 | ARC1:Zone1 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10389 | ARC1:Zone1 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10390 | ARC1:Zone1 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10391 | ARC1:Zone1 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10392 | ARC1:Zone1 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10393 | ARC1:Zone1 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10394 | ARC1:Zone1 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10395 | ARC1:Zone1 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10396 | ARC1:Zone1 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10397 | ARC1:Zone1 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10398 | ARC1:Zone1 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10399 | ARC1:Zone1 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10400 | ARC1:Zone1 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10401 | ARC1:Zone1 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10402 | ARC1:Zone1 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10403 | ARC1:Zone1 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10404 | ARC1:Zone1 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10405 | ARC1:Zone1 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10406 | ARC1:Zone1 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10407 | ARC1:Zone1 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10408 | ARC1:Zone1 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10409 | ARC1:Zone1 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10410 | ARC1:Zone1 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10411 | ARC1:Zone1 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10412 | ARC1:Zone1 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10413 | ARC1:Zone1 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10414 | ARC1:Zone1 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10415 | ARC1:Zone1 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10416 | ARC1:Zone1 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10417 | ARC1:Zone1 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10418 | ARC1:Zone1 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10419 | ARC1:Zone1 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10420 | ARC1:Zone1 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10421 | ARC1:Zone1 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10422 | ARC1:Zone1 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10423 | ARC1:Zone1 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10424 | ARC1:Zone1 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10425 | ARC1:Zone1 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10426 | ARC1:Zone1 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10427 | ARC1:Zone1 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10428 | ARC1:Zone1 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10429 | ARC1:Zone1 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10430 | ARC1:Zone1 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10431 | ARC1:Zone1 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10432 | ARC1:Zone1 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10433 | ARC1:Zone1 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10434 | ARC1:Zone1 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10435 | ARC1:Zone1 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10436 | ARC1:Zone1 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10437 | ARC1:Zone1 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10438 | ARC1:Zone1 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10439 | ARC1:Zone1 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10440 | ARC1:Zone1 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10441 | ARC1:Zone2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10442 | ARC1:Zone2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10443 | ARC1:Zone2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10444 | ARC1:Zone2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10445 | ARC1:Zone2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10446 | ARC1:Zone2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10447 | ARC1:Zone2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10448 | ARC1:Zone2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10449 | ARC1:Zone2 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10450 | ARC1:Zone2 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10451 | ARC1:Zone2 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10452 | ARC1:Zone2 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10453 | ARC1:Zone2 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10454 | ARC1:Zone2 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10455 | ARC1:Zone2 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10456 | ARC1:Zone2 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10457 | ARC1:Zone2 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10458 | ARC1:Zone2 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10459 | ARC1:Zone2 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10460 | ARC1:Zone2 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10461 | ARC1:Zone2 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10462 | ARC1:Zone2 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10463 | ARC1:Zone2 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10464 | ARC1:Zone2 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10465 | ARC1:Zone2 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10466 | ARC1:Zone2 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10467 | ARC1:Zone2 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10468 | ARC1:Zone2 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10469 | ARC1:Zone2 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10470 | ARC1:Zone2 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10471 | ARC1:Zone2 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10472 | ARC1:Zone2 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10473 | ARC1:Zone2 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10474 | ARC1:Zone2 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10475 | ARC1:Zone2 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10476 | ARC1:Zone2 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10477 | ARC1:Zone2 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10478 | ARC1:Zone2 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10479 | ARC1:Zone2 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10480 | ARC1:Zone2 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10481 | ARC1:Zone2 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10482 | ARC1:Zone2 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10483 | ARC1:Zone2 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10484 | ARC1:Zone2 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10485 | ARC1:Zone2 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10486 | ARC1:Zone2 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10487 | ARC1:Zone2 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10488 | ARC1:Zone2 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10489 | ARC1:Zone2 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10490 | ARC1:Zone2 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10491 | ARC1:Zone2 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10492 | ARC1:Zone2 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10493 | ARC1:Zone2 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10494 | ARC1:Zone2 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10495 | ARC1:Zone2 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10496 | ARC1:Zone2 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10497 | ARC1:Zone2 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10498 | ARC1:Zone2 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10499 | ARC1:Zone2 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10500 | ARC1:Zone2 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10501 | ARC1:Zone2 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10502 | ARC1:Zone2 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10503 | ARC1:Zone2 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10504 | ARC1:Zone2 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10505 | ARC1:Zone3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10506 | ARC1:Zone3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10507 | ARC1:Zone3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10508 | ARC1:Zone3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10509 | ARC1:Zone3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10510 | ARC1:Zone3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10511 | ARC1:Zone3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10512 | ARC1:Zone3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10513 | ARC1:Zone3 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10514 | ARC1:Zone3 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10515 | ARC1:Zone3 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10516 | ARC1:Zone3 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10517 | ARC1:Zone3 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10518 | ARC1:Zone3 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10519 | ARC1:Zone3 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10520 | ARC1:Zone3 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10521 | ARC1:Zone3 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10522 | ARC1:Zone3 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10523 | ARC1:Zone3 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10524 | ARC1:Zone3 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10525 | ARC1:Zone3 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10526 | ARC1:Zone3 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10527 | ARC1:Zone3 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10528 | ARC1:Zone3 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10529 | ARC1:Zone3 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10530 | ARC1:Zone3 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10531 | ARC1:Zone3 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10532 | ARC1:Zone3 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10533 | ARC1:Zone3 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10534 | ARC1:Zone3 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10535 | ARC1:Zone3 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10536 | ARC1:Zone3 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10537 | ARC1:Zone3 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10538 | ARC1:Zone3 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10539 | ARC1:Zone3 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10540 | ARC1:Zone3 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10541 | ARC1:Zone3 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10542 | ARC1:Zone3 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10543 | ARC1:Zone3 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10544 | ARC1:Zone3 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10545 | ARC1:Zone3 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10546 | ARC1:Zone3 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10547 | ARC1:Zone3 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10548 | ARC1:Zone3 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10549 | ARC1:Zone3 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10550 | ARC1:Zone3 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10551 | ARC1:Zone3 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10552 | ARC1:Zone3 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10553 | ARC1:Zone3 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10554 | ARC1:Zone3 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10555 | ARC1:Zone3 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10556 | ARC1:Zone3 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10557 | ARC1:Zone3 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10558 | ARC1:Zone3 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10559 | ARC1:Zone3 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10560 | ARC1:Zone3 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10561 | ARC1:Zone3 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10562 | ARC1:Zone3 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10563 | ARC1:Zone3 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10564 | ARC1:Zone3 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10565 | ARC1:Zone3 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10566 | ARC1:Zone3 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10567 | ARC1:Zone3 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10568 | ARC1:Zone3 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10569 | ARC1:Zone4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10570 | ARC1:Zone4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10571 | ARC1:Zone4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10572 | ARC1:Zone4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10573 | ARC1:Zone4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10574 | ARC1:Zone4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10575 | ARC1:Zone4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10576 | ARC1:Zone4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10577 | ARC1:Zone4 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10578 | ARC1:Zone4 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10579 | ARC1:Zone4 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10580 | ARC1:Zone4 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10581 | ARC1:Zone4 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10582 | ARC1:Zone4 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10583 | ARC1:Zone4 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10584 | ARC1:Zone4 Ph.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10585 | ARC1:Zone4 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10586 | ARC1:Zone4 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10587 | ARC1:Zone4 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10588 | ARC1:Zone4 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10589 | ARC1:Zone4 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10590 | ARC1:Zone4 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10591 | ARC1:Zone4 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10592 | ARC1:Zone4 Res.Curr Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10593 | ARC1:Zone4 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10594 | ARC1:Zone4 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10595 | ARC1:Zone4 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10596 | ARC1:Zone4 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10597 | ARC1:Zone4 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10598 | ARC1:Zone4 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10599 | ARC1:Zone4 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10600 | ARC1:Zone4 Light 1 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10601 | ARC1:Zone4 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10602 | ARC1:Zone4 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10603 | ARC1:Zone4 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10604 | ARC1:Zone4 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10605 | ARC1:Zone4 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10606 | ARC1:Zone4 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10607 | ARC1:Zone4 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10608 | ARC1:Zone4 Light 2 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10609 | ARC1:Zone4 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10610 | ARC1:Zone4 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10611 | ARC1:Zone4 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10612 | ARC1:Zone4 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10613 | ARC1:Zone4 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10614 | ARC1:Zone4 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10615 | ARC1:Zone4 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10616 | ARC1:Zone4 Light 3 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10617 | ARC1:Zone4 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10618 | ARC1:Zone4 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10619 | ARC1:Zone4 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10620 | ARC1:Zone4 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10621 | ARC1:Zone4 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10622 | ARC1:Zone4 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10623 | ARC1:Zone4 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10624 | ARC1:Zone4 Light 4 Enabled | R(W) | 1 | 0=Disabled;1=Enabled
10625 | ARC1:Zone4 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10626 | ARC1:Zone4 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10627 | ARC1:Zone4 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10628 | ARC1:Zone4 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10629 | ARC1:Zone4 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10630 | ARC1:Zone4 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10631 | ARC1:Zone4 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10632 | ARC1:Zone4 DI Enabled | R(W) | 1 | 0=Disabled;1=Light In;2=Current In
10633 | CTS1:CTS1 mode | R(W) | 1 | 0=Disabled;1=Activated
10634 | CTS2:CTS2 mode | R(W) | 1 | 0=Disabled;1=Activated
10635 | VTS1:VTS [60] mode | R(W) | 1 | 0=Disabled;1=Activated
10636 | FLX1:Fault locator [21FL] mode | R(W) | 1 | 0=Disabled;1=Activated
10637 | THD1:THD mode | R(W) | 1 | 0=Disabled;1=Activated
10638 | THDV1:THDV mode | R(W) | 1 | 0=Disabled;1=Activated
10639 | THDV1:THDV condition | R | 1 | 0=Normal;1=Start;2=Alarm;3=Blocked
10640 | CBW1:CBW mode | R(W) | 1 | 0=Disabled;1=Activated
10641 | NJK1:U0> RECL [79] mode | R(W) | 1 | 0=Disabled;1=Activated
10642 | SOF1:SOTF mode | R(W) | 1 | 0=Disabled;1=Activated
10643 | DOS1:Energy dose counter mode | R(W) | 1 | 0=Disabled;1=Activated
10644 | DOS2:Energy dose counter mode | R(W) | 1 | 0=Disabled;1=Activated
10645 | SYN1:SYN(1,2,3) [25] mode | R(W) | 1 | 0=Disabled;1=Activated
10646 | VJP1:Vector jump <DELTA><alpha> > [78] mode | R(W) | 1 | 0=Disabled;1=Activated
10647 | OBJS1:Phase-wise object mode | R(W) | 1 | 0=Disabled;1=Activated
10648 | OBJ1:Object1 mode | R(W) | 1 | 0=Disabled;1=Activated
10649 | OBJ2:Object2 mode | R(W) | 1 | 0=Disabled;1=Activated
10650 | OBJ3:Object3 mode | R(W) | 1 | 0=Disabled;1=Activated
10651 | OBJ4:Object4 mode | R(W) | 1 | 0=Disabled;1=Activated
10652 | OBJ5:Object5 mode | R(W) | 1 | 0=Disabled;1=Activated
10653 | OBJ6:Object6 mode | R(W) | 1 | 0=Disabled;1=Activated
10654 | OBJ7:Object7 mode | R(W) | 1 | 0=Disabled;1=Activated
10655 | OBJ8:Object8 mode | R(W) | 1 | 0=Disabled;1=Activated
10656 | OBJ9:Object9 mode | R(W) | 1 | 0=Disabled;1=Activated
10657 | OBJ10:Object10 mode | R(W) | 1 | 0=Disabled;1=Activated
10658 | CIN1:Indicator 1 mode | R(W) | 1 | 0=Disabled;1=Activated
10659 | CIN2:Indicator 2 mode | R(W) | 1 | 0=Disabled;1=Activated
10660 | CIN3:Indicator 3 mode | R(W) | 1 | 0=Disabled;1=Activated
10661 | CIN4:Indicator 4 mode | R(W) | 1 | 0=Disabled;1=Activated
10662 | CIN5:Indicator 5 mode | R(W) | 1 | 0=Disabled;1=Activated
10663 | CIN6:Indicator 6 mode | R(W) | 1 | 0=Disabled;1=Activated
10664 | CIN7:Indicator 7 mode | R(W) | 1 | 0=Disabled;1=Activated
10665 | CIN8:Indicator 8 mode | R(W) | 1 | 0=Disabled;1=Activated
10666 | CIN9:Indicator 9 mode | R(W) | 1 | 0=Disabled;1=Activated
10667 | CIN10:Indicator 10 mode | R(W) | 1 | 0=Disabled;1=Activated
10668 | CIN11:Indicator 11 mode | R(W) | 1 | 0=Disabled;1=Activated
10669 | CIN12:Indicator 12 mode | R(W) | 1 | 0=Disabled;1=Activated
10670 | CIN13:Indicator 13 mode | R(W) | 1 | 0=Disabled;1=Activated
10671 | CIN14:Indicator 14 mode | R(W) | 1 | 0=Disabled;1=Activated
10672 | CIN15:Indicator 15 mode | R(W) | 1 | 0=Disabled;1=Activated
10673 | CIN16:Indicator 16 mode | R(W) | 1 | 0=Disabled;1=Activated
10674 | CIN17:Indicator 17 mode | R(W) | 1 | 0=Disabled;1=Activated
10675 | CIN18:Indicator 18 mode | R(W) | 1 | 0=Disabled;1=Activated
10676 | CIN19:Indicator 19 mode | R(W) | 1 | 0=Disabled;1=Activated
10677 | CIN20:Indicator 20 mode | R(W) | 1 | 0=Disabled;1=Activated
10678 | AR1:Auto-recloser [79] mode | R(W) | 1 | 0=Disabled;1=Activated
10679 | VRG1:Vreg [AVR/90] mode | R(W) | 1 | 0=Disabled;1=Activated
10680 | EMON1:Monitor mode | R(W) | 1 | 0=Disabled;1=Activated
10681 | GMAG:Excitation control mode | R(W) | 1 | 0=Disabled;1=Activated
10682 | GSYN:DeadBus synchronizing | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
10683 |  |  |  | HR10682 (Lo-16bits)
10684 | GSYN:BlackStart synchronizing | R | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
10685 |  |  |  | HR10684 (Lo-16bits)
10686 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10687 |  |  |  | HR10686 (Lo-16bits)
10688 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10689 |  |  |  | HR10688 (Lo-16bits)
10690 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10691 |  |  |  | HR10690 (Lo-16bits)
10692 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10693 |  |  |  | HR10692 (Lo-16bits)
10694 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10695 |  |  |  | HR10694 (Lo-16bits)
10696 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10697 |  |  |  | HR10696 (Lo-16bits)
10698 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10699 |  |  |  | HR10698 (Lo-16bits)
10700 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10701 |  |  |  | HR10700 (Lo-16bits)
10702 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10703 |  |  |  | HR10702 (Lo-16bits)
10704 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10705 |  |  |  | HR10704 (Lo-16bits)
10706 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10707 |  |  |  | HR10706 (Lo-16bits)
10708 | VREC:Time | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
10709 |  |  |  | HR10708 (Lo-16bits)
10710 | VREC:ms | R | 1 | UINT32 [0...999]
10711 | VREC:ms | R | 1 | UINT32 [0...999]
10712 | VREC:ms | R | 1 | UINT32 [0...999]
10713 | VREC:ms | R | 1 | UINT32 [0...999]
10714 | VREC:ms | R | 1 | UINT32 [0...999]
10715 | VREC:ms | R | 1 | UINT32 [0...999]
10716 | VREC:ms | R | 1 | UINT32 [0...999]
10717 | VREC:ms | R | 1 | UINT32 [0...999]
10718 | VREC:ms | R | 1 | UINT32 [0...999]
10719 | VREC:ms | R | 1 | UINT32 [0...999]
10720 | VREC:ms | R | 1 | UINT32 [0...999]
10721 | VREC:ms | R | 1 | UINT32 [0...999]
10722 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10723 |  |  |  | HR10722 (Lo-16bits)
10724 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10725 |  |  |  | HR10724 (Lo-16bits)
10726 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10727 |  |  |  | HR10726 (Lo-16bits)
10728 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10729 |  |  |  | HR10728 (Lo-16bits)
10730 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10731 |  |  |  | HR10730 (Lo-16bits)
10732 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10733 |  |  |  | HR10732 (Lo-16bits)
10734 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10735 |  |  |  | HR10734 (Lo-16bits)
10736 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10737 |  |  |  | HR10736 (Lo-16bits)
10738 | DEV:Application package | R | 2 | STRING [...32] (Hi-16bits)
10739 |  |  |  | HR10738 (Lo-16bits)
10740 | EFX1:U0 (50Hz) pick-up setting | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
10741 |  |  |  | HR10740 (Lo-16bits)
10742 | EFX1:U0 (50Hz) pick-up setting | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
10743 |  |  |  | HR10742 (Lo-16bits)
10744 | EFX1:U0 (50Hz) pick-up setting | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
10745 |  |  |  | HR10744 (Lo-16bits)
10746 | EFX1:U0 (50Hz) pick-up setting | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
10747 |  |  |  | HR10746 (Lo-16bits)
10748 | EFX1:U0 (50Hz) pick-up setting | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
10749 |  |  |  | HR10748 (Lo-16bits)
10750 | EFX1:U0 (50Hz) pick-up setting | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
10751 |  |  |  | HR10750 (Lo-16bits)
10752 | EFX1:U0 (50Hz) pick-up setting | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
10753 |  |  |  | HR10752 (Lo-16bits)
10754 | EFX1:U0 (50Hz) pick-up setting | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
10755 |  |  |  | HR10754 (Lo-16bits)
10756 | EFX1:3I0 (5th harm.) pick-up setting [abs] | R(W) | 2 | FLOAT [0.05...1] (Hi-16bits)
10757 |  |  |  | HR10756 (Lo-16bits)
10758 | EFX1:3I0 (5th harm.) pick-up setting [abs] | R(W) | 2 | FLOAT [0.05...1] (Hi-16bits)
10759 |  |  |  | HR10758 (Lo-16bits)
10760 | EFX1:3I0 (5th harm.) pick-up setting [abs] | R(W) | 2 | FLOAT [0.05...1] (Hi-16bits)
10761 |  |  |  | HR10760 (Lo-16bits)
10762 | EFX1:3I0 (5th harm.) pick-up setting [abs] | R(W) | 2 | FLOAT [0.05...1] (Hi-16bits)
10763 |  |  |  | HR10762 (Lo-16bits)
10764 | EFX1:3I0 (5th harm.) pick-up setting [abs] | R(W) | 2 | FLOAT [0.05...1] (Hi-16bits)
10765 |  |  |  | HR10764 (Lo-16bits)
10766 | EFX1:3I0 (5th harm.) pick-up setting [abs] | R(W) | 2 | FLOAT [0.05...1] (Hi-16bits)
10767 |  |  |  | HR10766 (Lo-16bits)
10768 | EFX1:3I0 (5th harm.) pick-up setting [abs] | R(W) | 2 | FLOAT [0.05...1] (Hi-16bits)
10769 |  |  |  | HR10768 (Lo-16bits)
10770 | EFX1:3I0 (5th harm.) pick-up setting [abs] | R(W) | 2 | FLOAT [0.05...1] (Hi-16bits)
10771 |  |  |  | HR10770 (Lo-16bits)
10772 | EFX1:3I0 (5th harm.) angle range +/- setting | R(W) | 2 | FLOAT [10...45] (Hi-16bits)
10773 |  |  |  | HR10772 (Lo-16bits)
10774 | EFX1:3I0 (5th harm.) angle range +/- setting | R(W) | 2 | FLOAT [10...45] (Hi-16bits)
10775 |  |  |  | HR10774 (Lo-16bits)
10776 | EFX1:3I0 (5th harm.) angle range +/- setting | R(W) | 2 | FLOAT [10...45] (Hi-16bits)
10777 |  |  |  | HR10776 (Lo-16bits)
10778 | EFX1:3I0 (5th harm.) angle range +/- setting | R(W) | 2 | FLOAT [10...45] (Hi-16bits)
10779 |  |  |  | HR10778 (Lo-16bits)
10780 | EFX1:3I0 (5th harm.) angle range +/- setting | R(W) | 2 | FLOAT [10...45] (Hi-16bits)
10781 |  |  |  | HR10780 (Lo-16bits)
10782 | EFX1:3I0 (5th harm.) angle range +/- setting | R(W) | 2 | FLOAT [10...45] (Hi-16bits)
10783 |  |  |  | HR10782 (Lo-16bits)
10784 | EFX1:3I0 (5th harm.) angle range +/- setting | R(W) | 2 | FLOAT [10...45] (Hi-16bits)
10785 |  |  |  | HR10784 (Lo-16bits)
10786 | EFX1:3I0 (5th harm.) angle range +/- setting | R(W) | 2 | FLOAT [10...45] (Hi-16bits)
10787 |  |  |  | HR10786 (Lo-16bits)
10788 | EFX1:3I0 (5th harm.) angle center setting | R(W) | 2 | FLOAT [-90...90] (Hi-16bits)
10789 |  |  |  | HR10788 (Lo-16bits)
10790 | EFX1:3I0 (5th harm.) angle center setting | R(W) | 2 | FLOAT [-90...90] (Hi-16bits)
10791 |  |  |  | HR10790 (Lo-16bits)
10792 | EFX1:3I0 (5th harm.) angle center setting | R(W) | 2 | FLOAT [-90...90] (Hi-16bits)
10793 |  |  |  | HR10792 (Lo-16bits)
10794 | EFX1:3I0 (5th harm.) angle center setting | R(W) | 2 | FLOAT [-90...90] (Hi-16bits)
10795 |  |  |  | HR10794 (Lo-16bits)
10796 | EFX1:3I0 (5th harm.) angle center setting | R(W) | 2 | FLOAT [-90...90] (Hi-16bits)
10797 |  |  |  | HR10796 (Lo-16bits)
10798 | EFX1:3I0 (5th harm.) angle center setting | R(W) | 2 | FLOAT [-90...90] (Hi-16bits)
10799 |  |  |  | HR10798 (Lo-16bits)
10800 | EFX1:3I0 (5th harm.) angle center setting | R(W) | 2 | FLOAT [-90...90] (Hi-16bits)
10801 |  |  |  | HR10800 (Lo-16bits)
10802 | EFX1:3I0 (5th harm.) angle center setting | R(W) | 2 | FLOAT [-90...90] (Hi-16bits)
10803 |  |  |  | HR10802 (Lo-16bits)
10804 | CIN1:Indicator 1 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10805 | CIN1:Indicator 1 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10806 | CIN2:Indicator 2 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10807 | CIN2:Indicator 2 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10808 | CIN3:Indicator 3 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10809 | CIN3:Indicator 3 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10810 | CIN4:Indicator 4 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10811 | CIN4:Indicator 4 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10812 | CIN5:Indicator 5 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10813 | CIN5:Indicator 5 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10814 | CIN6:Indicator 6 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10815 | CIN6:Indicator 6 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10816 | CIN7:Indicator 7 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10817 | CIN7:Indicator 7 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10818 | CIN8:Indicator 8 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10819 | CIN8:Indicator 8 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10820 | CIN9:Indicator 9 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10821 | CIN9:Indicator 9 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10822 | CIN10:Indicator 10 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10823 | CIN10:Indicator 10 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10824 | CIN11:Indicator 11 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10825 | CIN11:Indicator 11 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10826 | CIN12:Indicator 12 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10827 | CIN12:Indicator 12 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10828 | CIN13:Indicator 13 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10829 | CIN13:Indicator 13 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10830 | CIN14:Indicator 14 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10831 | CIN14:Indicator 14 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10832 | CIN15:Indicator 15 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10833 | CIN15:Indicator 15 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10834 | CIN16:Indicator 16 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10835 | CIN16:Indicator 16 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10836 | CIN17:Indicator 17 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10837 | CIN17:Indicator 17 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10838 | CIN18:Indicator 18 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10839 | CIN18:Indicator 18 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10840 | CIN19:Indicator 19 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10841 | CIN19:Indicator 19 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10842 | CIN20:Indicator 20 status input | R(W) | 1 | 0=Signals;1=GooseDBPOS
10843 | CIN20:Indicator 20 status to display | R(W) | 1 | 0=GOOSE IN Switch 1;1=GOOSE IN Switch 2;2=GOOSE IN Switch 3;3=GOOSE IN Switch 4;4=GOOSE IN Switch 5;5=GOOSE IN Switch 6;6=GOOSE IN Switch 7;7=GOOSE IN Switch 8;8=GOOSE IN Switch 9;9=GOOSE IN Switch 10;10=GOOSE IN Switch 11;11=GOOSE IN Switch 12;12=GOOSE IN Switch 13;13=GOOSE IN Switch 14;14=GOOSE IN Switch 15;15=GOOSE IN Switch 16;16=GOOSE IN Switch 17;17=GOOSE IN Switch 18;18=GOOSE IN Switch 19;19=GOOSE IN Switch 20;20=GOOSE IN Switch 21;21=GOOSE IN Switch 22;22=GOOSE IN Switch 23;23=GOOSE IN Switch 24;24=GOOSE IN Switch 25;25=GOOSE IN Switch 26;26=GOOSE IN Switch 27;27=GOOSE IN Switch 28;28=GOOSE IN Switch 29;29=GOOSE IN Switch 30;30=GOOSE IN Switch 31;31=GOOSE IN Switch 32;32=GOOSE IN Switch 33;33=GOOSE IN Switch 34;34=GOOSE IN Switch 35;35=GOOSE IN Switch 36;36=GOOSE IN Switch 37;37=GOOSE IN Switch 38;38=GOOSE IN Switch 39;39=GOOSE IN Switch 40;40=GOOSE IN Switch 41;41=GOOSE IN Switch 42;42=GOOSE IN Switch 43;43=GOOSE IN Switch 44;44=GOOSE IN Switch 45;45=GOOSE IN Switch 46;46=GOOSE IN Switch 47;47=GOOSE IN Switch 48;48=GOOSE IN Switch 49;49=GOOSE IN Switch 50;50=GOOSE IN Switch 51;51=GOOSE IN Switch 52;52=GOOSE IN Switch 53;53=GOOSE IN Switch 54;54=GOOSE IN Switch 55;55=GOOSE IN Switch 56;56=GOOSE IN Switch 57;57=GOOSE IN Switch 58;58=GOOSE IN Switch 59;59=GOOSE IN Switch 60;60=GOOSE IN Switch 61;61=GOOSE IN Switch 62;62=GOOSE IN Switch 63;63=GOOSE IN Switch 64
10844 | PFC1:PFC> [55C] mode | R(W) | 1 | 0=Disabled;1=Activated
10845 | PFC1:PFC condition | R | 1 | 0=Normal;1=Discharging;2=Blocked;3=Switching interval;4=Starting
10846 | PFC1:Under voltage setting (more cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10847 |  |  |  | HR10846 (Lo-16bits)
10848 | PFC1:Under voltage setting (more cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10849 |  |  |  | HR10848 (Lo-16bits)
10850 | PFC1:Under voltage setting (more cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10851 |  |  |  | HR10850 (Lo-16bits)
10852 | PFC1:Under voltage setting (more cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10853 |  |  |  | HR10852 (Lo-16bits)
10854 | PFC1:Under voltage setting (more cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10855 |  |  |  | HR10854 (Lo-16bits)
10856 | PFC1:Under voltage setting (more cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10857 |  |  |  | HR10856 (Lo-16bits)
10858 | PFC1:Under voltage setting (more cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10859 |  |  |  | HR10858 (Lo-16bits)
10860 | PFC1:Under voltage setting (more cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10861 |  |  |  | HR10860 (Lo-16bits)
10862 | PFC1:Over voltage setting (less cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10863 |  |  |  | HR10862 (Lo-16bits)
10864 | PFC1:Over voltage setting (less cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10865 |  |  |  | HR10864 (Lo-16bits)
10866 | PFC1:Over voltage setting (less cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10867 |  |  |  | HR10866 (Lo-16bits)
10868 | PFC1:Over voltage setting (less cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10869 |  |  |  | HR10868 (Lo-16bits)
10870 | PFC1:Over voltage setting (less cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10871 |  |  |  | HR10870 (Lo-16bits)
10872 | PFC1:Over voltage setting (less cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10873 |  |  |  | HR10872 (Lo-16bits)
10874 | PFC1:Over voltage setting (less cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10875 |  |  |  | HR10874 (Lo-16bits)
10876 | PFC1:Over voltage setting (less cap.) | R(W) | 2 | FLOAT [70...130] (Hi-16bits)
10877 |  |  |  | HR10876 (Lo-16bits)
10878 | PFC1:Cos Pi set point (Cap+) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10879 |  |  |  | HR10878 (Lo-16bits)
10880 | PFC1:Cos Pi set point (Cap+) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10881 |  |  |  | HR10880 (Lo-16bits)
10882 | PFC1:Cos Pi set point (Cap+) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10883 |  |  |  | HR10882 (Lo-16bits)
10884 | PFC1:Cos Pi set point (Cap+) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10885 |  |  |  | HR10884 (Lo-16bits)
10886 | PFC1:Cos Pi set point (Cap+) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10887 |  |  |  | HR10886 (Lo-16bits)
10888 | PFC1:Cos Pi set point (Cap+) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10889 |  |  |  | HR10888 (Lo-16bits)
10890 | PFC1:Cos Pi set point (Cap+) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10891 |  |  |  | HR10890 (Lo-16bits)
10892 | PFC1:Cos Pi set point (Cap+) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10893 |  |  |  | HR10892 (Lo-16bits)
10894 | PFC1:Cos Pi set point (Cap-) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10895 |  |  |  | HR10894 (Lo-16bits)
10896 | PFC1:Cos Pi set point (Cap-) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10897 |  |  |  | HR10896 (Lo-16bits)
10898 | PFC1:Cos Pi set point (Cap-) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10899 |  |  |  | HR10898 (Lo-16bits)
10900 | PFC1:Cos Pi set point (Cap-) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10901 |  |  |  | HR10900 (Lo-16bits)
10902 | PFC1:Cos Pi set point (Cap-) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10903 |  |  |  | HR10902 (Lo-16bits)
10904 | PFC1:Cos Pi set point (Cap-) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10905 |  |  |  | HR10904 (Lo-16bits)
10906 | PFC1:Cos Pi set point (Cap-) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10907 |  |  |  | HR10906 (Lo-16bits)
10908 | PFC1:Cos Pi set point (Cap-) | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
10909 |  |  |  | HR10908 (Lo-16bits)
10910 | PFC1:More capacitance +kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10911 |  |  |  | HR10910 (Lo-16bits)
10912 | PFC1:More capacitance +kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10913 |  |  |  | HR10912 (Lo-16bits)
10914 | PFC1:More capacitance +kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10915 |  |  |  | HR10914 (Lo-16bits)
10916 | PFC1:More capacitance +kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10917 |  |  |  | HR10916 (Lo-16bits)
10918 | PFC1:More capacitance +kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10919 |  |  |  | HR10918 (Lo-16bits)
10920 | PFC1:More capacitance +kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10921 |  |  |  | HR10920 (Lo-16bits)
10922 | PFC1:More capacitance +kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10923 |  |  |  | HR10922 (Lo-16bits)
10924 | PFC1:More capacitance +kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10925 |  |  |  | HR10924 (Lo-16bits)
10926 | PFC1:Less capacitance -kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10927 |  |  |  | HR10926 (Lo-16bits)
10928 | PFC1:Less capacitance -kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10929 |  |  |  | HR10928 (Lo-16bits)
10930 | PFC1:Less capacitance -kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10931 |  |  |  | HR10930 (Lo-16bits)
10932 | PFC1:Less capacitance -kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10933 |  |  |  | HR10932 (Lo-16bits)
10934 | PFC1:Less capacitance -kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10935 |  |  |  | HR10934 (Lo-16bits)
10936 | PFC1:Less capacitance -kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10937 |  |  |  | HR10936 (Lo-16bits)
10938 | PFC1:Less capacitance -kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10939 |  |  |  | HR10938 (Lo-16bits)
10940 | PFC1:Less capacitance -kVAr threshold | R(W) | 2 | FLOAT [-50000...50000] (Hi-16bits)
10941 |  |  |  | HR10940 (Lo-16bits)
10942 | PFC1:Minimum current block limit | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10943 |  |  |  | HR10942 (Lo-16bits)
10944 | PFC1:Minimum current block limit | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10945 |  |  |  | HR10944 (Lo-16bits)
10946 | PFC1:Minimum current block limit | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10947 |  |  |  | HR10946 (Lo-16bits)
10948 | PFC1:Minimum current block limit | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10949 |  |  |  | HR10948 (Lo-16bits)
10950 | PFC1:Minimum current block limit | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10951 |  |  |  | HR10950 (Lo-16bits)
10952 | PFC1:Minimum current block limit | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10953 |  |  |  | HR10952 (Lo-16bits)
10954 | PFC1:Minimum current block limit | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10955 |  |  |  | HR10954 (Lo-16bits)
10956 | PFC1:Minimum current block limit | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
10957 |  |  |  | HR10956 (Lo-16bits)
10958 | PFC1:Minimum voltage block limit | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
10959 |  |  |  | HR10958 (Lo-16bits)
10960 | PFC1:Minimum voltage block limit | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
10961 |  |  |  | HR10960 (Lo-16bits)
10962 | PFC1:Minimum voltage block limit | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
10963 |  |  |  | HR10962 (Lo-16bits)
10964 | PFC1:Minimum voltage block limit | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
10965 |  |  |  | HR10964 (Lo-16bits)
10966 | PFC1:Minimum voltage block limit | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
10967 |  |  |  | HR10966 (Lo-16bits)
10968 | PFC1:Minimum voltage block limit | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
10969 |  |  |  | HR10968 (Lo-16bits)
10970 | PFC1:Minimum voltage block limit | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
10971 |  |  |  | HR10970 (Lo-16bits)
10972 | PFC1:Minimum voltage block limit | R(W) | 2 | FLOAT [0...50] (Hi-16bits)
10973 |  |  |  | HR10972 (Lo-16bits)
10974 | PFC1:Bank control starting delay | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10975 |  |  |  | HR10974 (Lo-16bits)
10976 | PFC1:Bank control starting delay | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10977 |  |  |  | HR10976 (Lo-16bits)
10978 | PFC1:Bank control starting delay | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10979 |  |  |  | HR10978 (Lo-16bits)
10980 | PFC1:Bank control starting delay | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10981 |  |  |  | HR10980 (Lo-16bits)
10982 | PFC1:Bank control starting delay | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10983 |  |  |  | HR10982 (Lo-16bits)
10984 | PFC1:Bank control starting delay | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10985 |  |  |  | HR10984 (Lo-16bits)
10986 | PFC1:Bank control starting delay | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10987 |  |  |  | HR10986 (Lo-16bits)
10988 | PFC1:Bank control starting delay | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10989 |  |  |  | HR10988 (Lo-16bits)
10990 | PFC1:Fast bank recontrol in use | R(W) | 1 | 0=No;1=Yes
10991 | PFC1:Fast bank recontrol in use | R(W) | 1 | 0=No;1=Yes
10992 | PFC1:Fast bank recontrol in use | R(W) | 1 | 0=No;1=Yes
10993 | PFC1:Fast bank recontrol in use | R(W) | 1 | 0=No;1=Yes
10994 | PFC1:Fast bank recontrol in use | R(W) | 1 | 0=No;1=Yes
10995 | PFC1:Fast bank recontrol in use | R(W) | 1 | 0=No;1=Yes
10996 | PFC1:Fast bank recontrol in use | R(W) | 1 | 0=No;1=Yes
10997 | PFC1:Fast bank recontrol in use | R(W) | 1 | 0=No;1=Yes
10998 | PFC1:Switch interval time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
10999 |  |  |  | HR10998 (Lo-16bits)
11000 | PFC1:Switch interval time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11001 |  |  |  | HR11000 (Lo-16bits)
11002 | PFC1:Switch interval time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11003 |  |  |  | HR11002 (Lo-16bits)
11004 | PFC1:Switch interval time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11005 |  |  |  | HR11004 (Lo-16bits)
11006 | PFC1:Switch interval time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11007 |  |  |  | HR11006 (Lo-16bits)
11008 | PFC1:Switch interval time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11009 |  |  |  | HR11008 (Lo-16bits)
11010 | PFC1:Switch interval time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11011 |  |  |  | HR11010 (Lo-16bits)
11012 | PFC1:Switch interval time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11013 |  |  |  | HR11012 (Lo-16bits)
11014 | PFC1:Discharge time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11015 |  |  |  | HR11014 (Lo-16bits)
11016 | PFC1:Discharge time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11017 |  |  |  | HR11016 (Lo-16bits)
11018 | PFC1:Discharge time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11019 |  |  |  | HR11018 (Lo-16bits)
11020 | PFC1:Discharge time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11021 |  |  |  | HR11020 (Lo-16bits)
11022 | PFC1:Discharge time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11023 |  |  |  | HR11022 (Lo-16bits)
11024 | PFC1:Discharge time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11025 |  |  |  | HR11024 (Lo-16bits)
11026 | PFC1:Discharge time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11027 |  |  |  | HR11026 (Lo-16bits)
11028 | PFC1:Discharge time | R(W) | 2 | FLOAT [1...1800] (Hi-16bits)
11029 |  |  |  | HR11028 (Lo-16bits)
11030 | VRG1:Circulating current (A) | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11031 |  |  |  | HR11030 (Lo-16bits)
11032 | VRG1:Circulating current deviation (%Un) | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11033 |  |  |  | HR11032 (Lo-16bits)
11034 | VRG1:Voltage deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11035 |  |  |  | HR11034 (Lo-16bits)
11036 | VRG1:Total deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11037 |  |  |  | HR11036 (Lo-16bits)
11038 | VRG1:Tap voltage (kV) | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11039 |  |  |  | HR11038 (Lo-16bits)
11040 | VRG1:Voltage difference (kV) | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11041 |  |  |  | HR11040 (Lo-16bits)
11042 | VRG1:Absolute tap location (parallel engine) | R | 2 | FLOAT [0...50] (Hi-16bits)
11043 |  |  |  | HR11042 (Lo-16bits)
11044 | VRG1:AVR T1 tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11045 |  |  |  | HR11044 (Lo-16bits)
11046 | VRG1:AVR T2 tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11047 |  |  |  | HR11046 (Lo-16bits)
11048 | VRG1:AVR T3 tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11049 |  |  |  | HR11048 (Lo-16bits)
11050 | VRG1:AVR T4 tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11051 |  |  |  | HR11050 (Lo-16bits)
11052 | VRG1:AVR T1 voltage deviation | R | 2 | FLOAT [-100...140] (Hi-16bits)
11053 |  |  |  | HR11052 (Lo-16bits)
11054 | VRG1:AVR T2 voltage deviation | R | 2 | FLOAT [-100...140] (Hi-16bits)
11055 |  |  |  | HR11054 (Lo-16bits)
11056 | VRG1:AVR T3 voltage deviation | R | 2 | FLOAT [-100...140] (Hi-16bits)
11057 |  |  |  | HR11056 (Lo-16bits)
11058 | VRG1:AVR T4 voltage deviation | R | 2 | FLOAT [-100...140] (Hi-16bits)
11059 |  |  |  | HR11058 (Lo-16bits)
11060 | VRG1:AVR T1 circulating current deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11061 |  |  |  | HR11060 (Lo-16bits)
11062 | VRG1:AVR T2 circulating current deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11063 |  |  |  | HR11062 (Lo-16bits)
11064 | VRG1:AVR T3 circulating current deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11065 |  |  |  | HR11064 (Lo-16bits)
11066 | VRG1:AVR T4 circulating current deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11067 |  |  |  | HR11066 (Lo-16bits)
11068 | VRG1:AVR T1 total deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11069 |  |  |  | HR11068 (Lo-16bits)
11070 | VRG1:AVR T2 total deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11071 |  |  |  | HR11070 (Lo-16bits)
11072 | VRG1:AVR T3 total deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11073 |  |  |  | HR11072 (Lo-16bits)
11074 | VRG1:AVR T4 total deviation | R | 2 | FLOAT [-50000...50000] (Hi-16bits)
11075 |  |  |  | HR11074 (Lo-16bits)
11076 | VRG1:AVR T1 Auto/Manual | R | 1 | 0=Automatic;1=Manual
11077 | VRG1:AVR T2 Auto/Manual | R | 1 | 0=Automatic;1=Manual
11078 | VRG1:AVR 3 Auto/Manual | R | 1 | 0=Automatic;1=Manual
11079 | VRG1:AVR T4 Auto/Manual | R | 1 | 0=Automatic;1=Manual
11080 | VRG1:AVR T1 Independent/Parallel | R | 1 | 0=Single;1=Parallel
11081 | VRG1:AVR T2 Independent/Parallel | R | 1 | 0=Single;1=Parallel
11082 | VRG1:AVR T3 Independent/Parallel | R | 1 | 0=Single;1=Parallel
11083 | VRG1:AVR T4 Independent/Parallel | R | 1 | 0=Single;1=Parallel
11084 | VRG1:U>/< T2 fast recontrol delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
11085 |  |  |  | HR11084 (Lo-16bits)
11086 | VRG1:U>/< T2 fast recontrol delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
11087 |  |  |  | HR11086 (Lo-16bits)
11088 | VRG1:U>/< T2 fast recontrol delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
11089 |  |  |  | HR11088 (Lo-16bits)
11090 | VRG1:U>/< T2 fast recontrol delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
11091 |  |  |  | HR11090 (Lo-16bits)
11092 | VRG1:U>/< T2 fast recontrol delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
11093 |  |  |  | HR11092 (Lo-16bits)
11094 | VRG1:U>/< T2 fast recontrol delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
11095 |  |  |  | HR11094 (Lo-16bits)
11096 | VRG1:U>/< T2 fast recontrol delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
11097 |  |  |  | HR11096 (Lo-16bits)
11098 | VRG1:U>/< T2 fast recontrol delay (DT) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
11099 |  |  |  | HR11098 (Lo-16bits)
11100 | AOUT2:mA In (T card) 1 mA In 1 | R | 2 | FLOAT [0...24] (Hi-16bits)
11101 |  |  |  | HR11100 (Lo-16bits)
11102 | AOUT2:mA In (T card) 1 mA In 2 | R | 2 | FLOAT [0...24] (Hi-16bits)
11103 |  |  |  | HR11102 (Lo-16bits)
11104 | AOUT2:mA In (T card) 1 mA In 3 | R | 2 | FLOAT [0...24] (Hi-16bits)
11105 |  |  |  | HR11104 (Lo-16bits)
11106 | AOUT2:mA In (T card) 1 mA In 4 | R | 2 | FLOAT [0...24] (Hi-16bits)
11107 |  |  |  | HR11106 (Lo-16bits)
11108 | AOUT2:mA In (T card) 2 mA In 1 | R | 2 | FLOAT [0...24] (Hi-16bits)
11109 |  |  |  | HR11108 (Lo-16bits)
11110 | AOUT2:mA In (T card) 2 mA In 2 | R | 2 | FLOAT [0...24] (Hi-16bits)
11111 |  |  |  | HR11110 (Lo-16bits)
11112 | AOUT2:mA In (T card) 2 mA In 3 | R | 2 | FLOAT [0...24] (Hi-16bits)
11113 |  |  |  | HR11112 (Lo-16bits)
11114 | AOUT2:mA In (T card) 2 mA In 4 | R | 2 | FLOAT [0...24] (Hi-16bits)
11115 |  |  |  | HR11114 (Lo-16bits)
11116 | AOUT2:mA Out Channel 1 Input Magnitude now (T option 1) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
11117 |  |  |  | HR11116 (Lo-16bits)
11118 | AOUT2:mA Out Channel 1 Outputs now (T option 1) | R | 2 | FLOAT [0...24] (Hi-16bits)
11119 |  |  |  | HR11118 (Lo-16bits)
11120 | AOUT2:mA Out Channel 2 Input Magnitude now (T option 2) | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
11121 |  |  |  | HR11120 (Lo-16bits)
11122 | AOUT2:mA Out Channel 2 Outputs now (T option 2) | R | 2 | FLOAT [0...24] (Hi-16bits)
11123 |  |  |  | HR11122 (Lo-16bits)
11124 | VRG1:AVR tap control status | R | 1 | 0=OK;1=Tap control failure
11125 | VRG1:AVR Parallel/Independent status to mimic | R | 1 | 0=Parallel;1=Independent
11126 | VRG1:AVR Follower&Master status to mimic | R | 1 | 0=Follower;1=Master
11127 | VRG1:AVR/block: Parallel communication failure | R | 1 | 0=Communication OK;1=Communication failure
11128 | VRG1:AVR/block: Tap differential failure | R | 1 | 0=Tap OK;1=Tap difference failure
11129 | VRG1:Hierarchy status to mimic | R | 1 | 0=Master & follower;1=Circulating reactive current
11130 | VRG1:Auto/Manual status to mimic | R | 1 | 0=Auto;1=Manual
11131 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11132 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11133 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11134 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11135 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11136 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11137 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11138 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11139 | VRG1:Relay in test mode | R | 1 | 1=On;2=Blocked;3=Test;4=Test/Blocked;5=Off
11140 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11141 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11142 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11143 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11144 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11145 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11146 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11147 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11148 | VRG1:Maximum tap raise position | R | 1 | 0=OK;1=Max. position
11149 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11150 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11151 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11152 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11153 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11154 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11155 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11156 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11157 | VRG1:Minimum tap lower position | R | 1 | 0=OK;1=Min. position
11158 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11159 |  |  |  | HR11158 (Lo-16bits)
11160 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11161 |  |  |  | HR11160 (Lo-16bits)
11162 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11163 |  |  |  | HR11162 (Lo-16bits)
11164 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11165 |  |  |  | HR11164 (Lo-16bits)
11166 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11167 |  |  |  | HR11166 (Lo-16bits)
11168 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11169 |  |  |  | HR11168 (Lo-16bits)
11170 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11171 |  |  |  | HR11170 (Lo-16bits)
11172 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11173 |  |  |  | HR11172 (Lo-16bits)
11174 | VRG1:Command with feedback (Tap position) | R | 2 | FLOAT [-30...30] (Hi-16bits)
11175 |  |  |  | HR11174 (Lo-16bits)
11176 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11177 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11178 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11179 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11180 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11181 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11182 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11183 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11184 | VRG1:Health | R | 1 | 0=Ok;1=Fail
11185 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11186 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11187 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11188 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11189 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11190 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11191 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11192 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11193 | VRG1:Automatic local block | R | 1 | 0=Normal;1=Blocked
11194 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11195 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11196 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11197 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11198 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11199 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11200 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11201 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11202 | VRG1:Operating Mode (Auto) | R | 1 | 0=Automatic;1=Manual
11203 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11204 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11205 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11206 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11207 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11208 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11209 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11210 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11211 | VRG1:Parallel operation | R | 1 | 0=Single;1=Parallel
11212 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11213 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11214 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11215 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11216 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11217 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11218 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11219 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11220 | VRG1:Status | R | 1 | 0=Follower;1=Leader
11221 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11222 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11223 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11224 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11225 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11226 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11227 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11228 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11229 | VRG1:Operation hierarchy | R | 1 | 0=Leader & follower;1=Circulating reactive current
11230 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11231 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11232 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11233 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11234 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11235 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11236 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11237 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11238 | VRG1:Parallel group | R | 1 | 0=NA;1=1;2=2;3=3;4=4
11239 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11240 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11241 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11242 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11243 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11244 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11245 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11246 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11247 | VRG1:Local parallel transformer ID | R | 1 | 0=NA;1=1;2=2;3=3;4=4;5=5;6=6;7=7;8=8;9=9
11248 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11249 |  |  |  | HR11248 (Lo-16bits)
11250 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11251 |  |  |  | HR11250 (Lo-16bits)
11252 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11253 |  |  |  | HR11252 (Lo-16bits)
11254 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11255 |  |  |  | HR11254 (Lo-16bits)
11256 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11257 |  |  |  | HR11256 (Lo-16bits)
11258 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11259 |  |  |  | HR11258 (Lo-16bits)
11260 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11261 |  |  |  | HR11260 (Lo-16bits)
11262 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11263 |  |  |  | HR11262 (Lo-16bits)
11264 | VRG1:Tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11265 |  |  |  | HR11264 (Lo-16bits)
11266 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11267 |  |  |  | HR11266 (Lo-16bits)
11268 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11269 |  |  |  | HR11268 (Lo-16bits)
11270 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11271 |  |  |  | HR11270 (Lo-16bits)
11272 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11273 |  |  |  | HR11272 (Lo-16bits)
11274 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11275 |  |  |  | HR11274 (Lo-16bits)
11276 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11277 |  |  |  | HR11276 (Lo-16bits)
11278 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11279 |  |  |  | HR11278 (Lo-16bits)
11280 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11281 |  |  |  | HR11280 (Lo-16bits)
11282 | VRG1:Local reactance X1 | R | 2 | FLOAT [0...500] (Hi-16bits)
11283 |  |  |  | HR11282 (Lo-16bits)
11284 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11285 |  |  |  | HR11284 (Lo-16bits)
11286 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11287 |  |  |  | HR11286 (Lo-16bits)
11288 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11289 |  |  |  | HR11288 (Lo-16bits)
11290 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11291 |  |  |  | HR11290 (Lo-16bits)
11292 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11293 |  |  |  | HR11292 (Lo-16bits)
11294 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11295 |  |  |  | HR11294 (Lo-16bits)
11296 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11297 |  |  |  | HR11296 (Lo-16bits)
11298 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11299 |  |  |  | HR11298 (Lo-16bits)
11300 | VRG1:Local load current I1 | R | 2 | FLOAT [0...1250] (Hi-16bits)
11301 |  |  |  | HR11300 (Lo-16bits)
11302 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11303 |  |  |  | HR11302 (Lo-16bits)
11304 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11305 |  |  |  | HR11304 (Lo-16bits)
11306 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11307 |  |  |  | HR11306 (Lo-16bits)
11308 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11309 |  |  |  | HR11308 (Lo-16bits)
11310 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11311 |  |  |  | HR11310 (Lo-16bits)
11312 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11313 |  |  |  | HR11312 (Lo-16bits)
11314 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11315 |  |  |  | HR11314 (Lo-16bits)
11316 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11317 |  |  |  | HR11316 (Lo-16bits)
11318 | VRG1:Local load current I1 angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
11319 |  |  |  | HR11318 (Lo-16bits)
11320 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11321 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11322 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11323 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11324 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11325 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11326 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11327 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11328 | VRG1:Leader command | R | 1 | 0=Normal;1=Lower;2=Raise
11329 | VRG1:ParallelTransfModeKind | R | 1 | 1=No Mode predifined;2=Master;3=Follower;4=Power Factor;5=Negative Reactance;6=Circulating Current;7=Circulating Reactive Current (var balancing);8=Circulating Reactive Current by equalizing power
11330 | COL1:ICOL> [49OL] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
11331 | COL2:ICOL>> [49OL] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
11332 | CNU1:CNU> [50UB] condition | R | 1 | 0=Normal;1=Alarm Start;2=Alarm On;3=Trip Start;4=Trip On;5=Blocked On
11333 | ASC1:Curve5 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11334 |  |  |  | HR11333 (Lo-16bits)
11335 | ASC1:Curve5 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11336 |  |  |  | HR11335 (Lo-16bits)
11337 | ASC1:Curve6 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11338 |  |  |  | HR11337 (Lo-16bits)
11339 | ASC1:Curve6 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11340 |  |  |  | HR11339 (Lo-16bits)
11341 | ASC1:Curve7 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11342 |  |  |  | HR11341 (Lo-16bits)
11343 | ASC1:Curve7 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11344 |  |  |  | HR11343 (Lo-16bits)
11345 | ASC1:Curve8 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11346 |  |  |  | HR11345 (Lo-16bits)
11347 | ASC1:Curve8 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11348 |  |  |  | HR11347 (Lo-16bits)
11349 | ASC1:Curve9 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11350 |  |  |  | HR11349 (Lo-16bits)
11351 | ASC1:Curve9 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11352 |  |  |  | HR11351 (Lo-16bits)
11353 | ASC1:Curve10 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11354 |  |  |  | HR11353 (Lo-16bits)
11355 | ASC1:Curve10 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
11356 |  |  |  | HR11355 (Lo-16bits)
11357 | TOLM1:TM> inhibit status | R | 1 | 0=Normal;1=Inhibit
11358 | LDIF1:L1 Bias current | R | 2 | FLOAT [0...50] (Hi-16bits)
11359 |  |  |  | HR11358 (Lo-16bits)
11360 | LDIF1:L1 Diff current | R | 2 | FLOAT [0...4000] (Hi-16bits)
11361 |  |  |  | HR11360 (Lo-16bits)
11362 | LDIF1:L1 Char current | R | 2 | FLOAT [0...4000] (Hi-16bits)
11363 |  |  |  | HR11362 (Lo-16bits)
11364 | LDIF1:L2 Bias current | R | 2 | FLOAT [0...50] (Hi-16bits)
11365 |  |  |  | HR11364 (Lo-16bits)
11366 | LDIF1:L2 Diff current | R | 2 | FLOAT [0...4000] (Hi-16bits)
11367 |  |  |  | HR11366 (Lo-16bits)
11368 | LDIF1:L2 Char current | R | 2 | FLOAT [0...4000] (Hi-16bits)
11369 |  |  |  | HR11368 (Lo-16bits)
11370 | LDIF1:L3 Bias current | R | 2 | FLOAT [0...50] (Hi-16bits)
11371 |  |  |  | HR11370 (Lo-16bits)
11372 | LDIF1:L3 Diff current | R | 2 | FLOAT [0...4000] (Hi-16bits)
11373 |  |  |  | HR11372 (Lo-16bits)
11374 | LDIF1:L3 Char current | R | 2 | FLOAT [0...4000] (Hi-16bits)
11375 |  |  |  | HR11374 (Lo-16bits)
11376 | LDIF1:IL1 magnitude Local | R | 2 | FLOAT [0...50] (Hi-16bits)
11377 |  |  |  | HR11376 (Lo-16bits)
11378 | LDIF1:IL2 magnitude Local | R | 2 | FLOAT [0...50] (Hi-16bits)
11379 |  |  |  | HR11378 (Lo-16bits)
11380 | LDIF1:IL3 magnitude Local | R | 2 | FLOAT [0...50] (Hi-16bits)
11381 |  |  |  | HR11380 (Lo-16bits)
11382 | LDIF1:IL1 angle Local | R | 2 | FLOAT [-360...360] (Hi-16bits)
11383 |  |  |  | HR11382 (Lo-16bits)
11384 | LDIF1:IL2 angle Local | R | 2 | FLOAT [-360...360] (Hi-16bits)
11385 |  |  |  | HR11384 (Lo-16bits)
11386 | LDIF1:IL3 angle Local | R | 2 | FLOAT [-360...360] (Hi-16bits)
11387 |  |  |  | HR11386 (Lo-16bits)
11388 | LDIF1:IL1 magnitude Remote1 | R | 2 | FLOAT [0...50] (Hi-16bits)
11389 |  |  |  | HR11388 (Lo-16bits)
11390 | LDIF1:IL2 magnitude Remote1 | R | 2 | FLOAT [0...50] (Hi-16bits)
11391 |  |  |  | HR11390 (Lo-16bits)
11392 | LDIF1:IL3 magnitude Remote1 | R | 2 | FLOAT [0...50] (Hi-16bits)
11393 |  |  |  | HR11392 (Lo-16bits)
11394 | LDIF1:IL1 angle Remote1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
11395 |  |  |  | HR11394 (Lo-16bits)
11396 | LDIF1:IL2 angle Remote1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
11397 |  |  |  | HR11396 (Lo-16bits)
11398 | LDIF1:IL3 angle Remote1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
11399 |  |  |  | HR11398 (Lo-16bits)
11400 | LDIF1:IL1 magnitude difference to Remote1 | R | 2 | FLOAT [0...50] (Hi-16bits)
11401 |  |  |  | HR11400 (Lo-16bits)
11402 | LDIF1:IL2 magnitude difference to Remote1 | R | 2 | FLOAT [0...50] (Hi-16bits)
11403 |  |  |  | HR11402 (Lo-16bits)
11404 | LDIF1:IL3 magnitude difference to Remote1 | R | 2 | FLOAT [0...50] (Hi-16bits)
11405 |  |  |  | HR11404 (Lo-16bits)
11406 | LDIF1:IL1 angle difference to Remote1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
11407 |  |  |  | HR11406 (Lo-16bits)
11408 | LDIF1:IL2 angle difference to Remote1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
11409 |  |  |  | HR11408 (Lo-16bits)
11410 | LDIF1:IL3 angle difference to Remote1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
11411 |  |  |  | HR11410 (Lo-16bits)
11412 | LDIF1:Remote signals angle corrected | R | 2 | FLOAT [-360...360] (Hi-16bits)
11413 |  |  |  | HR11412 (Lo-16bits)
11414 | LDIF1:Operating Mode | R | 1 | 0=Following Master Settings
11415 | LDIF1:Differential calculation mode | R | 1 | 0=Subtract;1=Add
11416 | LDIF1:Bias calculation mode | R | 1 | 0=Average;1=Maximum
11417 | LDIF1:Idb> Pickup | R | 2 | FLOAT [0.01...100] (Hi-16bits)
11418 |  |  |  | HR11417 (Lo-16bits)
11419 | LDIF1:Idb> Turnpoint 1 | R | 2 | FLOAT [0.01...50] (Hi-16bits)
11420 |  |  |  | HR11419 (Lo-16bits)
11421 | LDIF1:Idb> Slope 1 | R | 2 | FLOAT [0.01...250] (Hi-16bits)
11422 |  |  |  | HR11421 (Lo-16bits)
11423 | LDIF1:Idb> Turnpoint 2 | R | 2 | FLOAT [0.01...50] (Hi-16bits)
11424 |  |  |  | HR11423 (Lo-16bits)
11425 | LDIF1:Idb> Slope 2 | R | 2 | FLOAT [0.01...250] (Hi-16bits)
11426 |  |  |  | HR11425 (Lo-16bits)
11427 | LDIF1:Enable harmonic blocking | R | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
11428 | LDIF1:2nd harm block Pickup | R | 2 | FLOAT [0.01...50] (Hi-16bits)
11429 |  |  |  | HR11428 (Lo-16bits)
11430 | LDIF1:5th harm block Pickup | R | 2 | FLOAT [0.01...50] (Hi-16bits)
11431 |  |  |  | HR11430 (Lo-16bits)
11432 | LDIF1:Enable Idi> stage (nonbias) | R | 1 | 0=Disabled;1=Enabled
11433 | LDIF1:Idi> No bias Pickup | R | 2 | FLOAT [200...1500] (Hi-16bits)
11434 |  |  |  | HR11433 (Lo-16bits)
11435 | LDIF1:IdLb> BIAS TRIP | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11436 |  |  |  | HR11435 (Lo-16bits)
11437 | LDIF1:IdLb> BIAS BLOCKED | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11438 |  |  |  | HR11437 (Lo-16bits)
11439 | LDIF1:IdLi> NOBIAS TRIP | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11440 |  |  |  | HR11439 (Lo-16bits)
11441 | LDIF1:IdLi> NOBIAS BLOCKED | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11442 |  |  |  | HR11441 (Lo-16bits)
11443 | LDIF1:IdL> 2nd harm. block on | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11444 |  |  |  | HR11443 (Lo-16bits)
11445 | LDIF1:IdL> 5th harm. block on | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11446 |  |  |  | HR11445 (Lo-16bits)
11447 | LDIF1:Master node status | R | 2 | 0b=Master node;1b=System Running;2b=Protection Operational;3b=System rebooting;4b=Configuring, Id> suspended;5b=Biased diff blocked;6b=Instant diff blocked;7b=Phase A harm blk.;8b=Phase B harm blk.;9b=Phase C harm blk.;10b=LineDiff Enabled;11b=LineDiff Halted;12b=Bias Trip;13b=Instant Trip;14b=Remote1 halted;15b=Communication Ok;16b=Communication fail;17b=Object1 Open;18b=Object1 Closed;19b=Obj1 Open Cmd.;20b=Obj1 Close Cmd.;21b=Sub sampling f control (Hi-16bits)
11448 |  |  |  | HR11447 (Lo-16bits)
11449 | LDIF1:Local node status | R | 2 | 0b=Master node;1b=System Running;2b=Protection Operational;3b=System rebooting;4b=Configuring, Id> suspended;5b=Biased diff blocked;6b=Instant diff blocked;7b=Phase A harm blk.;8b=Phase B harm blk.;9b=Phase C harm blk.;10b=LineDiff Enabled;11b=LineDiff Halted;12b=Bias Trip;13b=Instant Trip;14b=Remote1 halted;15b=Communication Ok;16b=Communication fail;17b=Object1 Open;18b=Object1 Closed;19b=Obj1 Open Cmd.;20b=Obj1 Close Cmd.;21b=f sample follows master (Hi-16bits)
11450 |  |  |  | HR11449 (Lo-16bits)
11451 | LDIF1:Remote node 1 status | R | 2 | 0b=Master node;1b=System Running;2b=Protection Operational;3b=System rebooting;4b=Configuring, Id> suspended;5b=Biased diff blocked;6b=Instant diff blocked;7b=Phase A harm blk.;8b=Phase B harm blk.;9b=Phase C harm blk.;10b=LineDiff Enabled;11b=LineDiff Halted;12b=Bias Trip;13b=Instant Trip;14b=Remote1 halted;15b=Communication Ok;16b=Communication fail;17b=Object1 Open;18b=Object1 Closed;19b=Obj1 Open Cmd.;20b=Obj1 Close Cmd.;21b=f sample follows master (Hi-16bits)
11452 |  |  |  | HR11451 (Lo-16bits)
11453 | SYN1:SYN2 Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
11454 |  |  |  | HR11453 (Lo-16bits)
11455 | SYN1:SYN2 Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
11456 |  |  |  | HR11455 (Lo-16bits)
11457 | SYN1:SYN2 Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
11458 |  |  |  | HR11457 (Lo-16bits)
11459 | SYN1:SYN3 Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
11460 |  |  |  | HR11459 (Lo-16bits)
11461 | SYN1:SYN3 Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
11462 |  |  |  | HR11461 (Lo-16bits)
11463 | SYN1:SYN3 Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
11464 |  |  |  | HR11463 (Lo-16bits)
11465 | DMA1:Demand condition | R | 1 | 0=Normal;1=General alarm;2=Blocked
11466 | CTRL:Local/Remote status | R | 1 | 0=Remote;1=Local
11467 | TOLT1:TT> inhibit status | R | 1 | 0=Normal;1=Inhibit
11468 | TOLF1:TF> inhibit status | R | 1 | 0=Normal;1=Inhibit
11469 | OBJ1:Object1 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11470 | OBJ2:Object2 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11471 | OBJ3:Object3 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11472 | OBJ4:Object4 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11473 | OBJ5:Object5 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11474 | OBJ6:Object6 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11475 | OBJ7:Object7 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11476 | OBJ8:Object8 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11477 | OBJ9:Object9 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11478 | OBJ10:Object10 Withdraw Status | R | 1 | 0=WDIntermediate;1=WDCartOut;2=WDCart In;3=WDBad;4=Not in use
11479 | GSYN:Synchronizing by | R(W) | 1 | 0=System voltages to U3/U4 Input;1=Between U3/U4 Input
11480 | PFC1:Target power factor | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
11481 |  |  |  | HR11480 (Lo-16bits)
11482 | PFC1:Target power factor | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
11483 |  |  |  | HR11482 (Lo-16bits)
11484 | PFC1:Target power factor | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
11485 |  |  |  | HR11484 (Lo-16bits)
11486 | PFC1:Target power factor | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
11487 |  |  |  | HR11486 (Lo-16bits)
11488 | PFC1:Target power factor | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
11489 |  |  |  | HR11488 (Lo-16bits)
11490 | PFC1:Target power factor | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
11491 |  |  |  | HR11490 (Lo-16bits)
11492 | PFC1:Target power factor | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
11493 |  |  |  | HR11492 (Lo-16bits)
11494 | PFC1:Target power factor | R(W) | 2 | FLOAT [-1...1] (Hi-16bits)
11495 |  |  |  | HR11494 (Lo-16bits)
11496 | PFC1:Bank size for deltaQ calculation | R(W) | 2 | FLOAT [1...50000] (Hi-16bits)
11497 |  |  |  | HR11496 (Lo-16bits)
11498 | PFC1:Bank size for deltaQ calculation | R(W) | 2 | FLOAT [1...50000] (Hi-16bits)
11499 |  |  |  | HR11498 (Lo-16bits)
11500 | PFC1:Bank size for deltaQ calculation | R(W) | 2 | FLOAT [1...50000] (Hi-16bits)
11501 |  |  |  | HR11500 (Lo-16bits)
11502 | PFC1:Bank size for deltaQ calculation | R(W) | 2 | FLOAT [1...50000] (Hi-16bits)
11503 |  |  |  | HR11502 (Lo-16bits)
11504 | PFC1:Bank size for deltaQ calculation | R(W) | 2 | FLOAT [1...50000] (Hi-16bits)
11505 |  |  |  | HR11504 (Lo-16bits)
11506 | PFC1:Bank size for deltaQ calculation | R(W) | 2 | FLOAT [1...50000] (Hi-16bits)
11507 |  |  |  | HR11506 (Lo-16bits)
11508 | PFC1:Bank size for deltaQ calculation | R(W) | 2 | FLOAT [1...50000] (Hi-16bits)
11509 |  |  |  | HR11508 (Lo-16bits)
11510 | PFC1:Bank size for deltaQ calculation | R(W) | 2 | FLOAT [1...50000] (Hi-16bits)
11511 |  |  |  | HR11510 (Lo-16bits)
11512 | PFC1:More capacitance +kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11513 |  |  |  | HR11512 (Lo-16bits)
11514 | PFC1:More capacitance +kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11515 |  |  |  | HR11514 (Lo-16bits)
11516 | PFC1:More capacitance +kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11517 |  |  |  | HR11516 (Lo-16bits)
11518 | PFC1:More capacitance +kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11519 |  |  |  | HR11518 (Lo-16bits)
11520 | PFC1:More capacitance +kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11521 |  |  |  | HR11520 (Lo-16bits)
11522 | PFC1:More capacitance +kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11523 |  |  |  | HR11522 (Lo-16bits)
11524 | PFC1:More capacitance +kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11525 |  |  |  | HR11524 (Lo-16bits)
11526 | PFC1:More capacitance +kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11527 |  |  |  | HR11526 (Lo-16bits)
11528 | PFC1:Less capacitance -kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11529 |  |  |  | HR11528 (Lo-16bits)
11530 | PFC1:Less capacitance -kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11531 |  |  |  | HR11530 (Lo-16bits)
11532 | PFC1:Less capacitance -kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11533 |  |  |  | HR11532 (Lo-16bits)
11534 | PFC1:Less capacitance -kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11535 |  |  |  | HR11534 (Lo-16bits)
11536 | PFC1:Less capacitance -kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11537 |  |  |  | HR11536 (Lo-16bits)
11538 | PFC1:Less capacitance -kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11539 |  |  |  | HR11538 (Lo-16bits)
11540 | PFC1:Less capacitance -kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11541 |  |  |  | HR11540 (Lo-16bits)
11542 | PFC1:Less capacitance -kVAr percentage | R(W) | 2 | FLOAT [1...100] (Hi-16bits)
11543 |  |  |  | HR11542 (Lo-16bits)
11544 | VRG1:AVR T1 tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11545 |  |  |  | HR11544 (Lo-16bits)
11546 | VRG1:AVR T2 tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11547 |  |  |  | HR11546 (Lo-16bits)
11548 | VRG1:AVR T3 tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11549 |  |  |  | HR11548 (Lo-16bits)
11550 | VRG1:AVR T4 tap voltage | R | 2 | FLOAT [0...250] (Hi-16bits)
11551 |  |  |  | HR11550 (Lo-16bits)
11552 | VRG1:AVR running status to mimic | R | 1 | 0=AVR not running;1=AVR running
11553 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11554 |  |  |  | HR11553 (Lo-16bits)
11555 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11556 |  |  |  | HR11555 (Lo-16bits)
11557 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11558 |  |  |  | HR11557 (Lo-16bits)
11559 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11560 |  |  |  | HR11559 (Lo-16bits)
11561 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11562 |  |  |  | HR11561 (Lo-16bits)
11563 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11564 |  |  |  | HR11563 (Lo-16bits)
11565 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11566 |  |  |  | HR11565 (Lo-16bits)
11567 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11568 |  |  |  | HR11567 (Lo-16bits)
11569 | VRG1:Tap voltage level | R | 2 | FLOAT [0...250] (Hi-16bits)
11570 |  |  |  | HR11569 (Lo-16bits)
11571 | HSHC:HSO card output status | R | 2 | 0b=HSO1;1b=HSO2;2b=HSO3;3b=HSO4;4b=HSO5;5b=HSO6;6b=HSO7;7b=HSO8;8b=HSO9 (Hi-16bits)
11572 |  |  |  | HR11571 (Lo-16bits)
11573 | DIAG:Diagnostic alarm status | R | 2 | 0b=Temp. out of range;1b=Voltage out of range;2b=HW configuration invalid;3b=Relay output failure;4b=Option card A alarm;5b=Option card B alarm;6b=Option card C alarm;7b=Option card D alarm;8b=Option card E alarm;9b=Option card F alarm;10b=Safe setting mode active;11b=System overload;12b=GOOSE simulation enabled;13b=Device/LN mode not On;14b=UAC password issue;15b=Audit logging failed;16b=Option card G alarm;17b=Option card H alarm;18b=Option card I alarm;19b=Option card J alarm;20b=Option card K alarm;21b=Option card L alarm;22b=Option card M alarm;23b=Option card N alarm (Hi-16bits)
11574 |  |  |  | HR11573 (Lo-16bits)
11575 | IRF:Internal Relay Fault status | R | 2 | 0b=Storage error;1b=Logic file missing;2b=Aquisition unit error;3b=Measurement config error;4b=Relay hardware setup error;5b=System overload error;6b=Not configured yet;7b=Firmware upgrade done;8b=Slot supervision error;9b=Software inconsistency error;10b=Event overload; (Hi-16bits)
11576 |  |  |  | HR11575 (Lo-16bits)
11577 | LVRT1:LVRT [27T] mode | R(W) | 1 | 0=Disabled;1=Activated
11578 | LVRT1:LVRT condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
11579 | LVRT1:Fault start< | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11580 |  |  |  | HR11579 (Lo-16bits)
11581 | LVRT1:Fault start< | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11582 |  |  |  | HR11581 (Lo-16bits)
11583 | LVRT1:Fault start< | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11584 |  |  |  | HR11583 (Lo-16bits)
11585 | LVRT1:Fault start< | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11586 |  |  |  | HR11585 (Lo-16bits)
11587 | LVRT1:Fault start< | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11588 |  |  |  | HR11587 (Lo-16bits)
11589 | LVRT1:Fault start< | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11590 |  |  |  | HR11589 (Lo-16bits)
11591 | LVRT1:Fault start< | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11592 |  |  |  | HR11591 (Lo-16bits)
11593 | LVRT1:Fault start< | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11594 |  |  |  | HR11593 (Lo-16bits)
11595 | LVRT1:Fault release> | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11596 |  |  |  | HR11595 (Lo-16bits)
11597 | LVRT1:Fault release> | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11598 |  |  |  | HR11597 (Lo-16bits)
11599 | LVRT1:Fault release> | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11600 |  |  |  | HR11599 (Lo-16bits)
11601 | LVRT1:Fault release> | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11602 |  |  |  | HR11601 (Lo-16bits)
11603 | LVRT1:Fault release> | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11604 |  |  |  | HR11603 (Lo-16bits)
11605 | LVRT1:Fault release> | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11606 |  |  |  | HR11605 (Lo-16bits)
11607 | LVRT1:Fault release> | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11608 |  |  |  | HR11607 (Lo-16bits)
11609 | LVRT1:Fault release> | R(W) | 2 | FLOAT [50...120] (Hi-16bits)
11610 |  |  |  | HR11609 (Lo-16bits)
11611 | LVRT1:Low voltage block limit | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
11612 |  |  |  | HR11611 (Lo-16bits)
11613 | LVRT1:Low voltage block limit | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
11614 |  |  |  | HR11613 (Lo-16bits)
11615 | LVRT1:Low voltage block limit | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
11616 |  |  |  | HR11615 (Lo-16bits)
11617 | LVRT1:Low voltage block limit | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
11618 |  |  |  | HR11617 (Lo-16bits)
11619 | LVRT1:Low voltage block limit | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
11620 |  |  |  | HR11619 (Lo-16bits)
11621 | LVRT1:Low voltage block limit | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
11622 |  |  |  | HR11621 (Lo-16bits)
11623 | LVRT1:Low voltage block limit | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
11624 |  |  |  | HR11623 (Lo-16bits)
11625 | LVRT1:Low voltage block limit | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
11626 |  |  |  | HR11625 (Lo-16bits)
11627 | LVRT1:Number of knee points | R(W) | 1 | 0=2;1=3;2=4;3=5;4=6;5=7;6=8;7=9;8=10
11628 | LVRT1:Number of knee points | R(W) | 1 | 0=2;1=3;2=4;3=5;4=6;5=7;6=8;7=9;8=10
11629 | LVRT1:Number of knee points | R(W) | 1 | 0=2;1=3;2=4;3=5;4=6;5=7;6=8;7=9;8=10
11630 | LVRT1:Number of knee points | R(W) | 1 | 0=2;1=3;2=4;3=5;4=6;5=7;6=8;7=9;8=10
11631 | LVRT1:Number of knee points | R(W) | 1 | 0=2;1=3;2=4;3=5;4=6;5=7;6=8;7=9;8=10
11632 | LVRT1:Number of knee points | R(W) | 1 | 0=2;1=3;2=4;3=5;4=6;5=7;6=8;7=9;8=10
11633 | LVRT1:Number of knee points | R(W) | 1 | 0=2;1=3;2=4;3=5;4=6;5=7;6=8;7=9;8=10
11634 | LVRT1:Number of knee points | R(W) | 1 | 0=2;1=3;2=4;3=5;4=6;5=7;6=8;7=9;8=10
11635 | LVRT1:Amplitude plot[1] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11636 |  |  |  | HR11635 (Lo-16bits)
11637 | LVRT1:Amplitude plot[1] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11638 |  |  |  | HR11637 (Lo-16bits)
11639 | LVRT1:Amplitude plot[1] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11640 |  |  |  | HR11639 (Lo-16bits)
11641 | LVRT1:Amplitude plot[1] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11642 |  |  |  | HR11641 (Lo-16bits)
11643 | LVRT1:Amplitude plot[1] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11644 |  |  |  | HR11643 (Lo-16bits)
11645 | LVRT1:Amplitude plot[1] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11646 |  |  |  | HR11645 (Lo-16bits)
11647 | LVRT1:Amplitude plot[1] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11648 |  |  |  | HR11647 (Lo-16bits)
11649 | LVRT1:Amplitude plot[1] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11650 |  |  |  | HR11649 (Lo-16bits)
11651 | LVRT1:Time plot[1] | R | 2 | FLOAT [0...1800] (Hi-16bits)
11652 |  |  |  | HR11651 (Lo-16bits)
11653 | LVRT1:Time plot[1] | R | 2 | FLOAT [0...1800] (Hi-16bits)
11654 |  |  |  | HR11653 (Lo-16bits)
11655 | LVRT1:Time plot[1] | R | 2 | FLOAT [0...1800] (Hi-16bits)
11656 |  |  |  | HR11655 (Lo-16bits)
11657 | LVRT1:Time plot[1] | R | 2 | FLOAT [0...1800] (Hi-16bits)
11658 |  |  |  | HR11657 (Lo-16bits)
11659 | LVRT1:Time plot[1] | R | 2 | FLOAT [0...1800] (Hi-16bits)
11660 |  |  |  | HR11659 (Lo-16bits)
11661 | LVRT1:Time plot[1] | R | 2 | FLOAT [0...1800] (Hi-16bits)
11662 |  |  |  | HR11661 (Lo-16bits)
11663 | LVRT1:Time plot[1] | R | 2 | FLOAT [0...1800] (Hi-16bits)
11664 |  |  |  | HR11663 (Lo-16bits)
11665 | LVRT1:Time plot[1] | R | 2 | FLOAT [0...1800] (Hi-16bits)
11666 |  |  |  | HR11665 (Lo-16bits)
11667 | LVRT1:Amplitude plot[2] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11668 |  |  |  | HR11667 (Lo-16bits)
11669 | LVRT1:Amplitude plot[2] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11670 |  |  |  | HR11669 (Lo-16bits)
11671 | LVRT1:Amplitude plot[2] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11672 |  |  |  | HR11671 (Lo-16bits)
11673 | LVRT1:Amplitude plot[2] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11674 |  |  |  | HR11673 (Lo-16bits)
11675 | LVRT1:Amplitude plot[2] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11676 |  |  |  | HR11675 (Lo-16bits)
11677 | LVRT1:Amplitude plot[2] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11678 |  |  |  | HR11677 (Lo-16bits)
11679 | LVRT1:Amplitude plot[2] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11680 |  |  |  | HR11679 (Lo-16bits)
11681 | LVRT1:Amplitude plot[2] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11682 |  |  |  | HR11681 (Lo-16bits)
11683 | LVRT1:Time plot[2] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11684 |  |  |  | HR11683 (Lo-16bits)
11685 | LVRT1:Time plot[2] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11686 |  |  |  | HR11685 (Lo-16bits)
11687 | LVRT1:Time plot[2] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11688 |  |  |  | HR11687 (Lo-16bits)
11689 | LVRT1:Time plot[2] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11690 |  |  |  | HR11689 (Lo-16bits)
11691 | LVRT1:Time plot[2] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11692 |  |  |  | HR11691 (Lo-16bits)
11693 | LVRT1:Time plot[2] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11694 |  |  |  | HR11693 (Lo-16bits)
11695 | LVRT1:Time plot[2] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11696 |  |  |  | HR11695 (Lo-16bits)
11697 | LVRT1:Time plot[2] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11698 |  |  |  | HR11697 (Lo-16bits)
11699 | LVRT1:Amplitude plot[3] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11700 |  |  |  | HR11699 (Lo-16bits)
11701 | LVRT1:Amplitude plot[3] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11702 |  |  |  | HR11701 (Lo-16bits)
11703 | LVRT1:Amplitude plot[3] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11704 |  |  |  | HR11703 (Lo-16bits)
11705 | LVRT1:Amplitude plot[3] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11706 |  |  |  | HR11705 (Lo-16bits)
11707 | LVRT1:Amplitude plot[3] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11708 |  |  |  | HR11707 (Lo-16bits)
11709 | LVRT1:Amplitude plot[3] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11710 |  |  |  | HR11709 (Lo-16bits)
11711 | LVRT1:Amplitude plot[3] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11712 |  |  |  | HR11711 (Lo-16bits)
11713 | LVRT1:Amplitude plot[3] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11714 |  |  |  | HR11713 (Lo-16bits)
11715 | LVRT1:Time plot[3] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11716 |  |  |  | HR11715 (Lo-16bits)
11717 | LVRT1:Time plot[3] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11718 |  |  |  | HR11717 (Lo-16bits)
11719 | LVRT1:Time plot[3] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11720 |  |  |  | HR11719 (Lo-16bits)
11721 | LVRT1:Time plot[3] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11722 |  |  |  | HR11721 (Lo-16bits)
11723 | LVRT1:Time plot[3] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11724 |  |  |  | HR11723 (Lo-16bits)
11725 | LVRT1:Time plot[3] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11726 |  |  |  | HR11725 (Lo-16bits)
11727 | LVRT1:Time plot[3] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11728 |  |  |  | HR11727 (Lo-16bits)
11729 | LVRT1:Time plot[3] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11730 |  |  |  | HR11729 (Lo-16bits)
11731 | LVRT1:Amplitude plot[4] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11732 |  |  |  | HR11731 (Lo-16bits)
11733 | LVRT1:Amplitude plot[4] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11734 |  |  |  | HR11733 (Lo-16bits)
11735 | LVRT1:Amplitude plot[4] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11736 |  |  |  | HR11735 (Lo-16bits)
11737 | LVRT1:Amplitude plot[4] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11738 |  |  |  | HR11737 (Lo-16bits)
11739 | LVRT1:Amplitude plot[4] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11740 |  |  |  | HR11739 (Lo-16bits)
11741 | LVRT1:Amplitude plot[4] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11742 |  |  |  | HR11741 (Lo-16bits)
11743 | LVRT1:Amplitude plot[4] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11744 |  |  |  | HR11743 (Lo-16bits)
11745 | LVRT1:Amplitude plot[4] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11746 |  |  |  | HR11745 (Lo-16bits)
11747 | LVRT1:Time plot[4] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11748 |  |  |  | HR11747 (Lo-16bits)
11749 | LVRT1:Time plot[4] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11750 |  |  |  | HR11749 (Lo-16bits)
11751 | LVRT1:Time plot[4] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11752 |  |  |  | HR11751 (Lo-16bits)
11753 | LVRT1:Time plot[4] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11754 |  |  |  | HR11753 (Lo-16bits)
11755 | LVRT1:Time plot[4] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11756 |  |  |  | HR11755 (Lo-16bits)
11757 | LVRT1:Time plot[4] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11758 |  |  |  | HR11757 (Lo-16bits)
11759 | LVRT1:Time plot[4] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11760 |  |  |  | HR11759 (Lo-16bits)
11761 | LVRT1:Time plot[4] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11762 |  |  |  | HR11761 (Lo-16bits)
11763 | LVRT1:Amplitude plot[5] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11764 |  |  |  | HR11763 (Lo-16bits)
11765 | LVRT1:Amplitude plot[5] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11766 |  |  |  | HR11765 (Lo-16bits)
11767 | LVRT1:Amplitude plot[5] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11768 |  |  |  | HR11767 (Lo-16bits)
11769 | LVRT1:Amplitude plot[5] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11770 |  |  |  | HR11769 (Lo-16bits)
11771 | LVRT1:Amplitude plot[5] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11772 |  |  |  | HR11771 (Lo-16bits)
11773 | LVRT1:Amplitude plot[5] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11774 |  |  |  | HR11773 (Lo-16bits)
11775 | LVRT1:Amplitude plot[5] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11776 |  |  |  | HR11775 (Lo-16bits)
11777 | LVRT1:Amplitude plot[5] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11778 |  |  |  | HR11777 (Lo-16bits)
11779 | LVRT1:Time plot[5] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11780 |  |  |  | HR11779 (Lo-16bits)
11781 | LVRT1:Time plot[5] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11782 |  |  |  | HR11781 (Lo-16bits)
11783 | LVRT1:Time plot[5] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11784 |  |  |  | HR11783 (Lo-16bits)
11785 | LVRT1:Time plot[5] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11786 |  |  |  | HR11785 (Lo-16bits)
11787 | LVRT1:Time plot[5] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11788 |  |  |  | HR11787 (Lo-16bits)
11789 | LVRT1:Time plot[5] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11790 |  |  |  | HR11789 (Lo-16bits)
11791 | LVRT1:Time plot[5] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11792 |  |  |  | HR11791 (Lo-16bits)
11793 | LVRT1:Time plot[5] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11794 |  |  |  | HR11793 (Lo-16bits)
11795 | LVRT1:Amplitude plot[6] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11796 |  |  |  | HR11795 (Lo-16bits)
11797 | LVRT1:Amplitude plot[6] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11798 |  |  |  | HR11797 (Lo-16bits)
11799 | LVRT1:Amplitude plot[6] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11800 |  |  |  | HR11799 (Lo-16bits)
11801 | LVRT1:Amplitude plot[6] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11802 |  |  |  | HR11801 (Lo-16bits)
11803 | LVRT1:Amplitude plot[6] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11804 |  |  |  | HR11803 (Lo-16bits)
11805 | LVRT1:Amplitude plot[6] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11806 |  |  |  | HR11805 (Lo-16bits)
11807 | LVRT1:Amplitude plot[6] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11808 |  |  |  | HR11807 (Lo-16bits)
11809 | LVRT1:Amplitude plot[6] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11810 |  |  |  | HR11809 (Lo-16bits)
11811 | LVRT1:Time plot[6] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11812 |  |  |  | HR11811 (Lo-16bits)
11813 | LVRT1:Time plot[6] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11814 |  |  |  | HR11813 (Lo-16bits)
11815 | LVRT1:Time plot[6] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11816 |  |  |  | HR11815 (Lo-16bits)
11817 | LVRT1:Time plot[6] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11818 |  |  |  | HR11817 (Lo-16bits)
11819 | LVRT1:Time plot[6] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11820 |  |  |  | HR11819 (Lo-16bits)
11821 | LVRT1:Time plot[6] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11822 |  |  |  | HR11821 (Lo-16bits)
11823 | LVRT1:Time plot[6] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11824 |  |  |  | HR11823 (Lo-16bits)
11825 | LVRT1:Time plot[6] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11826 |  |  |  | HR11825 (Lo-16bits)
11827 | LVRT1:Amplitude plot[7] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11828 |  |  |  | HR11827 (Lo-16bits)
11829 | LVRT1:Amplitude plot[7] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11830 |  |  |  | HR11829 (Lo-16bits)
11831 | LVRT1:Amplitude plot[7] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11832 |  |  |  | HR11831 (Lo-16bits)
11833 | LVRT1:Amplitude plot[7] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11834 |  |  |  | HR11833 (Lo-16bits)
11835 | LVRT1:Amplitude plot[7] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11836 |  |  |  | HR11835 (Lo-16bits)
11837 | LVRT1:Amplitude plot[7] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11838 |  |  |  | HR11837 (Lo-16bits)
11839 | LVRT1:Amplitude plot[7] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11840 |  |  |  | HR11839 (Lo-16bits)
11841 | LVRT1:Amplitude plot[7] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11842 |  |  |  | HR11841 (Lo-16bits)
11843 | LVRT1:Time plot[7] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11844 |  |  |  | HR11843 (Lo-16bits)
11845 | LVRT1:Time plot[7] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11846 |  |  |  | HR11845 (Lo-16bits)
11847 | LVRT1:Time plot[7] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11848 |  |  |  | HR11847 (Lo-16bits)
11849 | LVRT1:Time plot[7] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11850 |  |  |  | HR11849 (Lo-16bits)
11851 | LVRT1:Time plot[7] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11852 |  |  |  | HR11851 (Lo-16bits)
11853 | LVRT1:Time plot[7] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11854 |  |  |  | HR11853 (Lo-16bits)
11855 | LVRT1:Time plot[7] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11856 |  |  |  | HR11855 (Lo-16bits)
11857 | LVRT1:Time plot[7] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11858 |  |  |  | HR11857 (Lo-16bits)
11859 | LVRT1:Amplitude plot[8] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11860 |  |  |  | HR11859 (Lo-16bits)
11861 | LVRT1:Amplitude plot[8] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11862 |  |  |  | HR11861 (Lo-16bits)
11863 | LVRT1:Amplitude plot[8] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11864 |  |  |  | HR11863 (Lo-16bits)
11865 | LVRT1:Amplitude plot[8] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11866 |  |  |  | HR11865 (Lo-16bits)
11867 | LVRT1:Amplitude plot[8] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11868 |  |  |  | HR11867 (Lo-16bits)
11869 | LVRT1:Amplitude plot[8] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11870 |  |  |  | HR11869 (Lo-16bits)
11871 | LVRT1:Amplitude plot[8] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11872 |  |  |  | HR11871 (Lo-16bits)
11873 | LVRT1:Amplitude plot[8] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11874 |  |  |  | HR11873 (Lo-16bits)
11875 | LVRT1:Time plot[8] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11876 |  |  |  | HR11875 (Lo-16bits)
11877 | LVRT1:Time plot[8] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11878 |  |  |  | HR11877 (Lo-16bits)
11879 | LVRT1:Time plot[8] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11880 |  |  |  | HR11879 (Lo-16bits)
11881 | LVRT1:Time plot[8] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11882 |  |  |  | HR11881 (Lo-16bits)
11883 | LVRT1:Time plot[8] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11884 |  |  |  | HR11883 (Lo-16bits)
11885 | LVRT1:Time plot[8] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11886 |  |  |  | HR11885 (Lo-16bits)
11887 | LVRT1:Time plot[8] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11888 |  |  |  | HR11887 (Lo-16bits)
11889 | LVRT1:Time plot[8] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11890 |  |  |  | HR11889 (Lo-16bits)
11891 | LVRT1:Amplitude plot[9] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11892 |  |  |  | HR11891 (Lo-16bits)
11893 | LVRT1:Amplitude plot[9] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11894 |  |  |  | HR11893 (Lo-16bits)
11895 | LVRT1:Amplitude plot[9] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11896 |  |  |  | HR11895 (Lo-16bits)
11897 | LVRT1:Amplitude plot[9] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11898 |  |  |  | HR11897 (Lo-16bits)
11899 | LVRT1:Amplitude plot[9] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11900 |  |  |  | HR11899 (Lo-16bits)
11901 | LVRT1:Amplitude plot[9] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11902 |  |  |  | HR11901 (Lo-16bits)
11903 | LVRT1:Amplitude plot[9] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11904 |  |  |  | HR11903 (Lo-16bits)
11905 | LVRT1:Amplitude plot[9] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11906 |  |  |  | HR11905 (Lo-16bits)
11907 | LVRT1:Time plot[9] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11908 |  |  |  | HR11907 (Lo-16bits)
11909 | LVRT1:Time plot[9] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11910 |  |  |  | HR11909 (Lo-16bits)
11911 | LVRT1:Time plot[9] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11912 |  |  |  | HR11911 (Lo-16bits)
11913 | LVRT1:Time plot[9] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11914 |  |  |  | HR11913 (Lo-16bits)
11915 | LVRT1:Time plot[9] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11916 |  |  |  | HR11915 (Lo-16bits)
11917 | LVRT1:Time plot[9] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11918 |  |  |  | HR11917 (Lo-16bits)
11919 | LVRT1:Time plot[9] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11920 |  |  |  | HR11919 (Lo-16bits)
11921 | LVRT1:Time plot[9] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11922 |  |  |  | HR11921 (Lo-16bits)
11923 | LVRT1:Amplitude plot[10] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11924 |  |  |  | HR11923 (Lo-16bits)
11925 | LVRT1:Amplitude plot[10] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11926 |  |  |  | HR11925 (Lo-16bits)
11927 | LVRT1:Amplitude plot[10] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11928 |  |  |  | HR11927 (Lo-16bits)
11929 | LVRT1:Amplitude plot[10] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11930 |  |  |  | HR11929 (Lo-16bits)
11931 | LVRT1:Amplitude plot[10] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11932 |  |  |  | HR11931 (Lo-16bits)
11933 | LVRT1:Amplitude plot[10] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11934 |  |  |  | HR11933 (Lo-16bits)
11935 | LVRT1:Amplitude plot[10] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11936 |  |  |  | HR11935 (Lo-16bits)
11937 | LVRT1:Amplitude plot[10] | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
11938 |  |  |  | HR11937 (Lo-16bits)
11939 | LVRT1:Time plot[10] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11940 |  |  |  | HR11939 (Lo-16bits)
11941 | LVRT1:Time plot[10] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11942 |  |  |  | HR11941 (Lo-16bits)
11943 | LVRT1:Time plot[10] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11944 |  |  |  | HR11943 (Lo-16bits)
11945 | LVRT1:Time plot[10] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11946 |  |  |  | HR11945 (Lo-16bits)
11947 | LVRT1:Time plot[10] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11948 |  |  |  | HR11947 (Lo-16bits)
11949 | LVRT1:Time plot[10] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11950 |  |  |  | HR11949 (Lo-16bits)
11951 | LVRT1:Time plot[10] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11952 |  |  |  | HR11951 (Lo-16bits)
11953 | LVRT1:Time plot[10] | R(W) | 2 | FLOAT [0.100...1800] (Hi-16bits)
11954 |  |  |  | HR11953 (Lo-16bits)
11955 | PVPS:PVPS Line comm ok | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11956 |  |  |  | HR11955 (Lo-16bits)
11957 | PVPS:PVPS Line comm failure | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11958 |  |  |  | HR11957 (Lo-16bits)
11959 | PVPS:PVPS Any line protection failure | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11960 |  |  |  | HR11959 (Lo-16bits)
11961 | PVPS:PVPS Units synchronization Ok | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11962 |  |  |  | HR11961 (Lo-16bits)
11963 | PVPS:PVPS Synchronization lost | R | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
11964 |  |  |  | HR11963 (Lo-16bits)
11965 | LDIF1:Enable configuration | R(W) | 1 | 0=Disabled;1=Enabled (Halt protection)
11966 | LDIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
11967 | LDIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
11968 | LDIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
11969 | LDIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
11970 | LDIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
11971 | LDIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
11972 | LDIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
11973 | LDIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
11974 | LDIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
11975 | LDIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
11976 | LDIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
11977 | LDIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
11978 | LDIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
11979 | LDIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
11980 | LDIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
11981 | LDIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
11982 | LDIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
11983 |  |  |  | HR11982 (Lo-16bits)
11984 | LDIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
11985 |  |  |  | HR11984 (Lo-16bits)
11986 | LDIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
11987 |  |  |  | HR11986 (Lo-16bits)
11988 | LDIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
11989 |  |  |  | HR11988 (Lo-16bits)
11990 | LDIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
11991 |  |  |  | HR11990 (Lo-16bits)
11992 | LDIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
11993 |  |  |  | HR11992 (Lo-16bits)
11994 | LDIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
11995 |  |  |  | HR11994 (Lo-16bits)
11996 | LDIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
11997 |  |  |  | HR11996 (Lo-16bits)
11998 | LDIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
11999 |  |  |  | HR11998 (Lo-16bits)
12000 | LDIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12001 |  |  |  | HR12000 (Lo-16bits)
12002 | LDIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12003 |  |  |  | HR12002 (Lo-16bits)
12004 | LDIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12005 |  |  |  | HR12004 (Lo-16bits)
12006 | LDIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12007 |  |  |  | HR12006 (Lo-16bits)
12008 | LDIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12009 |  |  |  | HR12008 (Lo-16bits)
12010 | LDIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12011 |  |  |  | HR12010 (Lo-16bits)
12012 | LDIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12013 |  |  |  | HR12012 (Lo-16bits)
12014 | LDIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12015 |  |  |  | HR12014 (Lo-16bits)
12016 | LDIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12017 |  |  |  | HR12016 (Lo-16bits)
12018 | LDIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12019 |  |  |  | HR12018 (Lo-16bits)
12020 | LDIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12021 |  |  |  | HR12020 (Lo-16bits)
12022 | LDIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12023 |  |  |  | HR12022 (Lo-16bits)
12024 | LDIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12025 |  |  |  | HR12024 (Lo-16bits)
12026 | LDIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12027 |  |  |  | HR12026 (Lo-16bits)
12028 | LDIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12029 |  |  |  | HR12028 (Lo-16bits)
12030 | LDIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12031 |  |  |  | HR12030 (Lo-16bits)
12032 | LDIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12033 |  |  |  | HR12032 (Lo-16bits)
12034 | LDIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12035 |  |  |  | HR12034 (Lo-16bits)
12036 | LDIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12037 |  |  |  | HR12036 (Lo-16bits)
12038 | LDIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12039 |  |  |  | HR12038 (Lo-16bits)
12040 | LDIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12041 |  |  |  | HR12040 (Lo-16bits)
12042 | LDIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12043 |  |  |  | HR12042 (Lo-16bits)
12044 | LDIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12045 |  |  |  | HR12044 (Lo-16bits)
12046 | LDIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12047 |  |  |  | HR12046 (Lo-16bits)
12048 | LDIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12049 |  |  |  | HR12048 (Lo-16bits)
12050 | LDIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12051 |  |  |  | HR12050 (Lo-16bits)
12052 | LDIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12053 |  |  |  | HR12052 (Lo-16bits)
12054 | LDIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12055 |  |  |  | HR12054 (Lo-16bits)
12056 | LDIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12057 |  |  |  | HR12056 (Lo-16bits)
12058 | LDIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12059 |  |  |  | HR12058 (Lo-16bits)
12060 | LDIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12061 |  |  |  | HR12060 (Lo-16bits)
12062 | LDIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12063 | LDIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12064 | LDIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12065 | LDIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12066 | LDIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12067 | LDIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12068 | LDIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12069 | LDIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12070 | LDIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12071 |  |  |  | HR12070 (Lo-16bits)
12072 | LDIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12073 |  |  |  | HR12072 (Lo-16bits)
12074 | LDIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12075 |  |  |  | HR12074 (Lo-16bits)
12076 | LDIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12077 |  |  |  | HR12076 (Lo-16bits)
12078 | LDIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12079 |  |  |  | HR12078 (Lo-16bits)
12080 | LDIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12081 |  |  |  | HR12080 (Lo-16bits)
12082 | LDIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12083 |  |  |  | HR12082 (Lo-16bits)
12084 | LDIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12085 |  |  |  | HR12084 (Lo-16bits)
12086 | LDIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12087 |  |  |  | HR12086 (Lo-16bits)
12088 | LDIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12089 |  |  |  | HR12088 (Lo-16bits)
12090 | LDIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12091 |  |  |  | HR12090 (Lo-16bits)
12092 | LDIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12093 |  |  |  | HR12092 (Lo-16bits)
12094 | LDIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12095 |  |  |  | HR12094 (Lo-16bits)
12096 | LDIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12097 |  |  |  | HR12096 (Lo-16bits)
12098 | LDIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12099 |  |  |  | HR12098 (Lo-16bits)
12100 | LDIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12101 |  |  |  | HR12100 (Lo-16bits)
12102 | LDIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12103 | LDIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12104 | LDIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12105 | LDIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12106 | LDIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12107 | LDIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12108 | LDIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12109 | LDIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12110 | LDIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12111 |  |  |  | HR12110 (Lo-16bits)
12112 | LDIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12113 |  |  |  | HR12112 (Lo-16bits)
12114 | LDIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12115 |  |  |  | HR12114 (Lo-16bits)
12116 | LDIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12117 |  |  |  | HR12116 (Lo-16bits)
12118 | LDIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12119 |  |  |  | HR12118 (Lo-16bits)
12120 | LDIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12121 |  |  |  | HR12120 (Lo-16bits)
12122 | LDIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12123 |  |  |  | HR12122 (Lo-16bits)
12124 | LDIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12125 |  |  |  | HR12124 (Lo-16bits)
12126 | DMA1:Combined status | R | 2 | 0b=IL1 alarm;1b=IL2 alarm;2b=IL3 alarm;3b=S 3phase alarm;4b=P 3phase alarm;5b=Q 3phase alarm;6b=PF 3phase alarm;7b=IL1 harmonic alarm;8b=IL2 harmonic alarm;9b=IL3 harmonic alarm;10b=Function blocked (Hi-16bits)
12127 |  |  |  | HR12126 (Lo-16bits)
12128 | CBF1:CBFP current measurement side | R(W) | 1 | 0=CT1;1=CT2
12129 | CBF1:Operating Mode selection | R(W) | 1 | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
12130 | CBF1:Operating Mode selection | R(W) | 1 | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
12131 | CBF1:Operating Mode selection | R(W) | 1 | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
12132 | CBF1:Operating Mode selection | R(W) | 1 | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
12133 | CBF1:Operating Mode selection | R(W) | 1 | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
12134 | CBF1:Operating Mode selection | R(W) | 1 | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
12135 | CBF1:Operating Mode selection | R(W) | 1 | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
12136 | CBF1:Operating Mode selection | R(W) | 1 | 0=Curr only;1=DO only;2=Signals only;3=Curr and DO;4=Curr or DO;5=Curr and signs;6=Curr or signs;7=Signs and DO;8=Signs or DO;9=Curr and signs and DO;10=Curr or signs or DO
12137 | CBF1:Iset | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
12138 |  |  |  | HR12137 (Lo-16bits)
12139 | CBF1:Iset | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
12140 |  |  |  | HR12139 (Lo-16bits)
12141 | CBF1:Iset | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
12142 |  |  |  | HR12141 (Lo-16bits)
12143 | CBF1:Iset | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
12144 |  |  |  | HR12143 (Lo-16bits)
12145 | CBF1:Iset | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
12146 |  |  |  | HR12145 (Lo-16bits)
12147 | CBF1:Iset | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
12148 |  |  |  | HR12147 (Lo-16bits)
12149 | CBF1:Iset | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
12150 |  |  |  | HR12149 (Lo-16bits)
12151 | CBF1:Iset | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
12152 |  |  |  | HR12151 (Lo-16bits)
12153 | CBF1:I0 input selection | R(W) | 1 | 0=Not in use;1=I01;2=I02;3=I0Calc
12154 | CBF1:I0 input selection | R(W) | 1 | 0=Not in use;1=I01;2=I02;3=I0Calc
12155 | CBF1:I0 input selection | R(W) | 1 | 0=Not in use;1=I01;2=I02;3=I0Calc
12156 | CBF1:I0 input selection | R(W) | 1 | 0=Not in use;1=I01;2=I02;3=I0Calc
12157 | CBF1:I0 input selection | R(W) | 1 | 0=Not in use;1=I01;2=I02;3=I0Calc
12158 | CBF1:I0 input selection | R(W) | 1 | 0=Not in use;1=I01;2=I02;3=I0Calc
12159 | CBF1:I0 input selection | R(W) | 1 | 0=Not in use;1=I01;2=I02;3=I0Calc
12160 | CBF1:I0 input selection | R(W) | 1 | 0=Not in use;1=I01;2=I02;3=I0Calc
12161 | CBF1:I0set | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
12162 |  |  |  | HR12161 (Lo-16bits)
12163 | CBF1:I0set | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
12164 |  |  |  | HR12163 (Lo-16bits)
12165 | CBF1:I0set | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
12166 |  |  |  | HR12165 (Lo-16bits)
12167 | CBF1:I0set | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
12168 |  |  |  | HR12167 (Lo-16bits)
12169 | CBF1:I0set | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
12170 |  |  |  | HR12169 (Lo-16bits)
12171 | CBF1:I0set | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
12172 |  |  |  | HR12171 (Lo-16bits)
12173 | CBF1:I0set | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
12174 |  |  |  | HR12173 (Lo-16bits)
12175 | CBF1:I0set | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
12176 |  |  |  | HR12175 (Lo-16bits)
12177 | CBF1:Enable retrip | R(W) | 1 | 0=No;1=Yes
12178 | CBF1:Enable retrip | R(W) | 1 | 0=No;1=Yes
12179 | CBF1:Enable retrip | R(W) | 1 | 0=No;1=Yes
12180 | CBF1:Enable retrip | R(W) | 1 | 0=No;1=Yes
12181 | CBF1:Enable retrip | R(W) | 1 | 0=No;1=Yes
12182 | CBF1:Enable retrip | R(W) | 1 | 0=No;1=Yes
12183 | CBF1:Enable retrip | R(W) | 1 | 0=No;1=Yes
12184 | CBF1:Enable retrip | R(W) | 1 | 0=No;1=Yes
12185 | CBF1:Retrip time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12186 |  |  |  | HR12185 (Lo-16bits)
12187 | CBF1:Retrip time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12188 |  |  |  | HR12187 (Lo-16bits)
12189 | CBF1:Retrip time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12190 |  |  |  | HR12189 (Lo-16bits)
12191 | CBF1:Retrip time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12192 |  |  |  | HR12191 (Lo-16bits)
12193 | CBF1:Retrip time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12194 |  |  |  | HR12193 (Lo-16bits)
12195 | CBF1:Retrip time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12196 |  |  |  | HR12195 (Lo-16bits)
12197 | CBF1:Retrip time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12198 |  |  |  | HR12197 (Lo-16bits)
12199 | CBF1:Retrip time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12200 |  |  |  | HR12199 (Lo-16bits)
12201 | CBF1:CBFP time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12202 |  |  |  | HR12201 (Lo-16bits)
12203 | CBF1:CBFP time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12204 |  |  |  | HR12203 (Lo-16bits)
12205 | CBF1:CBFP time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12206 |  |  |  | HR12205 (Lo-16bits)
12207 | CBF1:CBFP time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12208 |  |  |  | HR12207 (Lo-16bits)
12209 | CBF1:CBFP time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12210 |  |  |  | HR12209 (Lo-16bits)
12211 | CBF1:CBFP time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12212 |  |  |  | HR12211 (Lo-16bits)
12213 | CBF1:CBFP time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12214 |  |  |  | HR12213 (Lo-16bits)
12215 | CBF1:CBFP time delay | R(W) | 2 | FLOAT [0.05...1800] (Hi-16bits)
12216 |  |  |  | HR12215 (Lo-16bits)
12217 | MST1:MST mode | R(W) | 1 | 0=Disabled;1=Activated
12218 | MST1:MST measurement side | R(W) | 1 | 0=CT1;1=CT2
12219 | MST1:Per unitize relay currents to Motor In | R(W) | 1 | 0=No, use CT nominal as pu.;1=Yes, scale all to Imot
12220 | MST1:Motor nominal current | R(W) | 2 | FLOAT [0.1...10000] (Hi-16bits)
12221 |  |  |  | HR12220 (Lo-16bits)
12222 | MST1:Nominal Starting current | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
12223 |  |  |  | HR12222 (Lo-16bits)
12224 | MST1:Start detect current | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
12225 |  |  |  | HR12224 (Lo-16bits)
12226 | MST1:Min locked rotor current | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
12227 |  |  |  | HR12226 (Lo-16bits)
12228 | MST1:Max locked rotor current | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
12229 |  |  |  | HR12228 (Lo-16bits)
12230 | MST1:Maximum overload current | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
12231 |  |  |  | HR12230 (Lo-16bits)
12232 | MST1:No Load current | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
12233 |  |  |  | HR12232 (Lo-16bits)
12234 | MST1:Motor service factor | R(W) | 2 | FLOAT [0.01...5] (Hi-16bits)
12235 |  |  |  | HR12234 (Lo-16bits)
12236 | MST1:Hot condition theta limit | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12237 |  |  |  | HR12236 (Lo-16bits)
12238 | MST1:Safe stall time cold | R(W) | 2 | FLOAT [0.1...600] (Hi-16bits)
12239 |  |  |  | HR12238 (Lo-16bits)
12240 | MST1:Safe stall time hot | R(W) | 2 | FLOAT [0.1...600] (Hi-16bits)
12241 |  |  |  | HR12240 (Lo-16bits)
12242 | MST1:Allowed Starts when cold | R(W) | 1 | UINT32 [1...100]
12243 | MST1:Allowed Starts when hot | R(W) | 1 | UINT32 [1...100]
12244 | MST1:Given Hot/Cold starts in time of: | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12245 |  |  |  | HR12244 (Lo-16bits)
12246 | MST1:Min time betw. starts | R(W) | 2 | FLOAT [0.1...600] (Hi-16bits)
12247 |  |  |  | HR12246 (Lo-16bits)
12248 | MST1:Overall differential protection | R(W) | 1 | 0=Machine diff. (Yy);1=Diff.with trafo(Xx)
12249 | DIF1:Transf. Vect. group | R(W) | 1 | 0=Manual Set;1=Yy0;2=Yyn0;3=YNy0;4=YNyn0;5=Yy6;6=Yyn6;7=YNy6;8=YNyn6;9=Yd1;10=YNd1;11=Yd7;12=YNd7;13=Yd11;14=YNd11;15=Yd5;16=YNd5;17=Dy1;18=Dyn1;19=Dy7;20=Dyn7;21=Dy11;22=Dyn11;23=Dy5;24=Dyn5;25=Dd0;26=Dd6;
12250 | DIF1:HV side Star or Zigzag / Delta | R(W) | 1 | 0=Star / Zigzag;1=Delta;
12251 | DIF1:HV side grounded | R(W) | 1 | 0=Not grounded;1=Grounded;
12252 | DIF1:HV side lead or lag LV | R(W) | 1 | 0=Lead;1=Lag;
12253 | DIF1:LV side Star or Zigzag / Delta | R(W) | 1 | 0=Star / Zigzag;1=Delta;
12254 | DIF1:LV side grounded | R(W) | 1 | 0=Not grounded;1=Grounded;
12255 | DIF1:LV side lead or lag HV | R(W) | 1 | 0=Lead;1=Lag;
12256 | DIF1:HV-LV side phase angle | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
12257 |  |  |  | HR12256 (Lo-16bits)
12258 | DIF1:HV-LV side mag correction | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12259 |  |  |  | HR12258 (Lo-16bits)
12260 | DIF1:Enable Id0> (REF) HV side | R(W) | 1 | 0=Disabled;1=Enabled
12261 | DIF1:HV side Starpoint meas. | R(W) | 1 | 0=I01;1=I02
12262 | DIF1:Enable Id0> (REF) LV side | R(W) | 1 | 0=Disabled;1=Enabled
12263 | DIF1:LV side Starpoint meas. | R(W) | 1 | 0=I01;1=I02
12264 | DIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
12265 | DIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
12266 | DIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
12267 | DIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
12268 | DIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
12269 | DIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
12270 | DIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
12271 | DIF1:Differential calculation mode | R(W) | 1 | 0=Subtract;1=Add
12272 | DIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12273 | DIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12274 | DIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12275 | DIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12276 | DIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12277 | DIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12278 | DIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12279 | DIF1:Bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12280 | DIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12281 |  |  |  | HR12280 (Lo-16bits)
12282 | DIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12283 |  |  |  | HR12282 (Lo-16bits)
12284 | DIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12285 |  |  |  | HR12284 (Lo-16bits)
12286 | DIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12287 |  |  |  | HR12286 (Lo-16bits)
12288 | DIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12289 |  |  |  | HR12288 (Lo-16bits)
12290 | DIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12291 |  |  |  | HR12290 (Lo-16bits)
12292 | DIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12293 |  |  |  | HR12292 (Lo-16bits)
12294 | DIF1:Idb> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12295 |  |  |  | HR12294 (Lo-16bits)
12296 | DIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12297 |  |  |  | HR12296 (Lo-16bits)
12298 | DIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12299 |  |  |  | HR12298 (Lo-16bits)
12300 | DIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12301 |  |  |  | HR12300 (Lo-16bits)
12302 | DIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12303 |  |  |  | HR12302 (Lo-16bits)
12304 | DIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12305 |  |  |  | HR12304 (Lo-16bits)
12306 | DIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12307 |  |  |  | HR12306 (Lo-16bits)
12308 | DIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12309 |  |  |  | HR12308 (Lo-16bits)
12310 | DIF1:Idb> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12311 |  |  |  | HR12310 (Lo-16bits)
12312 | DIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12313 |  |  |  | HR12312 (Lo-16bits)
12314 | DIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12315 |  |  |  | HR12314 (Lo-16bits)
12316 | DIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12317 |  |  |  | HR12316 (Lo-16bits)
12318 | DIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12319 |  |  |  | HR12318 (Lo-16bits)
12320 | DIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12321 |  |  |  | HR12320 (Lo-16bits)
12322 | DIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12323 |  |  |  | HR12322 (Lo-16bits)
12324 | DIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12325 |  |  |  | HR12324 (Lo-16bits)
12326 | DIF1:Idb> Slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12327 |  |  |  | HR12326 (Lo-16bits)
12328 | DIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12329 |  |  |  | HR12328 (Lo-16bits)
12330 | DIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12331 |  |  |  | HR12330 (Lo-16bits)
12332 | DIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12333 |  |  |  | HR12332 (Lo-16bits)
12334 | DIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12335 |  |  |  | HR12334 (Lo-16bits)
12336 | DIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12337 |  |  |  | HR12336 (Lo-16bits)
12338 | DIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12339 |  |  |  | HR12338 (Lo-16bits)
12340 | DIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12341 |  |  |  | HR12340 (Lo-16bits)
12342 | DIF1:Idb> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12343 |  |  |  | HR12342 (Lo-16bits)
12344 | DIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12345 |  |  |  | HR12344 (Lo-16bits)
12346 | DIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12347 |  |  |  | HR12346 (Lo-16bits)
12348 | DIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12349 |  |  |  | HR12348 (Lo-16bits)
12350 | DIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12351 |  |  |  | HR12350 (Lo-16bits)
12352 | DIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12353 |  |  |  | HR12352 (Lo-16bits)
12354 | DIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12355 |  |  |  | HR12354 (Lo-16bits)
12356 | DIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12357 |  |  |  | HR12356 (Lo-16bits)
12358 | DIF1:Idb> Slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12359 |  |  |  | HR12358 (Lo-16bits)
12360 | DIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12361 | DIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12362 | DIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12363 | DIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12364 | DIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12365 | DIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12366 | DIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12367 | DIF1:Enable harmonic blocking | R(W) | 1 | 0=No harmonic blocking;1=2nd. harm.block.;2=5th.harm.block.;3=2nd.and 5th.harm.block
12368 | DIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12369 |  |  |  | HR12368 (Lo-16bits)
12370 | DIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12371 |  |  |  | HR12370 (Lo-16bits)
12372 | DIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12373 |  |  |  | HR12372 (Lo-16bits)
12374 | DIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12375 |  |  |  | HR12374 (Lo-16bits)
12376 | DIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12377 |  |  |  | HR12376 (Lo-16bits)
12378 | DIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12379 |  |  |  | HR12378 (Lo-16bits)
12380 | DIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12381 |  |  |  | HR12380 (Lo-16bits)
12382 | DIF1:2nd harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12383 |  |  |  | HR12382 (Lo-16bits)
12384 | DIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12385 |  |  |  | HR12384 (Lo-16bits)
12386 | DIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12387 |  |  |  | HR12386 (Lo-16bits)
12388 | DIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12389 |  |  |  | HR12388 (Lo-16bits)
12390 | DIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12391 |  |  |  | HR12390 (Lo-16bits)
12392 | DIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12393 |  |  |  | HR12392 (Lo-16bits)
12394 | DIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12395 |  |  |  | HR12394 (Lo-16bits)
12396 | DIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12397 |  |  |  | HR12396 (Lo-16bits)
12398 | DIF1:5th harm block Pickup | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12399 |  |  |  | HR12398 (Lo-16bits)
12400 | DIF1:5th harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
12401 |  |  |  | HR12400 (Lo-16bits)
12402 | DIF1:5th harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
12403 |  |  |  | HR12402 (Lo-16bits)
12404 | DIF1:5th harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
12405 |  |  |  | HR12404 (Lo-16bits)
12406 | DIF1:5th harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
12407 |  |  |  | HR12406 (Lo-16bits)
12408 | DIF1:5th harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
12409 |  |  |  | HR12408 (Lo-16bits)
12410 | DIF1:5th harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
12411 |  |  |  | HR12410 (Lo-16bits)
12412 | DIF1:5th harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
12413 |  |  |  | HR12412 (Lo-16bits)
12414 | DIF1:5th harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
12415 |  |  |  | HR12414 (Lo-16bits)
12416 | DIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12417 | DIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12418 | DIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12419 | DIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12420 | DIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12421 | DIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12422 | DIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12423 | DIF1:Enable Idi> stage (nonbias) | R(W) | 1 | 0=Disabled;1=Enabled
12424 | DIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12425 |  |  |  | HR12424 (Lo-16bits)
12426 | DIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12427 |  |  |  | HR12426 (Lo-16bits)
12428 | DIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12429 |  |  |  | HR12428 (Lo-16bits)
12430 | DIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12431 |  |  |  | HR12430 (Lo-16bits)
12432 | DIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12433 |  |  |  | HR12432 (Lo-16bits)
12434 | DIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12435 |  |  |  | HR12434 (Lo-16bits)
12436 | DIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12437 |  |  |  | HR12436 (Lo-16bits)
12438 | DIF1:Idi> No bias Pickup | R(W) | 2 | FLOAT [200...1500] (Hi-16bits)
12439 |  |  |  | HR12438 (Lo-16bits)
12440 | DIF1:HV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12441 | DIF1:HV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12442 | DIF1:HV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12443 | DIF1:HV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12444 | DIF1:HV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12445 | DIF1:HV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12446 | DIF1:HV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12447 | DIF1:HV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12448 | DIF1:HV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12449 | DIF1:HV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12450 | DIF1:HV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12451 | DIF1:HV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12452 | DIF1:HV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12453 | DIF1:HV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12454 | DIF1:HV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12455 | DIF1:HV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12456 | DIF1:HV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12457 |  |  |  | HR12456 (Lo-16bits)
12458 | DIF1:HV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12459 |  |  |  | HR12458 (Lo-16bits)
12460 | DIF1:HV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12461 |  |  |  | HR12460 (Lo-16bits)
12462 | DIF1:HV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12463 |  |  |  | HR12462 (Lo-16bits)
12464 | DIF1:HV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12465 |  |  |  | HR12464 (Lo-16bits)
12466 | DIF1:HV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12467 |  |  |  | HR12466 (Lo-16bits)
12468 | DIF1:HV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12469 |  |  |  | HR12468 (Lo-16bits)
12470 | DIF1:HV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12471 |  |  |  | HR12470 (Lo-16bits)
12472 | DIF1:HV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12473 |  |  |  | HR12472 (Lo-16bits)
12474 | DIF1:HV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12475 |  |  |  | HR12474 (Lo-16bits)
12476 | DIF1:HV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12477 |  |  |  | HR12476 (Lo-16bits)
12478 | DIF1:HV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12479 |  |  |  | HR12478 (Lo-16bits)
12480 | DIF1:HV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12481 |  |  |  | HR12480 (Lo-16bits)
12482 | DIF1:HV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12483 |  |  |  | HR12482 (Lo-16bits)
12484 | DIF1:HV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12485 |  |  |  | HR12484 (Lo-16bits)
12486 | DIF1:HV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12487 |  |  |  | HR12486 (Lo-16bits)
12488 | DIF1:HV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12489 |  |  |  | HR12488 (Lo-16bits)
12490 | DIF1:HV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12491 |  |  |  | HR12490 (Lo-16bits)
12492 | DIF1:HV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12493 |  |  |  | HR12492 (Lo-16bits)
12494 | DIF1:HV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12495 |  |  |  | HR12494 (Lo-16bits)
12496 | DIF1:HV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12497 |  |  |  | HR12496 (Lo-16bits)
12498 | DIF1:HV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12499 |  |  |  | HR12498 (Lo-16bits)
12500 | DIF1:HV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12501 |  |  |  | HR12500 (Lo-16bits)
12502 | DIF1:HV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12503 |  |  |  | HR12502 (Lo-16bits)
12504 | DIF1:HV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12505 |  |  |  | HR12504 (Lo-16bits)
12506 | DIF1:HV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12507 |  |  |  | HR12506 (Lo-16bits)
12508 | DIF1:HV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12509 |  |  |  | HR12508 (Lo-16bits)
12510 | DIF1:HV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12511 |  |  |  | HR12510 (Lo-16bits)
12512 | DIF1:HV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12513 |  |  |  | HR12512 (Lo-16bits)
12514 | DIF1:HV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12515 |  |  |  | HR12514 (Lo-16bits)
12516 | DIF1:HV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12517 |  |  |  | HR12516 (Lo-16bits)
12518 | DIF1:HV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12519 |  |  |  | HR12518 (Lo-16bits)
12520 | DIF1:HV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12521 |  |  |  | HR12520 (Lo-16bits)
12522 | DIF1:HV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12523 |  |  |  | HR12522 (Lo-16bits)
12524 | DIF1:HV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12525 |  |  |  | HR12524 (Lo-16bits)
12526 | DIF1:HV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12527 |  |  |  | HR12526 (Lo-16bits)
12528 | DIF1:HV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12529 |  |  |  | HR12528 (Lo-16bits)
12530 | DIF1:HV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12531 |  |  |  | HR12530 (Lo-16bits)
12532 | DIF1:HV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12533 |  |  |  | HR12532 (Lo-16bits)
12534 | DIF1:HV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12535 |  |  |  | HR12534 (Lo-16bits)
12536 | DIF1:LV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12537 | DIF1:LV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12538 | DIF1:LV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12539 | DIF1:LV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12540 | DIF1:LV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12541 | DIF1:LV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12542 | DIF1:LV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12543 | DIF1:LV REF diff calculation mode | R(W) | 1 | 0=Add;1=Subtract
12544 | DIF1:LV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12545 | DIF1:LV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12546 | DIF1:LV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12547 | DIF1:LV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12548 | DIF1:LV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12549 | DIF1:LV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12550 | DIF1:LV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12551 | DIF1:LV REF bias calculation mode | R(W) | 1 | 0=Average;1=Maximum
12552 | DIF1:LV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12553 |  |  |  | HR12552 (Lo-16bits)
12554 | DIF1:LV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12555 |  |  |  | HR12554 (Lo-16bits)
12556 | DIF1:LV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12557 |  |  |  | HR12556 (Lo-16bits)
12558 | DIF1:LV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12559 |  |  |  | HR12558 (Lo-16bits)
12560 | DIF1:LV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12561 |  |  |  | HR12560 (Lo-16bits)
12562 | DIF1:LV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12563 |  |  |  | HR12562 (Lo-16bits)
12564 | DIF1:LV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12565 |  |  |  | HR12564 (Lo-16bits)
12566 | DIF1:LV I0d> Pickup | R(W) | 2 | FLOAT [0.01...100] (Hi-16bits)
12567 |  |  |  | HR12566 (Lo-16bits)
12568 | DIF1:LV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12569 |  |  |  | HR12568 (Lo-16bits)
12570 | DIF1:LV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12571 |  |  |  | HR12570 (Lo-16bits)
12572 | DIF1:LV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12573 |  |  |  | HR12572 (Lo-16bits)
12574 | DIF1:LV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12575 |  |  |  | HR12574 (Lo-16bits)
12576 | DIF1:LV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12577 |  |  |  | HR12576 (Lo-16bits)
12578 | DIF1:LV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12579 |  |  |  | HR12578 (Lo-16bits)
12580 | DIF1:LV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12581 |  |  |  | HR12580 (Lo-16bits)
12582 | DIF1:LV I0d> Turnpoint 1 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12583 |  |  |  | HR12582 (Lo-16bits)
12584 | DIF1:LV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12585 |  |  |  | HR12584 (Lo-16bits)
12586 | DIF1:LV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12587 |  |  |  | HR12586 (Lo-16bits)
12588 | DIF1:LV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12589 |  |  |  | HR12588 (Lo-16bits)
12590 | DIF1:LV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12591 |  |  |  | HR12590 (Lo-16bits)
12592 | DIF1:LV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12593 |  |  |  | HR12592 (Lo-16bits)
12594 | DIF1:LV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12595 |  |  |  | HR12594 (Lo-16bits)
12596 | DIF1:LV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12597 |  |  |  | HR12596 (Lo-16bits)
12598 | DIF1:LV I0d> slope 1 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12599 |  |  |  | HR12598 (Lo-16bits)
12600 | DIF1:LV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12601 |  |  |  | HR12600 (Lo-16bits)
12602 | DIF1:LV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12603 |  |  |  | HR12602 (Lo-16bits)
12604 | DIF1:LV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12605 |  |  |  | HR12604 (Lo-16bits)
12606 | DIF1:LV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12607 |  |  |  | HR12606 (Lo-16bits)
12608 | DIF1:LV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12609 |  |  |  | HR12608 (Lo-16bits)
12610 | DIF1:LV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12611 |  |  |  | HR12610 (Lo-16bits)
12612 | DIF1:LV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12613 |  |  |  | HR12612 (Lo-16bits)
12614 | DIF1:LV I0d> Turnpoint 2 | R(W) | 2 | FLOAT [0.01...50] (Hi-16bits)
12615 |  |  |  | HR12614 (Lo-16bits)
12616 | DIF1:LV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12617 |  |  |  | HR12616 (Lo-16bits)
12618 | DIF1:LV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12619 |  |  |  | HR12618 (Lo-16bits)
12620 | DIF1:LV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12621 |  |  |  | HR12620 (Lo-16bits)
12622 | DIF1:LV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12623 |  |  |  | HR12622 (Lo-16bits)
12624 | DIF1:LV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12625 |  |  |  | HR12624 (Lo-16bits)
12626 | DIF1:LV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12627 |  |  |  | HR12626 (Lo-16bits)
12628 | DIF1:LV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12629 |  |  |  | HR12628 (Lo-16bits)
12630 | DIF1:LV I0d> slope 2 | R(W) | 2 | FLOAT [0.01...250] (Hi-16bits)
12631 |  |  |  | HR12630 (Lo-16bits)
12632 | TOLM1:TM> Current measurement side | R(W) | 1 | 0=CT1;1=CT2
12633 | TOLM1:Pick-up current (x In) | R(W) | 2 | FLOAT [0...40] (Hi-16bits)
12634 |  |  |  | HR12633 (Lo-16bits)
12635 | TOLM1:NPS Bias factor | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
12636 |  |  |  | HR12635 (Lo-16bits)
12637 | TOLM1:Thermal operation mode | R(W) | 1 | 2=Original;3=Wizard model
12638 | TOLM1:Thermal curve selector | R(W) | 1 | 0=I^2 curve;1=Water cooled;2=NEMA
12639 | TOLM1:NEMA Trip class | R(W) | 1 | 0=Class 5;1=Class 10;2=Class 20;3=Class 30
12640 | TOLM1:Long Heat T const (cold) | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
12641 |  |  |  | HR12640 (Lo-16bits)
12642 | TOLM1:Long Heat T const (hot) | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
12643 |  |  |  | HR12642 (Lo-16bits)
12644 | TOLM1:Long Cool T const Run | R(W) | 2 | FLOAT [0...3000] (Hi-16bits)
12645 |  |  |  | HR12644 (Lo-16bits)
12646 | TOLM1:Long Cool T const Stop | R(W) | 2 | FLOAT [0...3000] (Hi-16bits)
12647 |  |  |  | HR12646 (Lo-16bits)
12648 | TOLM1:Short Heat T const (cold) | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
12649 |  |  |  | HR12648 (Lo-16bits)
12650 | TOLM1:Short Heat T const (cold)est | R | 2 | FLOAT [0...500] (Hi-16bits)
12651 |  |  |  | HR12650 (Lo-16bits)
12652 | TOLM1:Short Heat T const (hot) | R(W) | 2 | FLOAT [0...500] (Hi-16bits)
12653 |  |  |  | HR12652 (Lo-16bits)
12654 | TOLM1:Short Heat T const (hot)est | R | 2 | FLOAT [0...500] (Hi-16bits)
12655 |  |  |  | HR12654 (Lo-16bits)
12656 | TOLM1:Short Cool T const | R(W) | 2 | FLOAT [0...3000] (Hi-16bits)
12657 |  |  |  | HR12656 (Lo-16bits)
12658 | TOLM1:Short Cool T const (est) | R | 2 | FLOAT [0...500] (Hi-16bits)
12659 |  |  |  | HR12658 (Lo-16bits)
12660 | TOLM1:Wf factor for L/S T const | R(W) | 2 | FLOAT [0...1] (Hi-16bits)
12661 |  |  |  | HR12660 (Lo-16bits)
12662 | TOLM1:Enable TM> Alarm1 | R(W) | 1 | 0=Disabled;1=Enabled
12663 | TOLM1:Enable TM> Alarm1 | R(W) | 1 | 0=Disabled;1=Enabled
12664 | TOLM1:Enable TM> Alarm1 | R(W) | 1 | 0=Disabled;1=Enabled
12665 | TOLM1:Enable TM> Alarm1 | R(W) | 1 | 0=Disabled;1=Enabled
12666 | TOLM1:Enable TM> Alarm1 | R(W) | 1 | 0=Disabled;1=Enabled
12667 | TOLM1:Enable TM> Alarm1 | R(W) | 1 | 0=Disabled;1=Enabled
12668 | TOLM1:Enable TM> Alarm1 | R(W) | 1 | 0=Disabled;1=Enabled
12669 | TOLM1:Enable TM> Alarm1 | R(W) | 1 | 0=Disabled;1=Enabled
12670 | TOLM1:TM> Alarm1 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12671 |  |  |  | HR12670 (Lo-16bits)
12672 | TOLM1:TM> Alarm1 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12673 |  |  |  | HR12672 (Lo-16bits)
12674 | TOLM1:TM> Alarm1 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12675 |  |  |  | HR12674 (Lo-16bits)
12676 | TOLM1:TM> Alarm1 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12677 |  |  |  | HR12676 (Lo-16bits)
12678 | TOLM1:TM> Alarm1 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12679 |  |  |  | HR12678 (Lo-16bits)
12680 | TOLM1:TM> Alarm1 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12681 |  |  |  | HR12680 (Lo-16bits)
12682 | TOLM1:TM> Alarm1 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12683 |  |  |  | HR12682 (Lo-16bits)
12684 | TOLM1:TM> Alarm1 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12685 |  |  |  | HR12684 (Lo-16bits)
12686 | TOLM1:Enable TM> Alarm2 | R(W) | 1 | 0=Disabled;1=Enabled
12687 | TOLM1:Enable TM> Alarm2 | R(W) | 1 | 0=Disabled;1=Enabled
12688 | TOLM1:Enable TM> Alarm2 | R(W) | 1 | 0=Disabled;1=Enabled
12689 | TOLM1:Enable TM> Alarm2 | R(W) | 1 | 0=Disabled;1=Enabled
12690 | TOLM1:Enable TM> Alarm2 | R(W) | 1 | 0=Disabled;1=Enabled
12691 | TOLM1:Enable TM> Alarm2 | R(W) | 1 | 0=Disabled;1=Enabled
12692 | TOLM1:Enable TM> Alarm2 | R(W) | 1 | 0=Disabled;1=Enabled
12693 | TOLM1:Enable TM> Alarm2 | R(W) | 1 | 0=Disabled;1=Enabled
12694 | TOLM1:TM> Alarm2 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12695 |  |  |  | HR12694 (Lo-16bits)
12696 | TOLM1:TM> Alarm2 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12697 |  |  |  | HR12696 (Lo-16bits)
12698 | TOLM1:TM> Alarm2 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12699 |  |  |  | HR12698 (Lo-16bits)
12700 | TOLM1:TM> Alarm2 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12701 |  |  |  | HR12700 (Lo-16bits)
12702 | TOLM1:TM> Alarm2 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12703 |  |  |  | HR12702 (Lo-16bits)
12704 | TOLM1:TM> Alarm2 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12705 |  |  |  | HR12704 (Lo-16bits)
12706 | TOLM1:TM> Alarm2 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12707 |  |  |  | HR12706 (Lo-16bits)
12708 | TOLM1:TM> Alarm2 level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12709 |  |  |  | HR12708 (Lo-16bits)
12710 | TOLM1:Enable TM> Rest Inhibit | R(W) | 1 | 0=Disabled;1=Enabled
12711 | TOLM1:Enable TM> Rest Inhibit | R(W) | 1 | 0=Disabled;1=Enabled
12712 | TOLM1:Enable TM> Rest Inhibit | R(W) | 1 | 0=Disabled;1=Enabled
12713 | TOLM1:Enable TM> Rest Inhibit | R(W) | 1 | 0=Disabled;1=Enabled
12714 | TOLM1:Enable TM> Rest Inhibit | R(W) | 1 | 0=Disabled;1=Enabled
12715 | TOLM1:Enable TM> Rest Inhibit | R(W) | 1 | 0=Disabled;1=Enabled
12716 | TOLM1:Enable TM> Rest Inhibit | R(W) | 1 | 0=Disabled;1=Enabled
12717 | TOLM1:Enable TM> Rest Inhibit | R(W) | 1 | 0=Disabled;1=Enabled
12718 | TOLM1:TM> Inhibit level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12719 |  |  |  | HR12718 (Lo-16bits)
12720 | TOLM1:TM> Inhibit level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12721 |  |  |  | HR12720 (Lo-16bits)
12722 | TOLM1:TM> Inhibit level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12723 |  |  |  | HR12722 (Lo-16bits)
12724 | TOLM1:TM> Inhibit level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12725 |  |  |  | HR12724 (Lo-16bits)
12726 | TOLM1:TM> Inhibit level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12727 |  |  |  | HR12726 (Lo-16bits)
12728 | TOLM1:TM> Inhibit level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12729 |  |  |  | HR12728 (Lo-16bits)
12730 | TOLM1:TM> Inhibit level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12731 |  |  |  | HR12730 (Lo-16bits)
12732 | TOLM1:TM> Inhibit level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12733 |  |  |  | HR12732 (Lo-16bits)
12734 | TOLM1:TM> Trip level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12735 |  |  |  | HR12734 (Lo-16bits)
12736 | TOLM1:TM> Trip level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12737 |  |  |  | HR12736 (Lo-16bits)
12738 | TOLM1:TM> Trip level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12739 |  |  |  | HR12738 (Lo-16bits)
12740 | TOLM1:TM> Trip level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12741 |  |  |  | HR12740 (Lo-16bits)
12742 | TOLM1:TM> Trip level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12743 |  |  |  | HR12742 (Lo-16bits)
12744 | TOLM1:TM> Trip level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12745 |  |  |  | HR12744 (Lo-16bits)
12746 | TOLM1:TM> Trip level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12747 |  |  |  | HR12746 (Lo-16bits)
12748 | TOLM1:TM> Trip level | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
12749 |  |  |  | HR12748 (Lo-16bits)
12750 | TOLM1:TM> Trip delay | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12751 |  |  |  | HR12750 (Lo-16bits)
12752 | TOLM1:TM> Trip delay | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12753 |  |  |  | HR12752 (Lo-16bits)
12754 | TOLM1:TM> Trip delay | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12755 |  |  |  | HR12754 (Lo-16bits)
12756 | TOLM1:TM> Trip delay | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12757 |  |  |  | HR12756 (Lo-16bits)
12758 | TOLM1:TM> Trip delay | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12759 |  |  |  | HR12758 (Lo-16bits)
12760 | TOLM1:TM> Trip delay | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12761 |  |  |  | HR12760 (Lo-16bits)
12762 | TOLM1:TM> Trip delay | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12763 |  |  |  | HR12762 (Lo-16bits)
12764 | TOLM1:TM> Trip delay | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12765 |  |  |  | HR12764 (Lo-16bits)
12766 | LCR1:ISt> measurement side | R(W) | 1 | 0=CT1;1=CT2
12767 | LCR1:Starting time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12768 |  |  |  | HR12767 (Lo-16bits)
12769 | LCR1:Starting time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12770 |  |  |  | HR12769 (Lo-16bits)
12771 | LCR1:Starting time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12772 |  |  |  | HR12771 (Lo-16bits)
12773 | LCR1:Starting time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12774 |  |  |  | HR12773 (Lo-16bits)
12775 | LCR1:Starting time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12776 |  |  |  | HR12775 (Lo-16bits)
12777 | LCR1:Starting time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12778 |  |  |  | HR12777 (Lo-16bits)
12779 | LCR1:Starting time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12780 |  |  |  | HR12779 (Lo-16bits)
12781 | LCR1:Starting time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12782 |  |  |  | HR12781 (Lo-16bits)
12783 | LCR1:Definite time or I2t | R(W) | 1 | 0=Definite;1=I2T mode
12784 | LCR1:Definite time or I2t | R(W) | 1 | 0=Definite;1=I2T mode
12785 | LCR1:Definite time or I2t | R(W) | 1 | 0=Definite;1=I2T mode
12786 | LCR1:Definite time or I2t | R(W) | 1 | 0=Definite;1=I2T mode
12787 | LCR1:Definite time or I2t | R(W) | 1 | 0=Definite;1=I2T mode
12788 | LCR1:Definite time or I2t | R(W) | 1 | 0=Definite;1=I2T mode
12789 | LCR1:Definite time or I2t | R(W) | 1 | 0=Definite;1=I2T mode
12790 | LCR1:Definite time or I2t | R(W) | 1 | 0=Definite;1=I2T mode
12791 | LCR1:Speed Switch in use | R(W) | 1 | 0=No;1=Yes
12792 | LCR1:Speed Switch in use | R(W) | 1 | 0=No;1=Yes
12793 | LCR1:Speed Switch in use | R(W) | 1 | 0=No;1=Yes
12794 | LCR1:Speed Switch in use | R(W) | 1 | 0=No;1=Yes
12795 | LCR1:Speed Switch in use | R(W) | 1 | 0=No;1=Yes
12796 | LCR1:Speed Switch in use | R(W) | 1 | 0=No;1=Yes
12797 | LCR1:Speed Switch in use | R(W) | 1 | 0=No;1=Yes
12798 | LCR1:Speed Switch in use | R(W) | 1 | 0=No;1=Yes
12799 | LCR1:Speed SW wait time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12800 |  |  |  | HR12799 (Lo-16bits)
12801 | LCR1:Speed SW wait time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12802 |  |  |  | HR12801 (Lo-16bits)
12803 | LCR1:Speed SW wait time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12804 |  |  |  | HR12803 (Lo-16bits)
12805 | LCR1:Speed SW wait time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12806 |  |  |  | HR12805 (Lo-16bits)
12807 | LCR1:Speed SW wait time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12808 |  |  |  | HR12807 (Lo-16bits)
12809 | LCR1:Speed SW wait time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12810 |  |  |  | HR12809 (Lo-16bits)
12811 | LCR1:Speed SW wait time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12812 |  |  |  | HR12811 (Lo-16bits)
12813 | LCR1:Speed SW wait time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12814 |  |  |  | HR12813 (Lo-16bits)
12815 | LCR1:Speed SW NO/NC | R(W) | 1 | 0=NO;1=NC
12816 | LCR1:Speed SW NO/NC | R(W) | 1 | 0=NO;1=NC
12817 | LCR1:Speed SW NO/NC | R(W) | 1 | 0=NO;1=NC
12818 | LCR1:Speed SW NO/NC | R(W) | 1 | 0=NO;1=NC
12819 | LCR1:Speed SW NO/NC | R(W) | 1 | 0=NO;1=NC
12820 | LCR1:Speed SW NO/NC | R(W) | 1 | 0=NO;1=NC
12821 | LCR1:Speed SW NO/NC | R(W) | 1 | 0=NO;1=NC
12822 | LCR1:Speed SW NO/NC | R(W) | 1 | 0=NO;1=NC
12823 | LCR1:Operate mode | R(W) | 1 | 0=Starts only;1=Starts and stall
12824 | LCR1:Operate mode | R(W) | 1 | 0=Starts only;1=Starts and stall
12825 | LCR1:Operate mode | R(W) | 1 | 0=Starts only;1=Starts and stall
12826 | LCR1:Operate mode | R(W) | 1 | 0=Starts only;1=Starts and stall
12827 | LCR1:Operate mode | R(W) | 1 | 0=Starts only;1=Starts and stall
12828 | LCR1:Operate mode | R(W) | 1 | 0=Starts only;1=Starts and stall
12829 | LCR1:Operate mode | R(W) | 1 | 0=Starts only;1=Starts and stall
12830 | LCR1:Operate mode | R(W) | 1 | 0=Starts only;1=Starts and stall
12831 | FSP1:N> Configuration | R(W) | 1 | 0=MotorDatabased;1=Usersettiming
12832 | FSP1:Time delay for start counting | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12833 |  |  |  | HR12832 (Lo-16bits)
12834 | FSP1:Time delay for restart inhibition | R(W) | 2 | FLOAT [0...3600] (Hi-16bits)
12835 |  |  |  | HR12834 (Lo-16bits)
12836 | SYN1:System voltages are measured on | R(W) | 1 | 0=Bus, Line is reference;1=Line, Bus is reference
12837 | SYN1:Use SYN1 | R(W) | 1 | 0=No;1=Yes
12838 | SYN1:SYN1 Start check | R(W) | 1 | 0=Always;1=On input
12839 | SYN1:SYN1 V Reference | R(W) | 1 | 0=Not in use;1=UL12;2=UL23;3=UL31;4=UL1;5=UL2;6=UL3
12840 | SYN1:SYN1 Switching | R(W) | 1 | 0=Not in use;1=Use SynSW
12841 | SYN1:SYN1 Switch bk time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12842 |  |  |  | HR12841 (Lo-16bits)
12843 | SYN1:SYN1 Switching Object | R(W) | 1 | 0=Object 1;1=Object2;2=Object3;3=Object4;4=Object5
12844 | SYN1:Use SYN2 | R(W) | 1 | 0=No;1=Yes
12845 | SYN1:SYN1 U conditions | R(W) | 1 | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
12846 | SYN1:SYN1 U conditions | R(W) | 1 | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
12847 | SYN1:SYN1 U conditions | R(W) | 1 | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
12848 | SYN1:SYN1 U conditions | R(W) | 1 | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
12849 | SYN1:SYN1 U conditions | R(W) | 1 | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
12850 | SYN1:SYN1 U conditions | R(W) | 1 | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
12851 | SYN1:SYN1 U conditions | R(W) | 1 | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
12852 | SYN1:SYN1 U conditions | R(W) | 1 | 0=LL only;1=LD only;2=DL only;3=LL & LD;4=LL & DL;5=LL & DD;6=LL & LD & DL;7=LL & LD & DD;8=LL & DL & DD;9=Bypass;12=LL & DL & LD & DD
12853 | SYN1:SYN1 U Gen > | R(W) | 2 | FLOAT [20...105] (Hi-16bits)
12854 |  |  |  | HR12853 (Lo-16bits)
12855 | SYN1:SYN1 U Gen > | R(W) | 2 | FLOAT [20...105] (Hi-16bits)
12856 |  |  |  | HR12855 (Lo-16bits)
12857 | SYN1:SYN1 U Gen > | R(W) | 2 | FLOAT [20...105] (Hi-16bits)
12858 |  |  |  | HR12857 (Lo-16bits)
12859 | SYN1:SYN1 U Gen > | R(W) | 2 | FLOAT [20...105] (Hi-16bits)
12860 |  |  |  | HR12859 (Lo-16bits)
12861 | SYN1:SYN1 U Gen > | R(W) | 2 | FLOAT [20...105] (Hi-16bits)
12862 |  |  |  | HR12861 (Lo-16bits)
12863 | SYN1:SYN1 U Gen > | R(W) | 2 | FLOAT [20...105] (Hi-16bits)
12864 |  |  |  | HR12863 (Lo-16bits)
12865 | SYN1:SYN1 U Gen > | R(W) | 2 | FLOAT [20...105] (Hi-16bits)
12866 |  |  |  | HR12865 (Lo-16bits)
12867 | SYN1:SYN1 U Gen > | R(W) | 2 | FLOAT [20...105] (Hi-16bits)
12868 |  |  |  | HR12867 (Lo-16bits)
12869 | SYN1:SYN1 U Gen < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12870 |  |  |  | HR12869 (Lo-16bits)
12871 | SYN1:SYN1 U Gen < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12872 |  |  |  | HR12871 (Lo-16bits)
12873 | SYN1:SYN1 U Gen < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12874 |  |  |  | HR12873 (Lo-16bits)
12875 | SYN1:SYN1 U Gen < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12876 |  |  |  | HR12875 (Lo-16bits)
12877 | SYN1:SYN1 U Gen < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12878 |  |  |  | HR12877 (Lo-16bits)
12879 | SYN1:SYN1 U Gen < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12880 |  |  |  | HR12879 (Lo-16bits)
12881 | SYN1:SYN1 U Gen < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12882 |  |  |  | HR12881 (Lo-16bits)
12883 | SYN1:SYN1 U Gen < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12884 |  |  |  | HR12883 (Lo-16bits)
12885 | SYN1:SYN1 U Bus < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12886 |  |  |  | HR12885 (Lo-16bits)
12887 | SYN1:SYN1 U Bus < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12888 |  |  |  | HR12887 (Lo-16bits)
12889 | SYN1:SYN1 U Bus < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12890 |  |  |  | HR12889 (Lo-16bits)
12891 | SYN1:SYN1 U Bus < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12892 |  |  |  | HR12891 (Lo-16bits)
12893 | SYN1:SYN1 U Bus < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12894 |  |  |  | HR12893 (Lo-16bits)
12895 | SYN1:SYN1 U Bus < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12896 |  |  |  | HR12895 (Lo-16bits)
12897 | SYN1:SYN1 U Bus < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12898 |  |  |  | HR12897 (Lo-16bits)
12899 | SYN1:SYN1 U Bus < | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
12900 |  |  |  | HR12899 (Lo-16bits)
12901 | SYN1:SYN1 f Gen > | R(W) | 2 | FLOAT [98...102] (Hi-16bits)
12902 |  |  |  | HR12901 (Lo-16bits)
12903 | SYN1:SYN1 f Gen > | R(W) | 2 | FLOAT [98...102] (Hi-16bits)
12904 |  |  |  | HR12903 (Lo-16bits)
12905 | SYN1:SYN1 f Gen > | R(W) | 2 | FLOAT [98...102] (Hi-16bits)
12906 |  |  |  | HR12905 (Lo-16bits)
12907 | SYN1:SYN1 f Gen > | R(W) | 2 | FLOAT [98...102] (Hi-16bits)
12908 |  |  |  | HR12907 (Lo-16bits)
12909 | SYN1:SYN1 f Gen > | R(W) | 2 | FLOAT [98...102] (Hi-16bits)
12910 |  |  |  | HR12909 (Lo-16bits)
12911 | SYN1:SYN1 f Gen > | R(W) | 2 | FLOAT [98...102] (Hi-16bits)
12912 |  |  |  | HR12911 (Lo-16bits)
12913 | SYN1:SYN1 f Gen > | R(W) | 2 | FLOAT [98...102] (Hi-16bits)
12914 |  |  |  | HR12913 (Lo-16bits)
12915 | SYN1:SYN1 f Gen > | R(W) | 2 | FLOAT [98...102] (Hi-16bits)
12916 |  |  |  | HR12915 (Lo-16bits)
12917 | SYN1:SYN1 Synchro check start time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12918 |  |  |  | HR12917 (Lo-16bits)
12919 | SYN1:SYN1 Synchro check start time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12920 |  |  |  | HR12919 (Lo-16bits)
12921 | SYN1:SYN1 Synchro check start time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12922 |  |  |  | HR12921 (Lo-16bits)
12923 | SYN1:SYN1 Synchro check start time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12924 |  |  |  | HR12923 (Lo-16bits)
12925 | SYN1:SYN1 Synchro check start time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12926 |  |  |  | HR12925 (Lo-16bits)
12927 | SYN1:SYN1 Synchro check start time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12928 |  |  |  | HR12927 (Lo-16bits)
12929 | SYN1:SYN1 Synchro check start time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12930 |  |  |  | HR12929 (Lo-16bits)
12931 | SYN1:SYN1 Synchro check start time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
12932 |  |  |  | HR12931 (Lo-16bits)
12933 | SYN1:SYN1 U live > | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12934 |  |  |  | HR12933 (Lo-16bits)
12935 | SYN1:SYN1 U live > | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12936 |  |  |  | HR12935 (Lo-16bits)
12937 | SYN1:SYN1 U live > | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12938 |  |  |  | HR12937 (Lo-16bits)
12939 | SYN1:SYN1 U live > | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12940 |  |  |  | HR12939 (Lo-16bits)
12941 | SYN1:SYN1 U live > | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12942 |  |  |  | HR12941 (Lo-16bits)
12943 | SYN1:SYN1 U live > | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12944 |  |  |  | HR12943 (Lo-16bits)
12945 | SYN1:SYN1 U live > | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12946 |  |  |  | HR12945 (Lo-16bits)
12947 | SYN1:SYN1 U live > | R(W) | 2 | FLOAT [0.1...100] (Hi-16bits)
12948 |  |  |  | HR12947 (Lo-16bits)
12949 | SYN1:SYN1 U dead < | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12950 |  |  |  | HR12949 (Lo-16bits)
12951 | SYN1:SYN1 U dead < | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12952 |  |  |  | HR12951 (Lo-16bits)
12953 | SYN1:SYN1 U dead < | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12954 |  |  |  | HR12953 (Lo-16bits)
12955 | SYN1:SYN1 U dead < | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12956 |  |  |  | HR12955 (Lo-16bits)
12957 | SYN1:SYN1 U dead < | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12958 |  |  |  | HR12957 (Lo-16bits)
12959 | SYN1:SYN1 U dead < | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12960 |  |  |  | HR12959 (Lo-16bits)
12961 | SYN1:SYN1 U dead < | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12962 |  |  |  | HR12961 (Lo-16bits)
12963 | SYN1:SYN1 U dead < | R(W) | 2 | FLOAT [0...100] (Hi-16bits)
12964 |  |  |  | HR12963 (Lo-16bits)
12965 | SYN1:SYN1 U diff < | R(W) | 2 | FLOAT [2...50] (Hi-16bits)
12966 |  |  |  | HR12965 (Lo-16bits)
12967 | SYN1:SYN1 U diff < | R(W) | 2 | FLOAT [2...50] (Hi-16bits)
12968 |  |  |  | HR12967 (Lo-16bits)
12969 | SYN1:SYN1 U diff < | R(W) | 2 | FLOAT [2...50] (Hi-16bits)
12970 |  |  |  | HR12969 (Lo-16bits)
12971 | SYN1:SYN1 U diff < | R(W) | 2 | FLOAT [2...50] (Hi-16bits)
12972 |  |  |  | HR12971 (Lo-16bits)
12973 | SYN1:SYN1 U diff < | R(W) | 2 | FLOAT [2...50] (Hi-16bits)
12974 |  |  |  | HR12973 (Lo-16bits)
12975 | SYN1:SYN1 U diff < | R(W) | 2 | FLOAT [2...50] (Hi-16bits)
12976 |  |  |  | HR12975 (Lo-16bits)
12977 | SYN1:SYN1 U diff < | R(W) | 2 | FLOAT [2...50] (Hi-16bits)
12978 |  |  |  | HR12977 (Lo-16bits)
12979 | SYN1:SYN1 U diff < | R(W) | 2 | FLOAT [2...50] (Hi-16bits)
12980 |  |  |  | HR12979 (Lo-16bits)
12981 | SYN1:SYN1 angle diff < | R(W) | 2 | FLOAT [3...90] (Hi-16bits)
12982 |  |  |  | HR12981 (Lo-16bits)
12983 | SYN1:SYN1 angle diff < | R(W) | 2 | FLOAT [3...90] (Hi-16bits)
12984 |  |  |  | HR12983 (Lo-16bits)
12985 | SYN1:SYN1 angle diff < | R(W) | 2 | FLOAT [3...90] (Hi-16bits)
12986 |  |  |  | HR12985 (Lo-16bits)
12987 | SYN1:SYN1 angle diff < | R(W) | 2 | FLOAT [3...90] (Hi-16bits)
12988 |  |  |  | HR12987 (Lo-16bits)
12989 | SYN1:SYN1 angle diff < | R(W) | 2 | FLOAT [3...90] (Hi-16bits)
12990 |  |  |  | HR12989 (Lo-16bits)
12991 | SYN1:SYN1 angle diff < | R(W) | 2 | FLOAT [3...90] (Hi-16bits)
12992 |  |  |  | HR12991 (Lo-16bits)
12993 | SYN1:SYN1 angle diff < | R(W) | 2 | FLOAT [3...90] (Hi-16bits)
12994 |  |  |  | HR12993 (Lo-16bits)
12995 | SYN1:SYN1 angle diff < | R(W) | 2 | FLOAT [3...90] (Hi-16bits)
12996 |  |  |  | HR12995 (Lo-16bits)
12997 | SYN1:SYN1 freq diff < | R(W) | 2 | FLOAT [0.05...0.5] (Hi-16bits)
12998 |  |  |  | HR12997 (Lo-16bits)
12999 | SYN1:SYN1 freq diff < | R(W) | 2 | FLOAT [0.05...0.5] (Hi-16bits)
13000 |  |  |  | HR12999 (Lo-16bits)
13001 | SYN1:SYN1 freq diff < | R(W) | 2 | FLOAT [0.05...0.5] (Hi-16bits)
13002 |  |  |  | HR13001 (Lo-16bits)
13003 | SYN1:SYN1 freq diff < | R(W) | 2 | FLOAT [0.05...0.5] (Hi-16bits)
13004 |  |  |  | HR13003 (Lo-16bits)
13005 | SYN1:SYN1 freq diff < | R(W) | 2 | FLOAT [0.05...0.5] (Hi-16bits)
13006 |  |  |  | HR13005 (Lo-16bits)
13007 | SYN1:SYN1 freq diff < | R(W) | 2 | FLOAT [0.05...0.5] (Hi-16bits)
13008 |  |  |  | HR13007 (Lo-16bits)
13009 | SYN1:SYN1 freq diff < | R(W) | 2 | FLOAT [0.05...0.5] (Hi-16bits)
13010 |  |  |  | HR13009 (Lo-16bits)
13011 | SYN1:SYN1 freq diff < | R(W) | 2 | FLOAT [0.05...0.5] (Hi-16bits)
13012 |  |  |  | HR13011 (Lo-16bits)
13013 | DMA1:POW1 3PH Apparent power (S) demand | R | 2 | FLOAT [0...1000000] (Hi-16bits)
13014 |  |  |  | HR13013 (Lo-16bits)
13015 | DMA1:POW1 3PH Active power (P) demand | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
13016 |  |  |  | HR13015 (Lo-16bits)
13017 | DMA1:POW1 3PH Reactive power (Q) demand | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
13018 |  |  |  | HR13017 (Lo-16bits)
13019 | DMA1:POW1 3PH PF demand | R | 2 | FLOAT [-1.000...1.000] (Hi-16bits)
13020 |  |  |  | HR13019 (Lo-16bits)
13021 | DMA1:IL1 harmonic demand | R | 2 | FLOAT [0...100000] (Hi-16bits)
13022 |  |  |  | HR13021 (Lo-16bits)
13023 | DMA1:IL2 harmonic demand | R | 2 | FLOAT [0...100000] (Hi-16bits)
13024 |  |  |  | HR13023 (Lo-16bits)
13025 | DMA1:IL3 harmonic demand | R | 2 | FLOAT [0...100000] (Hi-16bits)
13026 |  |  |  | HR13025 (Lo-16bits)
13027 | EFX1:Fault direction | R | 1 | 0=Unknown;1=Forward;2=Reverse;3=Undirectional
13028 | EFX1:Genral start to any direction | R | 1 | 0=Normal;1=Start
13029 | EFX1:General trip to any direction | R | 1 | 0=Normal;1=Trip
13030 | CPB1:Capacitor is now | R | 1 | 0=Disconnected Ready;1=Connected;2=Discharging;3=Overvoltage
13031 | DIF1:2nd harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
13032 |  |  |  | HR13031 (Lo-16bits)
13033 | DIF1:2nd harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
13034 |  |  |  | HR13033 (Lo-16bits)
13035 | DIF1:2nd harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
13036 |  |  |  | HR13035 (Lo-16bits)
13037 | DIF1:2nd harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
13038 |  |  |  | HR13037 (Lo-16bits)
13039 | DIF1:2nd harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
13040 |  |  |  | HR13039 (Lo-16bits)
13041 | DIF1:2nd harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
13042 |  |  |  | HR13041 (Lo-16bits)
13043 | DIF1:2nd harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
13044 |  |  |  | HR13043 (Lo-16bits)
13045 | DIF1:2nd harm maximum uptime | R(W) | 2 | FLOAT [0...10] (Hi-16bits)
13046 |  |  |  | HR13045 (Lo-16bits)
13047 | TOLM1:Enable TM> Trip | R(W) | 1 | 0=Disabled;1=Enabled
13048 | TOLM1:Enable TM> Trip | R(W) | 1 | 0=Disabled;1=Enabled
13049 | TOLM1:Enable TM> Trip | R(W) | 1 | 0=Disabled;1=Enabled
13050 | TOLM1:Enable TM> Trip | R(W) | 1 | 0=Disabled;1=Enabled
13051 | TOLM1:Enable TM> Trip | R(W) | 1 | 0=Disabled;1=Enabled
13052 | TOLM1:Enable TM> Trip | R(W) | 1 | 0=Disabled;1=Enabled
13053 | TOLM1:Enable TM> Trip | R(W) | 1 | 0=Disabled;1=Enabled
13054 | TOLM1:Enable TM> Trip | R(W) | 1 | 0=Disabled;1=Enabled
13055 | LPM:Z< [21] mode | R | 1 | 0=Disabled;1=Activated
13056 | ENC:Load encroachment condition | R | 1 | 0=Normal;1=Load encroachment detected
13057 | OOS2:PS&OOS condition | R | 1 | 0=Normal;1=Power Swing blocking;2=Out of step Trip
13058 | DPP1:Z< Z1PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13059 | DPP1:Z< Z1PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13060 |  |  |  | HR13059 (Lo-16bits)
13061 | DPP2:Z< Z2PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13062 | DPP2:Z< Z2PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13063 |  |  |  | HR13062 (Lo-16bits)
13064 | DPP3:Z< Z3PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13065 | DPP3:Z< Z3PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13066 |  |  |  | HR13065 (Lo-16bits)
13067 | DPP4:Z< Z4PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13068 | DPP4:Z< Z4PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13069 |  |  |  | HR13068 (Lo-16bits)
13070 | DPP5:Z< Z5PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13071 | DPP5:Z< Z5PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13072 |  |  |  | HR13071 (Lo-16bits)
13073 | DPP6:Z< Z6PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13074 | DPP6:Z< Z6PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13075 |  |  |  | HR13074 (Lo-16bits)
13076 | DPP7:Z< Z7PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13077 | DPP7:Z< Z7PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13078 |  |  |  | HR13077 (Lo-16bits)
13079 | DPP8:Z< Z8PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13080 | DPP8:Z< Z8PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13081 |  |  |  | HR13080 (Lo-16bits)
13082 | DPP9:Z< Z9PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13083 | DPP9:Z< Z9PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13084 |  |  |  | HR13083 (Lo-16bits)
13085 | DPP10:Z< Z10PP Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13086 | DPP10:Z< Z10PP Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13087 |  |  |  | HR13086 (Lo-16bits)
13088 | DPE1:Z< Z1PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13089 | DPE1:Z< Z1PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13090 |  |  |  | HR13089 (Lo-16bits)
13091 | DPE2:Z< Z2PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13092 | DPE2:Z< Z2PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13093 |  |  |  | HR13092 (Lo-16bits)
13094 | DPE3:Z< Z3PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13095 | DPE3:Z< Z3PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13096 |  |  |  | HR13095 (Lo-16bits)
13097 | DPE4:Z< Z4PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13098 | DPE4:Z< Z4PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13099 |  |  |  | HR13098 (Lo-16bits)
13100 | DPE5:Z< Z5PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13101 | DPE5:Z< Z5PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13102 |  |  |  | HR13101 (Lo-16bits)
13103 | DPE6:Z< Z6PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13104 | DPE6:Z< Z6PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13105 |  |  |  | HR13104 (Lo-16bits)
13106 | DPE7:Z< Z7PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13107 | DPE7:Z< Z7PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13108 |  |  |  | HR13107 (Lo-16bits)
13109 | DPE8:Z< Z8PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13110 | DPE8:Z< Z8PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13111 |  |  |  | HR13110 (Lo-16bits)
13112 | DPE9:Z< Z9PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13113 | DPE9:Z< Z9PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13114 |  |  |  | HR13113 (Lo-16bits)
13115 | DPE10:Z< Z10PE Zone condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
13116 | DPE10:Z< Z10PE Last fault location | R | 2 | FLOAT [-1800.000...1800.000] (Hi-16bits)
13117 |  |  |  | HR13116 (Lo-16bits)
19906 | Object6 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
19907 | Object7 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
19908 | Object8 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
19909 | Object9 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
19910 | Object10 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
19911 | Object S1 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020

## AQ 210 FVSPE, v2.1.1.3-247
HR | Parameter | Access | Length | Info
1 | Modbus requests | R/W=0 | 1 | Diagnostic request counter
2 | Modbus quality | R | 1 | Diagnostic quality
3 | Modbus errors | R/W=0 | 1 | Diagnostic error counter
4 | Modbus Ctrl OK | R/W=0 | 1 | Diagnostic Control OK counter
5 | Modbus Ctrl Errors | R/W=0 | 1 | Diagnostic Control Error counter
6 | Object1 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
7 | Object2 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
8 | Object3 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9 | Object4 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
10 | Object5 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
11 | Previous Event register | R | 6 | Event code
12 | Previous Event register | R | 6 | Event timestamp (ms)
13 | Previous Event register | R | 6 | Event timestamp (sec Hi-16bits)
14 | Previous Event register | R | 6 | Event timestamp (sec Lo-16bits)
15 | Previous Event register | R | 6 | Event sequential index
16 | Previous Event register | R | 6 | RESERVED
17 | Event register | R | 6 | Event code
18 | Event register | R | 6 | Event timestamp (ms)
19 | Event register | R | 6 | Event timestamp (sec Hi-16bits)
20 | Event register | R | 6 | Event timestamp (sec Lo-16bits)
21 | Event register | R | 6 | Event sequential index
22 | Event register | R | 6 | RESERVED
23 | System time | RW | 3 | System time (ms)
24 | System time | RW | 3 | System time (sec Hi-16bits)
25 | System time | RW | 3 | System time (sec Lo-16bits)
26 | MEAS1:Pri.Pha.curr.IL1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
27 |  |  |  | HR26 (Lo-16bits)
28 | MEAS1:Pri.Pha.curr.IL2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
29 |  |  |  | HR28 (Lo-16bits)
30 | MEAS1:Pri.Pha.curr.IL3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
31 |  |  |  | HR30 (Lo-16bits)
32 | MEAS1:Pri.Res.curr.I01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
33 |  |  |  | HR32 (Lo-16bits)
34 | MEAS1:Pri.Res.curr.I02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
35 |  |  |  | HR34 (Lo-16bits)
36 | MEAS1:Pha.angle IL1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
37 |  |  |  | HR36 (Lo-16bits)
38 | MEAS1:Pha.angle IL2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
39 |  |  |  | HR38 (Lo-16bits)
40 | MEAS1:Pha.angle IL3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
41 |  |  |  | HR40 (Lo-16bits)
42 | MEAS1:Res.curr.angle I01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
43 |  |  |  | HR42 (Lo-16bits)
44 | MEAS1:Res.curr.angle I02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
45 |  |  |  | HR44 (Lo-16bits)
46 | MEAS1:Pri.calc.I0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
47 |  |  |  | HR46 (Lo-16bits)
48 | MEAS1:calc.I0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
49 |  |  |  | HR48 (Lo-16bits)
50 | MEAS1:Pha.curr.IL1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
51 |  |  |  | HR50 (Lo-16bits)
52 | MEAS1:Pha.curr.IL2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
53 |  |  |  | HR52 (Lo-16bits)
54 | MEAS1:Pha.curr.IL3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
55 |  |  |  | HR54 (Lo-16bits)
56 | MEAS1:Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
57 |  |  |  | HR56 (Lo-16bits)
58 | MEAS1:Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
59 |  |  |  | HR58 (Lo-16bits)
60 | MEAS1:Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
61 |  |  |  | HR60 (Lo-16bits)
62 | MEAS1:Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
63 |  |  |  | HR62 (Lo-16bits)
64 | MEAS1:Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
65 |  |  |  | HR64 (Lo-16bits)
66 | MEAS1:Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
67 |  |  |  | HR66 (Lo-16bits)
68 | MEAS1:Res.curr.I01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
69 |  |  |  | HR68 (Lo-16bits)
70 | MEAS1:Res.curr.I02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
71 |  |  |  | HR70 (Lo-16bits)
72 | MEAS1:Pha.L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
73 |  |  |  | HR72 (Lo-16bits)
74 | MEAS1:Pha.L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
75 |  |  |  | HR74 (Lo-16bits)
76 | MEAS1:Pha.L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
77 |  |  |  | HR76 (Lo-16bits)
78 | MEAS1:Pha.L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
79 |  |  |  | HR78 (Lo-16bits)
80 | MEAS1:Pha.L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
81 |  |  |  | HR80 (Lo-16bits)
82 | MEAS1:Pha.L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
83 |  |  |  | HR82 (Lo-16bits)
84 | MEAS1:Res.I01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
85 |  |  |  | HR84 (Lo-16bits)
86 | MEAS1:Res.I01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
87 |  |  |  | HR86 (Lo-16bits)
88 | MEAS1:Res.I02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
89 |  |  |  | HR88 (Lo-16bits)
90 | MEAS1:Res.I02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
91 |  |  |  | HR90 (Lo-16bits)
92 | MEAS1:P-P curr.IL1 | R | 2 | FLOAT [0...500] (Hi-16bits)
93 |  |  |  | HR92 (Lo-16bits)
94 | MEAS1:P-P curr.IL2 | R | 2 | FLOAT [0...500] (Hi-16bits)
95 |  |  |  | HR94 (Lo-16bits)
96 | MEAS1:P-P curr.IL3 | R | 2 | FLOAT [0...500] (Hi-16bits)
97 |  |  |  | HR96 (Lo-16bits)
98 | MEAS1:P-P curr.I01 | R | 2 | FLOAT [0...500] (Hi-16bits)
99 |  |  |  | HR98 (Lo-16bits)
100 | MEAS1:P-P curr.I02 | R | 2 | FLOAT [0...500] (Hi-16bits)
101 |  |  |  | HR100 (Lo-16bits)
102 | MEAS1:IL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
103 |  |  |  | HR102 (Lo-16bits)
104 | MEAS1:IL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
105 |  |  |  | HR104 (Lo-16bits)
106 | MEAS1:IL1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
107 |  |  |  | HR106 (Lo-16bits)
108 | MEAS1:IL1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
109 |  |  |  | HR108 (Lo-16bits)
110 | MEAS1:IL1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
111 |  |  |  | HR110 (Lo-16bits)
112 | MEAS1:IL1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
113 |  |  |  | HR112 (Lo-16bits)
114 | MEAS1:IL1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
115 |  |  |  | HR114 (Lo-16bits)
116 | MEAS1:IL1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
117 |  |  |  | HR116 (Lo-16bits)
118 | MEAS1:IL1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
119 |  |  |  | HR118 (Lo-16bits)
120 | MEAS1:IL1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
121 |  |  |  | HR120 (Lo-16bits)
122 | MEAS1:IL1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
123 |  |  |  | HR122 (Lo-16bits)
124 | MEAS1:IL1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
125 |  |  |  | HR124 (Lo-16bits)
126 | MEAS1:IL1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
127 |  |  |  | HR126 (Lo-16bits)
128 | MEAS1:IL1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
129 |  |  |  | HR128 (Lo-16bits)
130 | MEAS1:IL1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
131 |  |  |  | HR130 (Lo-16bits)
132 | MEAS1:IL1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
133 |  |  |  | HR132 (Lo-16bits)
134 | MEAS1:IL1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
135 |  |  |  | HR134 (Lo-16bits)
136 | MEAS1:IL1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
137 |  |  |  | HR136 (Lo-16bits)
138 | MEAS1:IL1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
139 |  |  |  | HR138 (Lo-16bits)
140 | MEAS1:IL1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
141 |  |  |  | HR140 (Lo-16bits)
142 | MEAS1:IL1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
143 |  |  |  | HR142 (Lo-16bits)
144 | MEAS1:IL1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
145 |  |  |  | HR144 (Lo-16bits)
146 | MEAS1:IL1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
147 |  |  |  | HR146 (Lo-16bits)
148 | MEAS1:IL1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
149 |  |  |  | HR148 (Lo-16bits)
150 | MEAS1:IL1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
151 |  |  |  | HR150 (Lo-16bits)
152 | MEAS1:IL1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
153 |  |  |  | HR152 (Lo-16bits)
154 | MEAS1:IL1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
155 |  |  |  | HR154 (Lo-16bits)
156 | MEAS1:IL1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
157 |  |  |  | HR156 (Lo-16bits)
158 | MEAS1:IL1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
159 |  |  |  | HR158 (Lo-16bits)
160 | MEAS1:IL1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
161 |  |  |  | HR160 (Lo-16bits)
162 | MEAS1:IL1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
163 |  |  |  | HR162 (Lo-16bits)
164 | MEAS1:IL1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
165 |  |  |  | HR164 (Lo-16bits)
166 | MEAS1:IL1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
167 |  |  |  | HR166 (Lo-16bits)
168 | MEAS1:IL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
169 |  |  |  | HR168 (Lo-16bits)
170 | MEAS1:IL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
171 |  |  |  | HR170 (Lo-16bits)
172 | MEAS1:IL2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
173 |  |  |  | HR172 (Lo-16bits)
174 | MEAS1:IL2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
175 |  |  |  | HR174 (Lo-16bits)
176 | MEAS1:IL2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
177 |  |  |  | HR176 (Lo-16bits)
178 | MEAS1:IL2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
179 |  |  |  | HR178 (Lo-16bits)
180 | MEAS1:IL2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
181 |  |  |  | HR180 (Lo-16bits)
182 | MEAS1:IL2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
183 |  |  |  | HR182 (Lo-16bits)
184 | MEAS1:IL2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
185 |  |  |  | HR184 (Lo-16bits)
186 | MEAS1:IL2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
187 |  |  |  | HR186 (Lo-16bits)
188 | MEAS1:IL2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
189 |  |  |  | HR188 (Lo-16bits)
190 | MEAS1:IL2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
191 |  |  |  | HR190 (Lo-16bits)
192 | MEAS1:IL2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
193 |  |  |  | HR192 (Lo-16bits)
194 | MEAS1:IL2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
195 |  |  |  | HR194 (Lo-16bits)
196 | MEAS1:IL2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
197 |  |  |  | HR196 (Lo-16bits)
198 | MEAS1:IL2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
199 |  |  |  | HR198 (Lo-16bits)
200 | MEAS1:IL2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
201 |  |  |  | HR200 (Lo-16bits)
202 | MEAS1:IL2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
203 |  |  |  | HR202 (Lo-16bits)
204 | MEAS1:IL2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
205 |  |  |  | HR204 (Lo-16bits)
206 | MEAS1:IL2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
207 |  |  |  | HR206 (Lo-16bits)
208 | MEAS1:IL2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
209 |  |  |  | HR208 (Lo-16bits)
210 | MEAS1:IL2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
211 |  |  |  | HR210 (Lo-16bits)
212 | MEAS1:IL2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
213 |  |  |  | HR212 (Lo-16bits)
214 | MEAS1:IL2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
215 |  |  |  | HR214 (Lo-16bits)
216 | MEAS1:IL2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
217 |  |  |  | HR216 (Lo-16bits)
218 | MEAS1:IL2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
219 |  |  |  | HR218 (Lo-16bits)
220 | MEAS1:IL2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
221 |  |  |  | HR220 (Lo-16bits)
222 | MEAS1:IL2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
223 |  |  |  | HR222 (Lo-16bits)
224 | MEAS1:IL2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
225 |  |  |  | HR224 (Lo-16bits)
226 | MEAS1:IL2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
227 |  |  |  | HR226 (Lo-16bits)
228 | MEAS1:IL2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
229 |  |  |  | HR228 (Lo-16bits)
230 | MEAS1:IL2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
231 |  |  |  | HR230 (Lo-16bits)
232 | MEAS1:IL2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
233 |  |  |  | HR232 (Lo-16bits)
234 | MEAS1:IL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
235 |  |  |  | HR234 (Lo-16bits)
236 | MEAS1:IL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
237 |  |  |  | HR236 (Lo-16bits)
238 | MEAS1:IL3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
239 |  |  |  | HR238 (Lo-16bits)
240 | MEAS1:IL3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
241 |  |  |  | HR240 (Lo-16bits)
242 | MEAS1:IL3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
243 |  |  |  | HR242 (Lo-16bits)
244 | MEAS1:IL3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
245 |  |  |  | HR244 (Lo-16bits)
246 | MEAS1:IL3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
247 |  |  |  | HR246 (Lo-16bits)
248 | MEAS1:IL3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
249 |  |  |  | HR248 (Lo-16bits)
250 | MEAS1:IL3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
251 |  |  |  | HR250 (Lo-16bits)
252 | MEAS1:IL3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
253 |  |  |  | HR252 (Lo-16bits)
254 | MEAS1:IL3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
255 |  |  |  | HR254 (Lo-16bits)
256 | MEAS1:IL3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
257 |  |  |  | HR256 (Lo-16bits)
258 | MEAS1:IL3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
259 |  |  |  | HR258 (Lo-16bits)
260 | MEAS1:IL3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
261 |  |  |  | HR260 (Lo-16bits)
262 | MEAS1:IL3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
263 |  |  |  | HR262 (Lo-16bits)
264 | MEAS1:IL3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
265 |  |  |  | HR264 (Lo-16bits)
266 | MEAS1:IL3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
267 |  |  |  | HR266 (Lo-16bits)
268 | MEAS1:IL3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
269 |  |  |  | HR268 (Lo-16bits)
270 | MEAS1:IL3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
271 |  |  |  | HR270 (Lo-16bits)
272 | MEAS1:IL3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
273 |  |  |  | HR272 (Lo-16bits)
274 | MEAS1:IL3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
275 |  |  |  | HR274 (Lo-16bits)
276 | MEAS1:IL3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
277 |  |  |  | HR276 (Lo-16bits)
278 | MEAS1:IL3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
279 |  |  |  | HR278 (Lo-16bits)
280 | MEAS1:IL3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
281 |  |  |  | HR280 (Lo-16bits)
282 | MEAS1:IL3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
283 |  |  |  | HR282 (Lo-16bits)
284 | MEAS1:IL3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
285 |  |  |  | HR284 (Lo-16bits)
286 | MEAS1:IL3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
287 |  |  |  | HR286 (Lo-16bits)
288 | MEAS1:IL3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
289 |  |  |  | HR288 (Lo-16bits)
290 | MEAS1:IL3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
291 |  |  |  | HR290 (Lo-16bits)
292 | MEAS1:IL3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
293 |  |  |  | HR292 (Lo-16bits)
294 | MEAS1:IL3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
295 |  |  |  | HR294 (Lo-16bits)
296 | MEAS1:IL3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
297 |  |  |  | HR296 (Lo-16bits)
298 | MEAS1:IL3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
299 |  |  |  | HR298 (Lo-16bits)
300 | MEAS1:I01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
301 |  |  |  | HR300 (Lo-16bits)
302 | MEAS1:I01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
303 |  |  |  | HR302 (Lo-16bits)
304 | MEAS1:I01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
305 |  |  |  | HR304 (Lo-16bits)
306 | MEAS1:I01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
307 |  |  |  | HR306 (Lo-16bits)
308 | MEAS1:I01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
309 |  |  |  | HR308 (Lo-16bits)
310 | MEAS1:I01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
311 |  |  |  | HR310 (Lo-16bits)
312 | MEAS1:I01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
313 |  |  |  | HR312 (Lo-16bits)
314 | MEAS1:I01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
315 |  |  |  | HR314 (Lo-16bits)
316 | MEAS1:I01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
317 |  |  |  | HR316 (Lo-16bits)
318 | MEAS1:I01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
319 |  |  |  | HR318 (Lo-16bits)
320 | MEAS1:I01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
321 |  |  |  | HR320 (Lo-16bits)
322 | MEAS1:I01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
323 |  |  |  | HR322 (Lo-16bits)
324 | MEAS1:I01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
325 |  |  |  | HR324 (Lo-16bits)
326 | MEAS1:I01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
327 |  |  |  | HR326 (Lo-16bits)
328 | MEAS1:I01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
329 |  |  |  | HR328 (Lo-16bits)
330 | MEAS1:I01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
331 |  |  |  | HR330 (Lo-16bits)
332 | MEAS1:I01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
333 |  |  |  | HR332 (Lo-16bits)
334 | MEAS1:I01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
335 |  |  |  | HR334 (Lo-16bits)
336 | MEAS1:I01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
337 |  |  |  | HR336 (Lo-16bits)
338 | MEAS1:I01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
339 |  |  |  | HR338 (Lo-16bits)
340 | MEAS1:I01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
341 |  |  |  | HR340 (Lo-16bits)
342 | MEAS1:I01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
343 |  |  |  | HR342 (Lo-16bits)
344 | MEAS1:I01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
345 |  |  |  | HR344 (Lo-16bits)
346 | MEAS1:I01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
347 |  |  |  | HR346 (Lo-16bits)
348 | MEAS1:I01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
349 |  |  |  | HR348 (Lo-16bits)
350 | MEAS1:I01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
351 |  |  |  | HR350 (Lo-16bits)
352 | MEAS1:I01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
353 |  |  |  | HR352 (Lo-16bits)
354 | MEAS1:I01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
355 |  |  |  | HR354 (Lo-16bits)
356 | MEAS1:I01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
357 |  |  |  | HR356 (Lo-16bits)
358 | MEAS1:I01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
359 |  |  |  | HR358 (Lo-16bits)
360 | MEAS1:I01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
361 |  |  |  | HR360 (Lo-16bits)
362 | MEAS1:I01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
363 |  |  |  | HR362 (Lo-16bits)
364 | MEAS1:I01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
365 |  |  |  | HR364 (Lo-16bits)
366 | MEAS1:I02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
367 |  |  |  | HR366 (Lo-16bits)
368 | MEAS1:I02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
369 |  |  |  | HR368 (Lo-16bits)
370 | MEAS1:I02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
371 |  |  |  | HR370 (Lo-16bits)
372 | MEAS1:I02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
373 |  |  |  | HR372 (Lo-16bits)
374 | MEAS1:I02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
375 |  |  |  | HR374 (Lo-16bits)
376 | MEAS1:I02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
377 |  |  |  | HR376 (Lo-16bits)
378 | MEAS1:I02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
379 |  |  |  | HR378 (Lo-16bits)
380 | MEAS1:I02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
381 |  |  |  | HR380 (Lo-16bits)
382 | MEAS1:I02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
383 |  |  |  | HR382 (Lo-16bits)
384 | MEAS1:I02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
385 |  |  |  | HR384 (Lo-16bits)
386 | MEAS1:I02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
387 |  |  |  | HR386 (Lo-16bits)
388 | MEAS1:I02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
389 |  |  |  | HR388 (Lo-16bits)
390 | MEAS1:I02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
391 |  |  |  | HR390 (Lo-16bits)
392 | MEAS1:I02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
393 |  |  |  | HR392 (Lo-16bits)
394 | MEAS1:I02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
395 |  |  |  | HR394 (Lo-16bits)
396 | MEAS1:I02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
397 |  |  |  | HR396 (Lo-16bits)
398 | MEAS1:I02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
399 |  |  |  | HR398 (Lo-16bits)
400 | MEAS1:I02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
401 |  |  |  | HR400 (Lo-16bits)
402 | MEAS1:I02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
403 |  |  |  | HR402 (Lo-16bits)
404 | MEAS1:I02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
405 |  |  |  | HR404 (Lo-16bits)
406 | MEAS1:I02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
407 |  |  |  | HR406 (Lo-16bits)
408 | MEAS1:I02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
409 |  |  |  | HR408 (Lo-16bits)
410 | MEAS1:I02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
411 |  |  |  | HR410 (Lo-16bits)
412 | MEAS1:I02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
413 |  |  |  | HR412 (Lo-16bits)
414 | MEAS1:I02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
415 |  |  |  | HR414 (Lo-16bits)
416 | MEAS1:I02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
417 |  |  |  | HR416 (Lo-16bits)
418 | MEAS1:I02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
419 |  |  |  | HR418 (Lo-16bits)
420 | MEAS1:I02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
421 |  |  |  | HR420 (Lo-16bits)
422 | MEAS1:I02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
423 |  |  |  | HR422 (Lo-16bits)
424 | MEAS1:I02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
425 |  |  |  | HR424 (Lo-16bits)
426 | MEAS1:I02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
427 |  |  |  | HR426 (Lo-16bits)
428 | MEAS1:I02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
429 |  |  |  | HR428 (Lo-16bits)
430 | MEAS1:I02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
431 |  |  |  | HR430 (Lo-16bits)
432 | MEAS1:Meas1 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
433 |  |  |  | HR432 (Lo-16bits)
434 | MEAS2:Pri.Pha.curr.I''L1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
435 |  |  |  | HR434 (Lo-16bits)
436 | MEAS2:Pri.Pha.curr.I''L2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
437 |  |  |  | HR436 (Lo-16bits)
438 | MEAS2:Pri.Pha.curr.I''L3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
439 |  |  |  | HR438 (Lo-16bits)
440 | MEAS2:Pha.angle I''L1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
441 |  |  |  | HR440 (Lo-16bits)
442 | MEAS2:Pha.angle I''L2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
443 |  |  |  | HR442 (Lo-16bits)
444 | MEAS2:Pha.angle I''L3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
445 |  |  |  | HR444 (Lo-16bits)
446 | MEAS2:Pri.Res.curr.I''01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
447 |  |  |  | HR446 (Lo-16bits)
448 | MEAS2:Res.curr.angle I''01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
449 |  |  |  | HR448 (Lo-16bits)
450 | MEAS2:Pri.Res.curr.I''02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
451 |  |  |  | HR450 (Lo-16bits)
452 | MEAS2:Res.curr.angle I''02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
453 |  |  |  | HR452 (Lo-16bits)
454 | MEAS2:Pri.calc.I''0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
455 |  |  |  | HR454 (Lo-16bits)
456 | MEAS2:calc.I''0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
457 |  |  |  | HR456 (Lo-16bits)
458 | MEAS2:Pha.curr.I''L1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
459 |  |  |  | HR458 (Lo-16bits)
460 | MEAS2:Pha.curr.I''L2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
461 |  |  |  | HR460 (Lo-16bits)
462 | MEAS2:Pha.curr.I''L3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
463 |  |  |  | HR462 (Lo-16bits)
464 | MEAS2:I'' Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
465 |  |  |  | HR464 (Lo-16bits)
466 | MEAS2:I'' Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
467 |  |  |  | HR466 (Lo-16bits)
468 | MEAS2:I'' Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
469 |  |  |  | HR468 (Lo-16bits)
470 | MEAS2:I'' Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
471 |  |  |  | HR470 (Lo-16bits)
472 | MEAS2:I'' Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
473 |  |  |  | HR472 (Lo-16bits)
474 | MEAS2:I'' Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
475 |  |  |  | HR474 (Lo-16bits)
476 | MEAS2:Res.curr.I''01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
477 |  |  |  | HR476 (Lo-16bits)
478 | MEAS2:Res.curr.I''02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
479 |  |  |  | HR478 (Lo-16bits)
480 | MEAS2:Pha.I''L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
481 |  |  |  | HR480 (Lo-16bits)
482 | MEAS2:Pha.I''L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
483 |  |  |  | HR482 (Lo-16bits)
484 | MEAS2:Pha.I''L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
485 |  |  |  | HR484 (Lo-16bits)
486 | MEAS2:Pha.I''L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
487 |  |  |  | HR486 (Lo-16bits)
488 | MEAS2:Pha.I''L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
489 |  |  |  | HR488 (Lo-16bits)
490 | MEAS2:Pha.I''L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
491 |  |  |  | HR490 (Lo-16bits)
492 | MEAS2:Res.I''01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
493 |  |  |  | HR492 (Lo-16bits)
494 | MEAS2:Res.I''01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
495 |  |  |  | HR494 (Lo-16bits)
496 | MEAS2:Res.I''02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
497 |  |  |  | HR496 (Lo-16bits)
498 | MEAS2:Res.I''02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
499 |  |  |  | HR498 (Lo-16bits)
500 | MEAS2:P-P curr.I''L1 | R | 2 | FLOAT [0...500] (Hi-16bits)
501 |  |  |  | HR500 (Lo-16bits)
502 | MEAS2:P-P curr.I''L2 | R | 2 | FLOAT [0...500] (Hi-16bits)
503 |  |  |  | HR502 (Lo-16bits)
504 | MEAS2:P-P curr.I''L3 | R | 2 | FLOAT [0...500] (Hi-16bits)
505 |  |  |  | HR504 (Lo-16bits)
506 | MEAS2:P-P curr.I''01 | R | 2 | FLOAT [0...500] (Hi-16bits)
507 |  |  |  | HR506 (Lo-16bits)
508 | MEAS2:P-P curr.I''02 | R | 2 | FLOAT [0...500] (Hi-16bits)
509 |  |  |  | HR508 (Lo-16bits)
510 | MEAS2:I''L1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
511 |  |  |  | HR510 (Lo-16bits)
512 | MEAS2:I''L1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
513 |  |  |  | HR512 (Lo-16bits)
514 | MEAS2:I''L1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
515 |  |  |  | HR514 (Lo-16bits)
516 | MEAS2:I''L1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
517 |  |  |  | HR516 (Lo-16bits)
518 | MEAS2:I''L1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
519 |  |  |  | HR518 (Lo-16bits)
520 | MEAS2:I''L1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
521 |  |  |  | HR520 (Lo-16bits)
522 | MEAS2:I''L1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
523 |  |  |  | HR522 (Lo-16bits)
524 | MEAS2:I''L1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
525 |  |  |  | HR524 (Lo-16bits)
526 | MEAS2:I''L1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
527 |  |  |  | HR526 (Lo-16bits)
528 | MEAS2:I''L1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
529 |  |  |  | HR528 (Lo-16bits)
530 | MEAS2:I''L1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
531 |  |  |  | HR530 (Lo-16bits)
532 | MEAS2:I''L1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
533 |  |  |  | HR532 (Lo-16bits)
534 | MEAS2:I''L1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
535 |  |  |  | HR534 (Lo-16bits)
536 | MEAS2:I''L1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
537 |  |  |  | HR536 (Lo-16bits)
538 | MEAS2:I''L1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
539 |  |  |  | HR538 (Lo-16bits)
540 | MEAS2:I''L1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
541 |  |  |  | HR540 (Lo-16bits)
542 | MEAS2:I''L1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
543 |  |  |  | HR542 (Lo-16bits)
544 | MEAS2:I''L1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
545 |  |  |  | HR544 (Lo-16bits)
546 | MEAS2:I''L1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
547 |  |  |  | HR546 (Lo-16bits)
548 | MEAS2:I''L1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
549 |  |  |  | HR548 (Lo-16bits)
550 | MEAS2:I''L1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
551 |  |  |  | HR550 (Lo-16bits)
552 | MEAS2:I''L1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
553 |  |  |  | HR552 (Lo-16bits)
554 | MEAS2:I''L1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
555 |  |  |  | HR554 (Lo-16bits)
556 | MEAS2:I''L1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
557 |  |  |  | HR556 (Lo-16bits)
558 | MEAS2:I''L1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
559 |  |  |  | HR558 (Lo-16bits)
560 | MEAS2:I''L1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
561 |  |  |  | HR560 (Lo-16bits)
562 | MEAS2:I''L1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
563 |  |  |  | HR562 (Lo-16bits)
564 | MEAS2:I''L1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
565 |  |  |  | HR564 (Lo-16bits)
566 | MEAS2:I''L1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
567 |  |  |  | HR566 (Lo-16bits)
568 | MEAS2:I''L1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
569 |  |  |  | HR568 (Lo-16bits)
570 | MEAS2:I''L1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
571 |  |  |  | HR570 (Lo-16bits)
572 | MEAS2:I''L1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
573 |  |  |  | HR572 (Lo-16bits)
574 | MEAS2:I''L1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
575 |  |  |  | HR574 (Lo-16bits)
576 | MEAS2:I''L2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
577 |  |  |  | HR576 (Lo-16bits)
578 | MEAS2:I''L2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
579 |  |  |  | HR578 (Lo-16bits)
580 | MEAS2:I''L2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
581 |  |  |  | HR580 (Lo-16bits)
582 | MEAS2:I''L2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
583 |  |  |  | HR582 (Lo-16bits)
584 | MEAS2:I''L2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
585 |  |  |  | HR584 (Lo-16bits)
586 | MEAS2:I''L2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
587 |  |  |  | HR586 (Lo-16bits)
588 | MEAS2:I''L2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
589 |  |  |  | HR588 (Lo-16bits)
590 | MEAS2:I''L2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
591 |  |  |  | HR590 (Lo-16bits)
592 | MEAS2:I''L2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
593 |  |  |  | HR592 (Lo-16bits)
594 | MEAS2:I''L2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
595 |  |  |  | HR594 (Lo-16bits)
596 | MEAS2:I''L2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
597 |  |  |  | HR596 (Lo-16bits)
598 | MEAS2:I''L2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
599 |  |  |  | HR598 (Lo-16bits)
600 | MEAS2:I''L2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
601 |  |  |  | HR600 (Lo-16bits)
602 | MEAS2:I''L2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
603 |  |  |  | HR602 (Lo-16bits)
604 | MEAS2:I''L2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
605 |  |  |  | HR604 (Lo-16bits)
606 | MEAS2:I''L2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
607 |  |  |  | HR606 (Lo-16bits)
608 | MEAS2:I''L2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
609 |  |  |  | HR608 (Lo-16bits)
610 | MEAS2:I''L2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
611 |  |  |  | HR610 (Lo-16bits)
612 | MEAS2:I''L2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
613 |  |  |  | HR612 (Lo-16bits)
614 | MEAS2:I''L2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
615 |  |  |  | HR614 (Lo-16bits)
616 | MEAS2:I''L2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
617 |  |  |  | HR616 (Lo-16bits)
618 | MEAS2:I''L2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
619 |  |  |  | HR618 (Lo-16bits)
620 | MEAS2:I''L2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
621 |  |  |  | HR620 (Lo-16bits)
622 | MEAS2:I''L2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
623 |  |  |  | HR622 (Lo-16bits)
624 | MEAS2:I''L2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
625 |  |  |  | HR624 (Lo-16bits)
626 | MEAS2:I''L2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
627 |  |  |  | HR626 (Lo-16bits)
628 | MEAS2:I''L2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
629 |  |  |  | HR628 (Lo-16bits)
630 | MEAS2:I''L2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
631 |  |  |  | HR630 (Lo-16bits)
632 | MEAS2:I''L2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
633 |  |  |  | HR632 (Lo-16bits)
634 | MEAS2:I''L2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
635 |  |  |  | HR634 (Lo-16bits)
636 | MEAS2:I''L2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
637 |  |  |  | HR636 (Lo-16bits)
638 | MEAS2:I''L2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
639 |  |  |  | HR638 (Lo-16bits)
640 | MEAS2:I''L2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
641 |  |  |  | HR640 (Lo-16bits)
642 | MEAS2:I''L3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
643 |  |  |  | HR642 (Lo-16bits)
644 | MEAS2:I''L3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
645 |  |  |  | HR644 (Lo-16bits)
646 | MEAS2:I''L3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
647 |  |  |  | HR646 (Lo-16bits)
648 | MEAS2:I''L3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
649 |  |  |  | HR648 (Lo-16bits)
650 | MEAS2:I''L3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
651 |  |  |  | HR650 (Lo-16bits)
652 | MEAS2:I''L3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
653 |  |  |  | HR652 (Lo-16bits)
654 | MEAS2:I''L3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
655 |  |  |  | HR654 (Lo-16bits)
656 | MEAS2:I''L3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
657 |  |  |  | HR656 (Lo-16bits)
658 | MEAS2:I''L3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
659 |  |  |  | HR658 (Lo-16bits)
660 | MEAS2:I''L3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
661 |  |  |  | HR660 (Lo-16bits)
662 | MEAS2:I''L3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
663 |  |  |  | HR662 (Lo-16bits)
664 | MEAS2:I''L3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
665 |  |  |  | HR664 (Lo-16bits)
666 | MEAS2:I''L3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
667 |  |  |  | HR666 (Lo-16bits)
668 | MEAS2:I''L3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
669 |  |  |  | HR668 (Lo-16bits)
670 | MEAS2:I''L3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
671 |  |  |  | HR670 (Lo-16bits)
672 | MEAS2:I''L3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
673 |  |  |  | HR672 (Lo-16bits)
674 | MEAS2:I''L3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
675 |  |  |  | HR674 (Lo-16bits)
676 | MEAS2:I''L3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
677 |  |  |  | HR676 (Lo-16bits)
678 | MEAS2:I''L3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
679 |  |  |  | HR678 (Lo-16bits)
680 | MEAS2:I''L3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
681 |  |  |  | HR680 (Lo-16bits)
682 | MEAS2:I''L3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
683 |  |  |  | HR682 (Lo-16bits)
684 | MEAS2:I''L3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
685 |  |  |  | HR684 (Lo-16bits)
686 | MEAS2:I''L3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
687 |  |  |  | HR686 (Lo-16bits)
688 | MEAS2:I''L3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
689 |  |  |  | HR688 (Lo-16bits)
690 | MEAS2:I''L3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
691 |  |  |  | HR690 (Lo-16bits)
692 | MEAS2:I''L3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
693 |  |  |  | HR692 (Lo-16bits)
694 | MEAS2:I''L3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
695 |  |  |  | HR694 (Lo-16bits)
696 | MEAS2:I''L3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
697 |  |  |  | HR696 (Lo-16bits)
698 | MEAS2:I''L3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
699 |  |  |  | HR698 (Lo-16bits)
700 | MEAS2:I''L3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
701 |  |  |  | HR700 (Lo-16bits)
702 | MEAS2:I''L3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
703 |  |  |  | HR702 (Lo-16bits)
704 | MEAS2:I''L3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
705 |  |  |  | HR704 (Lo-16bits)
706 | MEAS2:I''L3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
707 |  |  |  | HR706 (Lo-16bits)
708 | MEAS2:I''01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
709 |  |  |  | HR708 (Lo-16bits)
710 | MEAS2:I''01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
711 |  |  |  | HR710 (Lo-16bits)
712 | MEAS2:I''01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
713 |  |  |  | HR712 (Lo-16bits)
714 | MEAS2:I''01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
715 |  |  |  | HR714 (Lo-16bits)
716 | MEAS2:I''01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
717 |  |  |  | HR716 (Lo-16bits)
718 | MEAS2:I''01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
719 |  |  |  | HR718 (Lo-16bits)
720 | MEAS2:I''01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
721 |  |  |  | HR720 (Lo-16bits)
722 | MEAS2:I''01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
723 |  |  |  | HR722 (Lo-16bits)
724 | MEAS2:I''01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
725 |  |  |  | HR724 (Lo-16bits)
726 | MEAS2:I''01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
727 |  |  |  | HR726 (Lo-16bits)
728 | MEAS2:I''01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
729 |  |  |  | HR728 (Lo-16bits)
730 | MEAS2:I''01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
731 |  |  |  | HR730 (Lo-16bits)
732 | MEAS2:I''01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
733 |  |  |  | HR732 (Lo-16bits)
734 | MEAS2:I''01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
735 |  |  |  | HR734 (Lo-16bits)
736 | MEAS2:I''01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
737 |  |  |  | HR736 (Lo-16bits)
738 | MEAS2:I''01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
739 |  |  |  | HR738 (Lo-16bits)
740 | MEAS2:I''01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
741 |  |  |  | HR740 (Lo-16bits)
742 | MEAS2:I''01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
743 |  |  |  | HR742 (Lo-16bits)
744 | MEAS2:I''01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
745 |  |  |  | HR744 (Lo-16bits)
746 | MEAS2:I''01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
747 |  |  |  | HR746 (Lo-16bits)
748 | MEAS2:I''01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
749 |  |  |  | HR748 (Lo-16bits)
750 | MEAS2:I''01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
751 |  |  |  | HR750 (Lo-16bits)
752 | MEAS2:I''01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
753 |  |  |  | HR752 (Lo-16bits)
754 | MEAS2:I''01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
755 |  |  |  | HR754 (Lo-16bits)
756 | MEAS2:I''01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
757 |  |  |  | HR756 (Lo-16bits)
758 | MEAS2:I''01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
759 |  |  |  | HR758 (Lo-16bits)
760 | MEAS2:I''01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
761 |  |  |  | HR760 (Lo-16bits)
762 | MEAS2:I''01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
763 |  |  |  | HR762 (Lo-16bits)
764 | MEAS2:I''01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
765 |  |  |  | HR764 (Lo-16bits)
766 | MEAS2:I''01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
767 |  |  |  | HR766 (Lo-16bits)
768 | MEAS2:I''01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
769 |  |  |  | HR768 (Lo-16bits)
770 | MEAS2:I''01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
771 |  |  |  | HR770 (Lo-16bits)
772 | MEAS2:I''01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
773 |  |  |  | HR772 (Lo-16bits)
774 | MEAS2:I''02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
775 |  |  |  | HR774 (Lo-16bits)
776 | MEAS2:I''02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
777 |  |  |  | HR776 (Lo-16bits)
778 | MEAS2:I''02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
779 |  |  |  | HR778 (Lo-16bits)
780 | MEAS2:I''02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
781 |  |  |  | HR780 (Lo-16bits)
782 | MEAS2:I''02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
783 |  |  |  | HR782 (Lo-16bits)
784 | MEAS2:I''02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
785 |  |  |  | HR784 (Lo-16bits)
786 | MEAS2:I''02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
787 |  |  |  | HR786 (Lo-16bits)
788 | MEAS2:I''02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
789 |  |  |  | HR788 (Lo-16bits)
790 | MEAS2:I''02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
791 |  |  |  | HR790 (Lo-16bits)
792 | MEAS2:I''02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
793 |  |  |  | HR792 (Lo-16bits)
794 | MEAS2:I''02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
795 |  |  |  | HR794 (Lo-16bits)
796 | MEAS2:I''02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
797 |  |  |  | HR796 (Lo-16bits)
798 | MEAS2:I''02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
799 |  |  |  | HR798 (Lo-16bits)
800 | MEAS2:I''02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
801 |  |  |  | HR800 (Lo-16bits)
802 | MEAS2:I''02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
803 |  |  |  | HR802 (Lo-16bits)
804 | MEAS2:I''02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
805 |  |  |  | HR804 (Lo-16bits)
806 | MEAS2:I''02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
807 |  |  |  | HR806 (Lo-16bits)
808 | MEAS2:I''02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
809 |  |  |  | HR808 (Lo-16bits)
810 | MEAS2:I''02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
811 |  |  |  | HR810 (Lo-16bits)
812 | MEAS2:I''02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
813 |  |  |  | HR812 (Lo-16bits)
814 | MEAS2:I''02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
815 |  |  |  | HR814 (Lo-16bits)
816 | MEAS2:I''02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
817 |  |  |  | HR816 (Lo-16bits)
818 | MEAS2:I''02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
819 |  |  |  | HR818 (Lo-16bits)
820 | MEAS2:I''02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
821 |  |  |  | HR820 (Lo-16bits)
822 | MEAS2:I''02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
823 |  |  |  | HR822 (Lo-16bits)
824 | MEAS2:I''02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
825 |  |  |  | HR824 (Lo-16bits)
826 | MEAS2:I''02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
827 |  |  |  | HR826 (Lo-16bits)
828 | MEAS2:I''02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
829 |  |  |  | HR828 (Lo-16bits)
830 | MEAS2:I''02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
831 |  |  |  | HR830 (Lo-16bits)
832 | MEAS2:I''02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
833 |  |  |  | HR832 (Lo-16bits)
834 | MEAS2:I''02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
835 |  |  |  | HR834 (Lo-16bits)
836 | MEAS2:I''02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
837 |  |  |  | HR836 (Lo-16bits)
838 | MEAS2:I''02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
839 |  |  |  | HR838 (Lo-16bits)
840 | MEAS2:MEAS2 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
841 |  |  |  | HR840 (Lo-16bits)
842 | MEAS3:U1Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
843 |  |  |  | HR842 (Lo-16bits)
844 | MEAS3:U1Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
845 |  |  |  | HR844 (Lo-16bits)
846 | MEAS3:U2Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
847 |  |  |  | HR846 (Lo-16bits)
848 | MEAS3:U2Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
849 |  |  |  | HR848 (Lo-16bits)
850 | MEAS3:U3Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
851 |  |  |  | HR850 (Lo-16bits)
852 | MEAS3:U3Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
853 |  |  |  | HR852 (Lo-16bits)
854 | MEAS3:U4Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
855 |  |  |  | HR854 (Lo-16bits)
856 | MEAS3:U4Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
857 |  |  |  | HR856 (Lo-16bits)
858 | MEAS3:U1Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
859 |  |  |  | HR858 (Lo-16bits)
860 | MEAS3:U1Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
861 |  |  |  | HR860 (Lo-16bits)
862 | MEAS3:U2Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
863 |  |  |  | HR862 (Lo-16bits)
864 | MEAS3:U2Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
865 |  |  |  | HR864 (Lo-16bits)
866 | MEAS3:U3Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
867 |  |  |  | HR866 (Lo-16bits)
868 | MEAS3:U3Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
869 |  |  |  | HR868 (Lo-16bits)
870 | MEAS3:U4Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
871 |  |  |  | HR870 (Lo-16bits)
872 | MEAS3:U4Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
873 |  |  |  | HR872 (Lo-16bits)
874 | MEAS3:Pos.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
875 |  |  |  | HR874 (Lo-16bits)
876 | MEAS3:Pos.seq.Volt.sec | R | 2 | FLOAT [0...480] (Hi-16bits)
877 |  |  |  | HR876 (Lo-16bits)
878 | MEAS3:Neg.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
879 |  |  |  | HR878 (Lo-16bits)
880 | MEAS3:Neg.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
881 |  |  |  | HR880 (Lo-16bits)
882 | MEAS3:Zero.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
883 |  |  |  | HR882 (Lo-16bits)
884 | MEAS3:Zero.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
885 |  |  |  | HR884 (Lo-16bits)
886 | MEAS3:U0 Calc. pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
887 |  |  |  | HR886 (Lo-16bits)
888 | MEAS3:U0 Calc.Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
889 |  |  |  | HR888 (Lo-16bits)
890 | MEAS3:U1 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
891 |  |  |  | HR890 (Lo-16bits)
892 | MEAS3:U2 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
893 |  |  |  | HR892 (Lo-16bits)
894 | MEAS3:U3 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
895 |  |  |  | HR894 (Lo-16bits)
896 | MEAS3:U4 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
897 |  |  |  | HR896 (Lo-16bits)
898 | MEAS3:Pos.Seq volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
899 |  |  |  | HR898 (Lo-16bits)
900 | MEAS3:Neg.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
901 |  |  |  | HR900 (Lo-16bits)
902 | MEAS3:Zero.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
903 |  |  |  | HR902 (Lo-16bits)
904 | MEAS3:System volt UL12 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
905 |  |  |  | HR904 (Lo-16bits)
906 | MEAS3:System volt UL12 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
907 |  |  |  | HR906 (Lo-16bits)
908 | MEAS3:System volt UL12 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
909 |  |  |  | HR908 (Lo-16bits)
910 | MEAS3:System volt UL23 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
911 |  |  |  | HR910 (Lo-16bits)
912 | MEAS3:System volt UL23 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
913 |  |  |  | HR912 (Lo-16bits)
914 | MEAS3:System volt UL23 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
915 |  |  |  | HR914 (Lo-16bits)
916 | MEAS3:System volt UL31 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
917 |  |  |  | HR916 (Lo-16bits)
918 | MEAS3:System volt UL31 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
919 |  |  |  | HR918 (Lo-16bits)
920 | MEAS3:System volt UL31 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
921 |  |  |  | HR920 (Lo-16bits)
922 | MEAS3:System volt UL1 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
923 |  |  |  | HR922 (Lo-16bits)
924 | MEAS3:System volt UL1 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
925 |  |  |  | HR924 (Lo-16bits)
926 | MEAS3:System volt UL1 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
927 |  |  |  | HR926 (Lo-16bits)
928 | MEAS3:System volt UL2 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
929 |  |  |  | HR928 (Lo-16bits)
930 | MEAS3:System volt UL2 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
931 |  |  |  | HR930 (Lo-16bits)
932 | MEAS3:System volt UL2 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
933 |  |  |  | HR932 (Lo-16bits)
934 | MEAS3:System volt UL3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
935 |  |  |  | HR934 (Lo-16bits)
936 | MEAS3:System volt UL3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
937 |  |  |  | HR936 (Lo-16bits)
938 | MEAS3:System volt UL3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
939 |  |  |  | HR938 (Lo-16bits)
940 | MEAS3:System volt U0 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
941 |  |  |  | HR940 (Lo-16bits)
942 | MEAS3:System volt U0 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
943 |  |  |  | HR942 (Lo-16bits)
944 | MEAS3:System volt U0 mag(%) | R | 2 | FLOAT [0...120] (Hi-16bits)
945 |  |  |  | HR944 (Lo-16bits)
946 | MEAS3:System volt U0 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
947 |  |  |  | HR946 (Lo-16bits)
948 | MEAS3:System volt U3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
949 |  |  |  | HR948 (Lo-16bits)
950 | MEAS3:System volt U3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
951 |  |  |  | HR950 (Lo-16bits)
952 | MEAS3:System volt U3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
953 |  |  |  | HR952 (Lo-16bits)
954 | MEAS3:System volt U4 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
955 |  |  |  | HR954 (Lo-16bits)
956 | MEAS3:System volt U4 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
957 |  |  |  | HR956 (Lo-16bits)
958 | MEAS3:System volt U4 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
959 |  |  |  | HR958 (Lo-16bits)
960 | MEAS3:System volt UL1 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
961 |  |  |  | HR960 (Lo-16bits)
962 | MEAS3:System volt UL2 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
963 |  |  |  | HR962 (Lo-16bits)
964 | MEAS3:System volt UL3 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
965 |  |  |  | HR964 (Lo-16bits)
966 | MEAS3:UL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
967 |  |  |  | HR966 (Lo-16bits)
968 | MEAS3:UL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
969 |  |  |  | HR968 (Lo-16bits)
970 | MEAS3:UL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
971 |  |  |  | HR970 (Lo-16bits)
972 | MEAS3:UL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
973 |  |  |  | HR972 (Lo-16bits)
974 | MEAS3:UL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
975 |  |  |  | HR974 (Lo-16bits)
976 | MEAS3:UL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
977 |  |  |  | HR976 (Lo-16bits)
978 | MEAS3:U1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
979 |  |  |  | HR978 (Lo-16bits)
980 | MEAS3:U1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
981 |  |  |  | HR980 (Lo-16bits)
982 | MEAS3:U1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
983 |  |  |  | HR982 (Lo-16bits)
984 | MEAS3:U1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
985 |  |  |  | HR984 (Lo-16bits)
986 | MEAS3:U1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
987 |  |  |  | HR986 (Lo-16bits)
988 | MEAS3:U1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
989 |  |  |  | HR988 (Lo-16bits)
990 | MEAS3:U1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
991 |  |  |  | HR990 (Lo-16bits)
992 | MEAS3:U1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
993 |  |  |  | HR992 (Lo-16bits)
994 | MEAS3:U1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
995 |  |  |  | HR994 (Lo-16bits)
996 | MEAS3:U1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
997 |  |  |  | HR996 (Lo-16bits)
998 | MEAS3:U1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
999 |  |  |  | HR998 (Lo-16bits)
1000 | MEAS3:U1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1001 |  |  |  | HR1000 (Lo-16bits)
1002 | MEAS3:U1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1003 |  |  |  | HR1002 (Lo-16bits)
1004 | MEAS3:U1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1005 |  |  |  | HR1004 (Lo-16bits)
1006 | MEAS3:U1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1007 |  |  |  | HR1006 (Lo-16bits)
1008 | MEAS3:U1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1009 |  |  |  | HR1008 (Lo-16bits)
1010 | MEAS3:U1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1011 |  |  |  | HR1010 (Lo-16bits)
1012 | MEAS3:U1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1013 |  |  |  | HR1012 (Lo-16bits)
1014 | MEAS3:U1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1015 |  |  |  | HR1014 (Lo-16bits)
1016 | MEAS3:U1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1017 |  |  |  | HR1016 (Lo-16bits)
1018 | MEAS3:U1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1019 |  |  |  | HR1018 (Lo-16bits)
1020 | MEAS3:U1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1021 |  |  |  | HR1020 (Lo-16bits)
1022 | MEAS3:U1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1023 |  |  |  | HR1022 (Lo-16bits)
1024 | MEAS3:U1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1025 |  |  |  | HR1024 (Lo-16bits)
1026 | MEAS3:U1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1027 |  |  |  | HR1026 (Lo-16bits)
1028 | MEAS3:U1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1029 |  |  |  | HR1028 (Lo-16bits)
1030 | MEAS3:U1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1031 |  |  |  | HR1030 (Lo-16bits)
1032 | MEAS3:U1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1033 |  |  |  | HR1032 (Lo-16bits)
1034 | MEAS3:U1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1035 |  |  |  | HR1034 (Lo-16bits)
1036 | MEAS3:U1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1037 |  |  |  | HR1036 (Lo-16bits)
1038 | MEAS3:U1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1039 |  |  |  | HR1038 (Lo-16bits)
1040 | MEAS3:U2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1041 |  |  |  | HR1040 (Lo-16bits)
1042 | MEAS3:U2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1043 |  |  |  | HR1042 (Lo-16bits)
1044 | MEAS3:U2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1045 |  |  |  | HR1044 (Lo-16bits)
1046 | MEAS3:U2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1047 |  |  |  | HR1046 (Lo-16bits)
1048 | MEAS3:U2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1049 |  |  |  | HR1048 (Lo-16bits)
1050 | MEAS3:U2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1051 |  |  |  | HR1050 (Lo-16bits)
1052 | MEAS3:U2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1053 |  |  |  | HR1052 (Lo-16bits)
1054 | MEAS3:U2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1055 |  |  |  | HR1054 (Lo-16bits)
1056 | MEAS3:U2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1057 |  |  |  | HR1056 (Lo-16bits)
1058 | MEAS3:U2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1059 |  |  |  | HR1058 (Lo-16bits)
1060 | MEAS3:U2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1061 |  |  |  | HR1060 (Lo-16bits)
1062 | MEAS3:U2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1063 |  |  |  | HR1062 (Lo-16bits)
1064 | MEAS3:U2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1065 |  |  |  | HR1064 (Lo-16bits)
1066 | MEAS3:U2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1067 |  |  |  | HR1066 (Lo-16bits)
1068 | MEAS3:U2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1069 |  |  |  | HR1068 (Lo-16bits)
1070 | MEAS3:U2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1071 |  |  |  | HR1070 (Lo-16bits)
1072 | MEAS3:U2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1073 |  |  |  | HR1072 (Lo-16bits)
1074 | MEAS3:U2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1075 |  |  |  | HR1074 (Lo-16bits)
1076 | MEAS3:U2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1077 |  |  |  | HR1076 (Lo-16bits)
1078 | MEAS3:U2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1079 |  |  |  | HR1078 (Lo-16bits)
1080 | MEAS3:U2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1081 |  |  |  | HR1080 (Lo-16bits)
1082 | MEAS3:U2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1083 |  |  |  | HR1082 (Lo-16bits)
1084 | MEAS3:U2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1085 |  |  |  | HR1084 (Lo-16bits)
1086 | MEAS3:U2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1087 |  |  |  | HR1086 (Lo-16bits)
1088 | MEAS3:U2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1089 |  |  |  | HR1088 (Lo-16bits)
1090 | MEAS3:U2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1091 |  |  |  | HR1090 (Lo-16bits)
1092 | MEAS3:U2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1093 |  |  |  | HR1092 (Lo-16bits)
1094 | MEAS3:U2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1095 |  |  |  | HR1094 (Lo-16bits)
1096 | MEAS3:U2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1097 |  |  |  | HR1096 (Lo-16bits)
1098 | MEAS3:U2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1099 |  |  |  | HR1098 (Lo-16bits)
1100 | MEAS3:U2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1101 |  |  |  | HR1100 (Lo-16bits)
1102 | MEAS3:U3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1103 |  |  |  | HR1102 (Lo-16bits)
1104 | MEAS3:U3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1105 |  |  |  | HR1104 (Lo-16bits)
1106 | MEAS3:U3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1107 |  |  |  | HR1106 (Lo-16bits)
1108 | MEAS3:U3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1109 |  |  |  | HR1108 (Lo-16bits)
1110 | MEAS3:U3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1111 |  |  |  | HR1110 (Lo-16bits)
1112 | MEAS3:U3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1113 |  |  |  | HR1112 (Lo-16bits)
1114 | MEAS3:U3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1115 |  |  |  | HR1114 (Lo-16bits)
1116 | MEAS3:U3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1117 |  |  |  | HR1116 (Lo-16bits)
1118 | MEAS3:U3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1119 |  |  |  | HR1118 (Lo-16bits)
1120 | MEAS3:U3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1121 |  |  |  | HR1120 (Lo-16bits)
1122 | MEAS3:U3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1123 |  |  |  | HR1122 (Lo-16bits)
1124 | MEAS3:U3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1125 |  |  |  | HR1124 (Lo-16bits)
1126 | MEAS3:U3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1127 |  |  |  | HR1126 (Lo-16bits)
1128 | MEAS3:U3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1129 |  |  |  | HR1128 (Lo-16bits)
1130 | MEAS3:U3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1131 |  |  |  | HR1130 (Lo-16bits)
1132 | MEAS3:U3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1133 |  |  |  | HR1132 (Lo-16bits)
1134 | MEAS3:U3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1135 |  |  |  | HR1134 (Lo-16bits)
1136 | MEAS3:U3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1137 |  |  |  | HR1136 (Lo-16bits)
1138 | MEAS3:U3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1139 |  |  |  | HR1138 (Lo-16bits)
1140 | MEAS3:U3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1141 |  |  |  | HR1140 (Lo-16bits)
1142 | MEAS3:U3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1143 |  |  |  | HR1142 (Lo-16bits)
1144 | MEAS3:U3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1145 |  |  |  | HR1144 (Lo-16bits)
1146 | MEAS3:U3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1147 |  |  |  | HR1146 (Lo-16bits)
1148 | MEAS3:U3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1149 |  |  |  | HR1148 (Lo-16bits)
1150 | MEAS3:U3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1151 |  |  |  | HR1150 (Lo-16bits)
1152 | MEAS3:U3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1153 |  |  |  | HR1152 (Lo-16bits)
1154 | MEAS3:U3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1155 |  |  |  | HR1154 (Lo-16bits)
1156 | MEAS3:U3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1157 |  |  |  | HR1156 (Lo-16bits)
1158 | MEAS3:U3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1159 |  |  |  | HR1158 (Lo-16bits)
1160 | MEAS3:U3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1161 |  |  |  | HR1160 (Lo-16bits)
1162 | MEAS3:U3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1163 |  |  |  | HR1162 (Lo-16bits)
1164 | MEAS3:U4 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1165 |  |  |  | HR1164 (Lo-16bits)
1166 | MEAS3:U4 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1167 |  |  |  | HR1166 (Lo-16bits)
1168 | MEAS3:U4 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1169 |  |  |  | HR1168 (Lo-16bits)
1170 | MEAS3:U4 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1171 |  |  |  | HR1170 (Lo-16bits)
1172 | MEAS3:U4 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1173 |  |  |  | HR1172 (Lo-16bits)
1174 | MEAS3:U4 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1175 |  |  |  | HR1174 (Lo-16bits)
1176 | MEAS3:U4 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1177 |  |  |  | HR1176 (Lo-16bits)
1178 | MEAS3:U4 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1179 |  |  |  | HR1178 (Lo-16bits)
1180 | MEAS3:U4 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1181 |  |  |  | HR1180 (Lo-16bits)
1182 | MEAS3:U4 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1183 |  |  |  | HR1182 (Lo-16bits)
1184 | MEAS3:U4 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1185 |  |  |  | HR1184 (Lo-16bits)
1186 | MEAS3:U4 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1187 |  |  |  | HR1186 (Lo-16bits)
1188 | MEAS3:U4 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1189 |  |  |  | HR1188 (Lo-16bits)
1190 | MEAS3:U4 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1191 |  |  |  | HR1190 (Lo-16bits)
1192 | MEAS3:U4 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1193 |  |  |  | HR1192 (Lo-16bits)
1194 | MEAS3:U4 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1195 |  |  |  | HR1194 (Lo-16bits)
1196 | MEAS3:U4 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1197 |  |  |  | HR1196 (Lo-16bits)
1198 | MEAS3:U4 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1199 |  |  |  | HR1198 (Lo-16bits)
1200 | MEAS3:U4 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1201 |  |  |  | HR1200 (Lo-16bits)
1202 | MEAS3:U4 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1203 |  |  |  | HR1202 (Lo-16bits)
1204 | MEAS3:U4 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1205 |  |  |  | HR1204 (Lo-16bits)
1206 | MEAS3:U4 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1207 |  |  |  | HR1206 (Lo-16bits)
1208 | MEAS3:U4 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1209 |  |  |  | HR1208 (Lo-16bits)
1210 | MEAS3:U4 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1211 |  |  |  | HR1210 (Lo-16bits)
1212 | MEAS3:U4 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1213 |  |  |  | HR1212 (Lo-16bits)
1214 | MEAS3:U4 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1215 |  |  |  | HR1214 (Lo-16bits)
1216 | MEAS3:U4 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1217 |  |  |  | HR1216 (Lo-16bits)
1218 | MEAS3:U4 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1219 |  |  |  | HR1218 (Lo-16bits)
1220 | MEAS3:U4 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1221 |  |  |  | HR1220 (Lo-16bits)
1222 | MEAS3:U4 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1223 |  |  |  | HR1222 (Lo-16bits)
1224 | MEAS3:U4 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1225 |  |  |  | HR1224 (Lo-16bits)
1226 | IMERX:IL1 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1227 |  |  |  | HR1226 (Lo-16bits)
1228 | IMERX:IL1 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1229 |  |  |  | HR1228 (Lo-16bits)
1230 | IMERX:IL2 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1231 |  |  |  | HR1230 (Lo-16bits)
1232 | IMERX:IL2 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1233 |  |  |  | HR1232 (Lo-16bits)
1234 | IMERX:IL3 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1235 |  |  |  | HR1234 (Lo-16bits)
1236 | IMERX:IL3 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1237 |  |  |  | HR1236 (Lo-16bits)
1238 | IMERX:Pos.seq. Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1239 |  |  |  | HR1238 (Lo-16bits)
1240 | IMERX:Pos.Seq. Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1241 |  |  |  | HR1240 (Lo-16bits)
1242 | IMERX:I01 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1243 |  |  |  | HR1242 (Lo-16bits)
1244 | IMERX:I01 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1245 |  |  |  | HR1244 (Lo-16bits)
1246 | IMERX:I02 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1247 |  |  |  | HR1246 (Lo-16bits)
1248 | IMERX:I02 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1249 |  |  |  | HR1248 (Lo-16bits)
1250 | IMERX:I01 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1251 |  |  |  | HR1250 (Lo-16bits)
1252 | IMERX:I01 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1253 |  |  |  | HR1252 (Lo-16bits)
1254 | IMERX:I02 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1255 |  |  |  | HR1254 (Lo-16bits)
1256 | IMERX:I02 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1257 |  |  |  | HR1256 (Lo-16bits)
1258 | POW1:Export Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1259 |  |  |  | HR1258 (Lo-16bits)
1260 | POW1:Export Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1261 |  |  |  | HR1260 (Lo-16bits)
1262 | POW1:Import Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1263 |  |  |  | HR1262 (Lo-16bits)
1264 | POW1:Import Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1265 |  |  |  | HR1264 (Lo-16bits)
1266 | POW1:Active Energy (P) Export/Import balance MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1267 |  |  |  | HR1266 (Lo-16bits)
1268 | POW1:Active Energy (P) Export/Import balance kWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1269 |  |  |  | HR1268 (Lo-16bits)
1270 | POW1:Exported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1271 |  |  |  | HR1270 (Lo-16bits)
1272 | POW1:Exported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1273 |  |  |  | HR1272 (Lo-16bits)
1274 | POW1:Imported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1275 |  |  |  | HR1274 (Lo-16bits)
1276 | POW1:Imported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1277 |  |  |  | HR1276 (Lo-16bits)
1278 | POW1:Reactive Energy (Q) balance while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1279 |  |  |  | HR1278 (Lo-16bits)
1280 | POW1:Reactive Energy (Q) balance while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1281 |  |  |  | HR1280 (Lo-16bits)
1282 | POW1:Exported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1283 |  |  |  | HR1282 (Lo-16bits)
1284 | POW1:Exported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1285 |  |  |  | HR1284 (Lo-16bits)
1286 | POW1:Imported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1287 |  |  |  | HR1286 (Lo-16bits)
1288 | POW1:Imported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1289 |  |  |  | HR1288 (Lo-16bits)
1290 | POW1:Reactive Energy (Q) balance while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1291 |  |  |  | HR1290 (Lo-16bits)
1292 | POW1:Reactive Energy (Q) balance while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1293 |  |  |  | HR1292 (Lo-16bits)
1294 | POW1:Apparent Energy (S) while Export (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1295 |  |  |  | HR1294 (Lo-16bits)
1296 | POW1:Apparent Energy (S) while Export (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1297 |  |  |  | HR1296 (Lo-16bits)
1298 | POW1:Apparent Energy (S) while Import (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1299 |  |  |  | HR1298 (Lo-16bits)
1300 | POW1:Apparent Energy (S) while Import (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1301 |  |  |  | HR1300 (Lo-16bits)
1302 | POW1:Apparent Energy (S) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1303 |  |  |  | HR1302 (Lo-16bits)
1304 | POW1:Real Energy (P) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1305 |  |  |  | HR1304 (Lo-16bits)
1306 | POW1:Reactive Energy (Q) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1307 |  |  |  | HR1306 (Lo-16bits)
1308 | POW1:Real Energy (P) Supply (Default supply direction towards busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1309 |  |  |  | HR1308 (Lo-16bits)
1310 | POW1:Reactive Energy (Q) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1311 |  |  |  | HR1310 (Lo-16bits)
1312 | POW1:Real Energy (P) Demand (Default demand direction from busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1313 |  |  |  | HR1312 (Lo-16bits)
1314 | POW1:Reactive Energy (Q) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1315 |  |  |  | HR1314 (Lo-16bits)
1316 | POW1:Reset 3ph Energies | RW | 1 | 0=-;1=Reset
1317 | POW1:POW1 3PH Apparent power (S) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1318 |  |  |  | HR1317 (Lo-16bits)
1319 | POW1:POW1 3PH Apparent power (S MVA) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1320 |  |  |  | HR1319 (Lo-16bits)
1321 | POW1:POW1 3PH Active power (P) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1322 |  |  |  | HR1321 (Lo-16bits)
1323 | POW1:POW1 3PH Active power (P MW) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1324 |  |  |  | HR1323 (Lo-16bits)
1325 | POW1:POW1 3PH Reactive power (Q) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1326 |  |  |  | HR1325 (Lo-16bits)
1327 | POW1:POW1 3PH Reactive power (QMVar) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1328 |  |  |  | HR1327 (Lo-16bits)
1329 | POW1:POW1 3PH Tan(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1330 |  |  |  | HR1329 (Lo-16bits)
1331 | POW1:POW1 3PH Cos(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1332 |  |  |  | HR1331 (Lo-16bits)
1333 | POW1:3PH PF | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1334 |  |  |  | HR1333 (Lo-16bits)
1335 | ASC1:Curve1 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1336 |  |  |  | HR1335 (Lo-16bits)
1337 | ASC1:Curve1 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1338 |  |  |  | HR1337 (Lo-16bits)
1339 | ASC1:Curve2 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1340 |  |  |  | HR1339 (Lo-16bits)
1341 | ASC1:Curve2 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1342 |  |  |  | HR1341 (Lo-16bits)
1343 | ASC1:Curve3 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1344 |  |  |  | HR1343 (Lo-16bits)
1345 | ASC1:Curve3 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1346 |  |  |  | HR1345 (Lo-16bits)
1347 | ASC1:Curve4 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1348 |  |  |  | HR1347 (Lo-16bits)
1349 | ASC1:Curve4 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1350 |  |  |  | HR1349 (Lo-16bits)
1351 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1352 |  |  |  | HR1351 (Lo-16bits)
1353 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1354 |  |  |  | HR1353 (Lo-16bits)
1355 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1356 |  |  |  | HR1355 (Lo-16bits)
1357 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1358 |  |  |  | HR1357 (Lo-16bits)
1359 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1360 |  |  |  | HR1359 (Lo-16bits)
1361 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1362 |  |  |  | HR1361 (Lo-16bits)
1363 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1364 |  |  |  | HR1363 (Lo-16bits)
1365 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1366 |  |  |  | HR1365 (Lo-16bits)
1367 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1368 |  |  |  | HR1367 (Lo-16bits)
1369 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1370 |  |  |  | HR1369 (Lo-16bits)
1371 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1372 |  |  |  | HR1371 (Lo-16bits)
1373 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1374 |  |  |  | HR1373 (Lo-16bits)
1375 | M1CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1376 |  |  |  | HR1375 (Lo-16bits)
1377 | M1CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1378 |  |  |  | HR1377 (Lo-16bits)
1379 | M1CT2:I01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1380 |  |  |  | HR1379 (Lo-16bits)
1381 | M1CT2:I01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1382 |  |  |  | HR1381 (Lo-16bits)
1383 | M1CT3:I02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1384 |  |  |  | HR1383 (Lo-16bits)
1385 | M1CT3:I02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1386 |  |  |  | HR1385 (Lo-16bits)
1387 | M2CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1388 |  |  |  | HR1387 (Lo-16bits)
1389 | M2CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1390 |  |  |  | HR1389 (Lo-16bits)
1391 | M2CT2:I''01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1392 |  |  |  | HR1391 (Lo-16bits)
1393 | M2CT2:I''01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1394 |  |  |  | HR1393 (Lo-16bits)
1395 | M2CT3:I''02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1396 |  |  |  | HR1395 (Lo-16bits)
1397 | M2CT3:I''02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1398 |  |  |  | HR1397 (Lo-16bits)
1399 | M1VT1:VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1400 |  |  |  | HR1399 (Lo-16bits)
1401 | M1VT1:VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1402 |  |  |  | HR1401 (Lo-16bits)
1403 | M1VT1:U3 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1404 |  |  |  | HR1403 (Lo-16bits)
1405 | M1VT1:U3 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1406 |  |  |  | HR1405 (Lo-16bits)
1407 | M1VT1:U4 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1408 |  |  |  | HR1407 (Lo-16bits)
1409 | M1VT1:U4 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1410 |  |  |  | HR1409 (Lo-16bits)
1411 | FREQS:f atm. Protections (when not measurable returns to nominal) | R | 2 | FLOAT [0...75] (Hi-16bits)
1412 |  |  |  | HR1411 (Lo-16bits)
1413 | FREQS:f atm. Display (when not measurable is 0Hz) | R | 2 | FLOAT [0...75] (Hi-16bits)
1414 |  |  |  | HR1413 (Lo-16bits)
1415 | FREQS:SS1.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1416 |  |  |  | HR1415 (Lo-16bits)
1417 | FREQS:SS2.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1418 |  |  |  | HR1417 (Lo-16bits)
1419 | DIGI:DIs (cpu) | R | 2 | 0b=DI1;1b=DI2;2b=DI3; (Hi-16bits)
1420 |  |  |  | HR1419 (Lo-16bits)
1421 | DIGI:DIs (input option 1) | R | 2 | 0b=DI4;1b=DI5;2b=DI6;3b=DI7;4b=DI8;5b=DI9;6b=DI10;7b=DI11 (Hi-16bits)
1422 |  |  |  | HR1421 (Lo-16bits)
1423 | DIGI:DIs (input option 2) | R | 2 | 0b=DI12;1b=DI13;2b=DI14;3b=DI15;4b=DI16;5b=DI17;6b=DI18;7b=DI19 (Hi-16bits)
1424 |  |  |  | HR1423 (Lo-16bits)
1425 | DIGI:DIs (input option 3) | R | 2 | 0b=DI20;1b=DI21;2b=DI22;3b=DI23;4b=DI24;5b=DI25;6b=DI26;7b=DI27 (Hi-16bits)
1426 |  |  |  | HR1425 (Lo-16bits)
1427 | DIGI:DIs (input option 4) | R | 2 | 0b=D28;1b=DI29;2b=DI30;3b=DI31;4b=DI32;5b=DI33;6b=DI34;7b=DI35 (Hi-16bits)
1428 |  |  |  | HR1427 (Lo-16bits)
1429 | DIGI:DIs (input option 5) | R | 2 | 0b=DI36;1b=DI37;2b=DI38;3b=DI39;4b=DI40;5b=DI41;6b=DI42;7b=DI43 (Hi-16bits)
1430 |  |  |  | HR1429 (Lo-16bits)
1431 | DIGI:DIs (input option 6) | R | 2 | 0b=DI44;1b=DI45;2b=DI46;3b=DI47;4b=DI48;5b=DI49;6b=DI50;7b=DI51 (Hi-16bits)
1432 |  |  |  | HR1431 (Lo-16bits)
1433 | DIGI:Dis 1-32 | R | 2 | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32 (Hi-16bits)
1434 |  |  |  | HR1433 (Lo-16bits)
1435 | DIGI:Dis 33-64 | R | 2 | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51 (Hi-16bits)
1436 |  |  |  | HR1435 (Lo-16bits)
1437 | DIGI:DI1 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1438 |  |  |  | HR1437 (Lo-16bits)
1439 | DIGI:DI1 Counter Clear | RW | 1 | 0=-;1=Clear
1440 | DIGI:DI2 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1441 |  |  |  | HR1440 (Lo-16bits)
1442 | DIGI:DI2 Counter Clear | RW | 1 | 0=-;1=Clear
1443 | DIGI:DI3 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1444 |  |  |  | HR1443 (Lo-16bits)
1445 | DIGI:DI3 Counter Clear | RW | 1 | 0=-;1=Clear
1446 | DIGI:DI4 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1447 |  |  |  | HR1446 (Lo-16bits)
1448 | DIGI:DI4 Counter Clear | RW | 1 | 0=-;1=Clear
1449 | DIGI:DI5 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1450 |  |  |  | HR1449 (Lo-16bits)
1451 | DIGI:DI5 Counter Clear | RW | 1 | 0=-;1=Clear
1452 | DIGI:DI6 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1453 |  |  |  | HR1452 (Lo-16bits)
1454 | DIGI:DI6 Counter Clear | RW | 1 | 0=-;1=Clear
1455 | DIGI:DI7 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1456 |  |  |  | HR1455 (Lo-16bits)
1457 | DIGI:DI7 Counter Clear | RW | 1 | 0=-;1=Clear
1458 | DIGI:DI8 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1459 |  |  |  | HR1458 (Lo-16bits)
1460 | DIGI:DI8 Counter Clear | RW | 1 | 0=-;1=Clear
1461 | DIGI:DI9 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1462 |  |  |  | HR1461 (Lo-16bits)
1463 | DIGI:DI9 Counter Clear | RW | 1 | 0=-;1=Clear
1464 | DIGI:DI10 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1465 |  |  |  | HR1464 (Lo-16bits)
1466 | DIGI:DI10 Counter Clear | RW | 1 | 0=-;1=Clear
1467 | DIGI:DI11 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1468 |  |  |  | HR1467 (Lo-16bits)
1469 | DIGI:DI11 Counter Clear | RW | 1 | 0=-;1=Clear
1470 | DIGI:DI12 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1471 |  |  |  | HR1470 (Lo-16bits)
1472 | DIGI:DI12 Counter Clear | RW | 1 | 0=-;1=Clear
1473 | DIGI:DI13 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1474 |  |  |  | HR1473 (Lo-16bits)
1475 | DIGI:DI13 Counter Clear | RW | 1 | 0=-;1=Clear
1476 | DIGI:DI14 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1477 |  |  |  | HR1476 (Lo-16bits)
1478 | DIGI:DI14 Counter Clear | RW | 1 | 0=-;1=Clear
1479 | DIGI:DI15 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1480 |  |  |  | HR1479 (Lo-16bits)
1481 | DIGI:DI15 Counter Clear | RW | 1 | 0=-;1=Clear
1482 | DIGI:DI16 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1483 |  |  |  | HR1482 (Lo-16bits)
1484 | DIGI:DI16 Counter Clear | RW | 1 | 0=-;1=Clear
1485 | DIGI:DI17 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1486 |  |  |  | HR1485 (Lo-16bits)
1487 | DIGI:DI17 Counter Clear | RW | 1 | 0=-;1=Clear
1488 | DIGI:DI18 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1489 |  |  |  | HR1488 (Lo-16bits)
1490 | DIGI:DI18 Counter Clear | RW | 1 | 0=-;1=Clear
1491 | DIGI:DI19 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1492 |  |  |  | HR1491 (Lo-16bits)
1493 | DIGI:DI19 Counter Clear | RW | 1 | 0=-;1=Clear
1494 | DIGI:DI20 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1495 |  |  |  | HR1494 (Lo-16bits)
1496 | DIGI:DI20 Counter Clear | RW | 1 | 0=-;1=Clear
1497 | DIGI:DI21 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1498 |  |  |  | HR1497 (Lo-16bits)
1499 | DIGI:DI21 Counter Clear | RW | 1 | 0=-;1=Clear
1500 | DIGI:DI22 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1501 |  |  |  | HR1500 (Lo-16bits)
1502 | DIGI:DI22 Counter Clear | RW | 1 | 0=-;1=Clear
1503 | DIGI:DI23 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1504 |  |  |  | HR1503 (Lo-16bits)
1505 | DIGI:DI23 Counter Clear | RW | 1 | 0=-;1=Clear
1506 | DIGI:DI24 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1507 |  |  |  | HR1506 (Lo-16bits)
1508 | DIGI:DI24 Counter Clear | RW | 1 | 0=-;1=Clear
1509 | DIGI:DI25 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1510 |  |  |  | HR1509 (Lo-16bits)
1511 | DIGI:DI25 Counter Clear | RW | 1 | 0=-;1=Clear
1512 | DIGI:DI26 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1513 |  |  |  | HR1512 (Lo-16bits)
1514 | DIGI:DI26 Counter Clear | RW | 1 | 0=-;1=Clear
1515 | DIGI:DI27 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1516 |  |  |  | HR1515 (Lo-16bits)
1517 | DIGI:DI27 Counter Clear | RW | 1 | 0=-;1=Clear
1518 | DIGI:DI28 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1519 |  |  |  | HR1518 (Lo-16bits)
1520 | DIGI:DI28 Counter Clear | RW | 1 | 0=-;1=Clear
1521 | DIGI:DI29 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1522 |  |  |  | HR1521 (Lo-16bits)
1523 | DIGI:DI29 Counter Clear | RW | 1 | 0=-;1=Clear
1524 | DIGI:DI30 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1525 |  |  |  | HR1524 (Lo-16bits)
1526 | DIGI:DI30 Counter Clear | RW | 1 | 0=-;1=Clear
1527 | DIGI:DI31 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1528 |  |  |  | HR1527 (Lo-16bits)
1529 | DIGI:DI31 Counter Clear | RW | 1 | 0=-;1=Clear
1530 | DIGI:DI32 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1531 |  |  |  | HR1530 (Lo-16bits)
1532 | DIGI:DI32 Counter Clear | RW | 1 | 0=-;1=Clear
1533 | DIGI:DI33 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1534 |  |  |  | HR1533 (Lo-16bits)
1535 | DIGI:DI33 Counter Clear | RW | 1 | 0=-;1=Clear
1536 | DIGI:DI34 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1537 |  |  |  | HR1536 (Lo-16bits)
1538 | DIGI:DI34 Counter Clear | RW | 1 | 0=-;1=Clear
1539 | DIGI:DI35 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1540 |  |  |  | HR1539 (Lo-16bits)
1541 | DIGI:DI35 Counter Clear | RW | 1 | 0=-;1=Clear
1542 | DIGI:DI36 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1543 |  |  |  | HR1542 (Lo-16bits)
1544 | DIGI:DI36 Counter Clear | RW | 1 | 0=-;1=Clear
1545 | DIGI:DI37 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1546 |  |  |  | HR1545 (Lo-16bits)
1547 | DIGI:DI37 Counter Clear | RW | 1 | 0=-;1=Clear
1548 | DIGI:DI38 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1549 |  |  |  | HR1548 (Lo-16bits)
1550 | DIGI:DI38 Counter Clear | RW | 1 | 0=-;1=Clear
1551 | DIGI:DI39 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1552 |  |  |  | HR1551 (Lo-16bits)
1553 | DIGI:DI39 Counter Clear | RW | 1 | 0=-;1=Clear
1554 | DIGI:DI40 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1555 |  |  |  | HR1554 (Lo-16bits)
1556 | DIGI:DI40 Counter Clear | RW | 1 | 0=-;1=Clear
1557 | DIGI:DI41 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1558 |  |  |  | HR1557 (Lo-16bits)
1559 | DIGI:DI41 Counter Clear | RW | 1 | 0=-;1=Clear
1560 | DIGI:DI42 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1561 |  |  |  | HR1560 (Lo-16bits)
1562 | DIGI:DI42 Counter Clear | RW | 1 | 0=-;1=Clear
1563 | DIGI:DI43 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1564 |  |  |  | HR1563 (Lo-16bits)
1565 | DIGI:DI43 Counter Clear | RW | 1 | 0=-;1=Clear
1566 | DIGI:DI44 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1567 |  |  |  | HR1566 (Lo-16bits)
1568 | DIGI:DI44 Counter Clear | RW | 1 | 0=-;1=Clear
1569 | DIGI:DI45 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1570 |  |  |  | HR1569 (Lo-16bits)
1571 | DIGI:DI45 Counter Clear | RW | 1 | 0=-;1=Clear
1572 | DIGI:DI46 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1573 |  |  |  | HR1572 (Lo-16bits)
1574 | DIGI:DI46 Counter Clear | RW | 1 | 0=-;1=Clear
1575 | DIGI:DI47 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1576 |  |  |  | HR1575 (Lo-16bits)
1577 | DIGI:DI47 Counter Clear | RW | 1 | 0=-;1=Clear
1578 | DIGI:DI48 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1579 |  |  |  | HR1578 (Lo-16bits)
1580 | DIGI:DI48 Counter Clear | RW | 1 | 0=-;1=Clear
1581 | DIGI:DI49 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1582 |  |  |  | HR1581 (Lo-16bits)
1583 | DIGI:DI49 Counter Clear | RW | 1 | 0=-;1=Clear
1584 | DIGI:DI50 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1585 |  |  |  | HR1584 (Lo-16bits)
1586 | DIGI:DI50 Counter Clear | RW | 1 | 0=-;1=Clear
1587 | DIGI:DI51 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1588 |  |  |  | HR1587 (Lo-16bits)
1589 | DIGI:DI51 Counter Clear | RW | 1 | 0=-;1=Clear
1590 | RELE:Outputs status | R | 2 | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15 (Hi-16bits)
1591 |  |  |  | HR1590 (Lo-16bits)
1592 | SGS:Active setting group | R | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
1593 | SGS:Force SG | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1594 | SGS:Force SG change | RW | 1 | 0=Disabled;1=Enabled
1595 | SGS:Used setting groups | RW | 1 | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
1596 | SGS:Remote SG change | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1597 | CTRL:Local/Remote status | R | 1 | 0=Remote;1=Local
1598 | DEV:Serial number | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1599 |  |  |  | HR1598 (Lo-16bits)
1600 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1601 |  |  |  | HR1600 (Lo-16bits)
1602 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1603 |  |  |  | HR1602 (Lo-16bits)
1604 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1605 |  |  |  | HR1604 (Lo-16bits)
1606 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1607 |  |  |  | HR1606 (Lo-16bits)
1608 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1609 |  |  |  | HR1608 (Lo-16bits)
1610 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1611 |  |  |  | HR1610 (Lo-16bits)
1612 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1613 |  |  |  | HR1612 (Lo-16bits)
1614 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1615 |  |  |  | HR1614 (Lo-16bits)
1616 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1617 |  |  |  | HR1616 (Lo-16bits)
1618 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1619 |  |  |  | HR1618 (Lo-16bits)
1620 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1621 |  |  |  | HR1620 (Lo-16bits)
1622 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1623 |  |  |  | HR1622 (Lo-16bits)
1624 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1625 |  |  |  | HR1624 (Lo-16bits)
1626 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1627 |  |  |  | HR1626 (Lo-16bits)
1628 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1629 |  |  |  | HR1628 (Lo-16bits)
1630 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1631 |  |  |  | HR1630 (Lo-16bits)
1632 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1633 |  |  |  | HR1632 (Lo-16bits)
1634 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1635 |  |  |  | HR1634 (Lo-16bits)
1636 | DIAG:Configuration changed | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1637 |  |  |  | HR1636 (Lo-16bits)
1638 | MBTCP:Enable mapped setting value modification through Modbus | RW | 1 | 0=Disabled;1=Enabled
1639 | MBIO:MBIO ModA Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1640 |  |  |  | HR1639 (Lo-16bits)
1641 | MBIO:MBIO ModA Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1642 |  |  |  | HR1641 (Lo-16bits)
1643 | MBIO:MBIO ModA Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1644 |  |  |  | HR1643 (Lo-16bits)
1645 | MBIO:MBIO ModA Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1646 |  |  |  | HR1645 (Lo-16bits)
1647 | MBIO:MBIO ModA Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1648 |  |  |  | HR1647 (Lo-16bits)
1649 | MBIO:MBIO ModA Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1650 |  |  |  | HR1649 (Lo-16bits)
1651 | MBIO:MBIO ModA Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1652 |  |  |  | HR1651 (Lo-16bits)
1653 | MBIO:MBIO ModA Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1654 |  |  |  | HR1653 (Lo-16bits)
1655 | MBIO:MBIO ModB Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1656 |  |  |  | HR1655 (Lo-16bits)
1657 | MBIO:MBIO ModB Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1658 |  |  |  | HR1657 (Lo-16bits)
1659 | MBIO:MBIO ModB Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1660 |  |  |  | HR1659 (Lo-16bits)
1661 | MBIO:MBIO ModB Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1662 |  |  |  | HR1661 (Lo-16bits)
1663 | MBIO:MBIO ModB Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1664 |  |  |  | HR1663 (Lo-16bits)
1665 | MBIO:MBIO ModB Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1666 |  |  |  | HR1665 (Lo-16bits)
1667 | MBIO:MBIO ModB Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1668 |  |  |  | HR1667 (Lo-16bits)
1669 | MBIO:MBIO ModB Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1670 |  |  |  | HR1669 (Lo-16bits)
1671 | MBIO:MBIO ModC Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1672 |  |  |  | HR1671 (Lo-16bits)
1673 | MBIO:MBIO ModC Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1674 |  |  |  | HR1673 (Lo-16bits)
1675 | MBIO:MBIO ModC Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1676 |  |  |  | HR1675 (Lo-16bits)
1677 | MBIO:MBIO ModC Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1678 |  |  |  | HR1677 (Lo-16bits)
1679 | MBIO:MBIO ModC Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1680 |  |  |  | HR1679 (Lo-16bits)
1681 | MBIO:MBIO ModC Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1682 |  |  |  | HR1681 (Lo-16bits)
1683 | MBIO:MBIO ModC Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1684 |  |  |  | HR1683 (Lo-16bits)
1685 | MBIO:MBIO ModC Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1686 |  |  |  | HR1685 (Lo-16bits)
1687 | LOGIC:Reset Latches | RW | 1 | 0=-;1=Reset
1688 | LOGIC1:Logic out 1-32 | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
1689 |  |  |  | HR1688 (Lo-16bits)
1690 | NOC1:I> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1691 | NOC1:I> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1692 | NOC1:I> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1693 | NOC1:I> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1694 | NOC1:I> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1695 | NOC1:I> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1696 |  |  |  | HR1695 (Lo-16bits)
1697 | NOC1:I> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1698 |  |  |  | HR1697 (Lo-16bits)
1699 | NOC1:I> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1700 |  |  |  | HR1699 (Lo-16bits)
1701 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1702 |  |  |  | HR1701 (Lo-16bits)
1703 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1704 |  |  |  | HR1703 (Lo-16bits)
1705 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1706 |  |  |  | HR1705 (Lo-16bits)
1707 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1708 |  |  |  | HR1707 (Lo-16bits)
1709 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1710 |  |  |  | HR1709 (Lo-16bits)
1711 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1712 |  |  |  | HR1711 (Lo-16bits)
1713 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1714 |  |  |  | HR1713 (Lo-16bits)
1715 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1716 |  |  |  | HR1715 (Lo-16bits)
1717 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1718 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1719 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1720 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1721 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1722 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1723 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1724 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1725 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1726 |  |  |  | HR1725 (Lo-16bits)
1727 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1728 |  |  |  | HR1727 (Lo-16bits)
1729 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1730 |  |  |  | HR1729 (Lo-16bits)
1731 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1732 |  |  |  | HR1731 (Lo-16bits)
1733 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1734 |  |  |  | HR1733 (Lo-16bits)
1735 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1736 |  |  |  | HR1735 (Lo-16bits)
1737 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1738 |  |  |  | HR1737 (Lo-16bits)
1739 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1740 |  |  |  | HR1739 (Lo-16bits)
1741 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1742 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1743 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1744 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1745 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1746 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1747 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1748 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1749 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1750 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1751 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1752 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1753 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1754 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1755 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1756 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1757 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1758 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1759 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1760 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1761 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1762 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1763 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1764 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1765 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1766 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1767 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1768 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1769 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1770 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1771 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1772 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1773 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1774 |  |  |  | HR1773 (Lo-16bits)
1775 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1776 |  |  |  | HR1775 (Lo-16bits)
1777 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1778 |  |  |  | HR1777 (Lo-16bits)
1779 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1780 |  |  |  | HR1779 (Lo-16bits)
1781 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1782 |  |  |  | HR1781 (Lo-16bits)
1783 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1784 |  |  |  | HR1783 (Lo-16bits)
1785 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1786 |  |  |  | HR1785 (Lo-16bits)
1787 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1788 |  |  |  | HR1787 (Lo-16bits)
1789 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1790 |  |  |  | HR1789 (Lo-16bits)
1791 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1792 |  |  |  | HR1791 (Lo-16bits)
1793 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1794 |  |  |  | HR1793 (Lo-16bits)
1795 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1796 |  |  |  | HR1795 (Lo-16bits)
1797 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1798 |  |  |  | HR1797 (Lo-16bits)
1799 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1800 |  |  |  | HR1799 (Lo-16bits)
1801 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1802 |  |  |  | HR1801 (Lo-16bits)
1803 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1804 |  |  |  | HR1803 (Lo-16bits)
1805 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1806 |  |  |  | HR1805 (Lo-16bits)
1807 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1808 |  |  |  | HR1807 (Lo-16bits)
1809 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1810 |  |  |  | HR1809 (Lo-16bits)
1811 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1812 |  |  |  | HR1811 (Lo-16bits)
1813 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1814 |  |  |  | HR1813 (Lo-16bits)
1815 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1816 |  |  |  | HR1815 (Lo-16bits)
1817 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1818 |  |  |  | HR1817 (Lo-16bits)
1819 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1820 |  |  |  | HR1819 (Lo-16bits)
1821 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1822 |  |  |  | HR1821 (Lo-16bits)
1823 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1824 |  |  |  | HR1823 (Lo-16bits)
1825 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1826 |  |  |  | HR1825 (Lo-16bits)
1827 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1828 |  |  |  | HR1827 (Lo-16bits)
1829 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1830 |  |  |  | HR1829 (Lo-16bits)
1831 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1832 |  |  |  | HR1831 (Lo-16bits)
1833 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1834 |  |  |  | HR1833 (Lo-16bits)
1835 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1836 |  |  |  | HR1835 (Lo-16bits)
1837 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1838 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1839 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1840 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1841 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1842 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1843 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1844 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1845 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1846 |  |  |  | HR1845 (Lo-16bits)
1847 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1848 |  |  |  | HR1847 (Lo-16bits)
1849 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1850 |  |  |  | HR1849 (Lo-16bits)
1851 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1852 |  |  |  | HR1851 (Lo-16bits)
1853 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1854 |  |  |  | HR1853 (Lo-16bits)
1855 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1856 |  |  |  | HR1855 (Lo-16bits)
1857 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1858 |  |  |  | HR1857 (Lo-16bits)
1859 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1860 |  |  |  | HR1859 (Lo-16bits)
1861 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1862 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1863 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1864 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1865 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1866 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1867 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1868 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1869 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1870 |  |  |  | HR1869 (Lo-16bits)
1871 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1872 |  |  |  | HR1871 (Lo-16bits)
1873 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1874 |  |  |  | HR1873 (Lo-16bits)
1875 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1876 |  |  |  | HR1875 (Lo-16bits)
1877 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1878 |  |  |  | HR1877 (Lo-16bits)
1879 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1880 |  |  |  | HR1879 (Lo-16bits)
1881 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1882 |  |  |  | HR1881 (Lo-16bits)
1883 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1884 |  |  |  | HR1883 (Lo-16bits)
1885 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1886 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1887 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1888 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1889 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1890 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1891 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1892 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1893 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1894 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1895 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1896 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1897 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1898 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1899 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1900 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1901 | NOC1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
1902 |  |  |  | HR1901 (Lo-16bits)
1903 | NOC1:Delay type | RW | 1 | 0=DT;1=IDMT
1904 | NOC1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
1905 |  |  |  | HR1904 (Lo-16bits)
1906 | NOC1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
1907 | NOC1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1908 | NOC1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1909 | NOC1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
1910 | NOC1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
1911 |  |  |  | HR1910 (Lo-16bits)
1912 | NOC1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
1913 |  |  |  | HR1912 (Lo-16bits)
1914 | NOC1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
1915 |  |  |  | HR1914 (Lo-16bits)
1916 | NOC1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
1917 |  |  |  | HR1916 (Lo-16bits)
1918 | NOC1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
1919 | NOC1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
1920 | NOC2:I>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1921 | NOC2:I>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1922 | NOC2:I>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1923 | NOC2:I>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1924 | NOC2:I>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1925 | NOC2:I>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1926 |  |  |  | HR1925 (Lo-16bits)
1927 | NOC2:I>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1928 |  |  |  | HR1927 (Lo-16bits)
1929 | NOC2:I>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1930 |  |  |  | HR1929 (Lo-16bits)
1931 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1932 |  |  |  | HR1931 (Lo-16bits)
1933 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1934 |  |  |  | HR1933 (Lo-16bits)
1935 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1936 |  |  |  | HR1935 (Lo-16bits)
1937 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1938 |  |  |  | HR1937 (Lo-16bits)
1939 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1940 |  |  |  | HR1939 (Lo-16bits)
1941 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1942 |  |  |  | HR1941 (Lo-16bits)
1943 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1944 |  |  |  | HR1943 (Lo-16bits)
1945 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1946 |  |  |  | HR1945 (Lo-16bits)
1947 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1948 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1949 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1950 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1951 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1952 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1953 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1954 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1955 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1956 |  |  |  | HR1955 (Lo-16bits)
1957 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1958 |  |  |  | HR1957 (Lo-16bits)
1959 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1960 |  |  |  | HR1959 (Lo-16bits)
1961 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1962 |  |  |  | HR1961 (Lo-16bits)
1963 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1964 |  |  |  | HR1963 (Lo-16bits)
1965 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1966 |  |  |  | HR1965 (Lo-16bits)
1967 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1968 |  |  |  | HR1967 (Lo-16bits)
1969 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1970 |  |  |  | HR1969 (Lo-16bits)
1971 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1972 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1973 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1974 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1975 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1976 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1977 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1978 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1979 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1980 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1981 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1982 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1983 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1984 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1985 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1986 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1987 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1988 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1989 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1990 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1991 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1992 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1993 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1994 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1995 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1996 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1997 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1998 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1999 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2000 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2001 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2002 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2003 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2004 |  |  |  | HR2003 (Lo-16bits)
2005 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2006 |  |  |  | HR2005 (Lo-16bits)
2007 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2008 |  |  |  | HR2007 (Lo-16bits)
2009 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2010 |  |  |  | HR2009 (Lo-16bits)
2011 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2012 |  |  |  | HR2011 (Lo-16bits)
2013 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2014 |  |  |  | HR2013 (Lo-16bits)
2015 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2016 |  |  |  | HR2015 (Lo-16bits)
2017 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2018 |  |  |  | HR2017 (Lo-16bits)
2019 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2020 |  |  |  | HR2019 (Lo-16bits)
2021 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2022 |  |  |  | HR2021 (Lo-16bits)
2023 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2024 |  |  |  | HR2023 (Lo-16bits)
2025 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2026 |  |  |  | HR2025 (Lo-16bits)
2027 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2028 |  |  |  | HR2027 (Lo-16bits)
2029 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2030 |  |  |  | HR2029 (Lo-16bits)
2031 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2032 |  |  |  | HR2031 (Lo-16bits)
2033 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2034 |  |  |  | HR2033 (Lo-16bits)
2035 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2036 |  |  |  | HR2035 (Lo-16bits)
2037 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2038 |  |  |  | HR2037 (Lo-16bits)
2039 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2040 |  |  |  | HR2039 (Lo-16bits)
2041 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2042 |  |  |  | HR2041 (Lo-16bits)
2043 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2044 |  |  |  | HR2043 (Lo-16bits)
2045 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2046 |  |  |  | HR2045 (Lo-16bits)
2047 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2048 |  |  |  | HR2047 (Lo-16bits)
2049 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2050 |  |  |  | HR2049 (Lo-16bits)
2051 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2052 |  |  |  | HR2051 (Lo-16bits)
2053 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2054 |  |  |  | HR2053 (Lo-16bits)
2055 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2056 |  |  |  | HR2055 (Lo-16bits)
2057 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2058 |  |  |  | HR2057 (Lo-16bits)
2059 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2060 |  |  |  | HR2059 (Lo-16bits)
2061 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2062 |  |  |  | HR2061 (Lo-16bits)
2063 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2064 |  |  |  | HR2063 (Lo-16bits)
2065 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2066 |  |  |  | HR2065 (Lo-16bits)
2067 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2068 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2069 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2070 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2071 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2072 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2073 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2074 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2075 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2076 |  |  |  | HR2075 (Lo-16bits)
2077 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2078 |  |  |  | HR2077 (Lo-16bits)
2079 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2080 |  |  |  | HR2079 (Lo-16bits)
2081 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2082 |  |  |  | HR2081 (Lo-16bits)
2083 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2084 |  |  |  | HR2083 (Lo-16bits)
2085 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2086 |  |  |  | HR2085 (Lo-16bits)
2087 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2088 |  |  |  | HR2087 (Lo-16bits)
2089 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2090 |  |  |  | HR2089 (Lo-16bits)
2091 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2092 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2093 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2094 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2095 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2096 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2097 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2098 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2099 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2100 |  |  |  | HR2099 (Lo-16bits)
2101 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2102 |  |  |  | HR2101 (Lo-16bits)
2103 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2104 |  |  |  | HR2103 (Lo-16bits)
2105 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2106 |  |  |  | HR2105 (Lo-16bits)
2107 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2108 |  |  |  | HR2107 (Lo-16bits)
2109 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2110 |  |  |  | HR2109 (Lo-16bits)
2111 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2112 |  |  |  | HR2111 (Lo-16bits)
2113 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2114 |  |  |  | HR2113 (Lo-16bits)
2115 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2116 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2117 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2118 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2119 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2120 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2121 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2122 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2123 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2124 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2125 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2126 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2127 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2128 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2129 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2130 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2131 | NOC2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2132 |  |  |  | HR2131 (Lo-16bits)
2133 | NOC2:Delay type | RW | 1 | 0=DT;1=IDMT
2134 | NOC2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2135 |  |  |  | HR2134 (Lo-16bits)
2136 | NOC2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2137 | NOC2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2138 | NOC2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2139 | NOC2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2140 | NOC2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2141 |  |  |  | HR2140 (Lo-16bits)
2142 | NOC2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2143 |  |  |  | HR2142 (Lo-16bits)
2144 | NOC2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2145 |  |  |  | HR2144 (Lo-16bits)
2146 | NOC2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2147 |  |  |  | HR2146 (Lo-16bits)
2148 | NOC2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2149 | NOC2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2150 | NOC3:I>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2151 | NOC3:I>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2152 | NOC3:I>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2153 | NOC3:I>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2154 | NOC3:I>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2155 | NOC3:I>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2156 |  |  |  | HR2155 (Lo-16bits)
2157 | NOC3:I>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2158 |  |  |  | HR2157 (Lo-16bits)
2159 | NOC3:I>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2160 |  |  |  | HR2159 (Lo-16bits)
2161 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2162 |  |  |  | HR2161 (Lo-16bits)
2163 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2164 |  |  |  | HR2163 (Lo-16bits)
2165 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2166 |  |  |  | HR2165 (Lo-16bits)
2167 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2168 |  |  |  | HR2167 (Lo-16bits)
2169 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2170 |  |  |  | HR2169 (Lo-16bits)
2171 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2172 |  |  |  | HR2171 (Lo-16bits)
2173 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2174 |  |  |  | HR2173 (Lo-16bits)
2175 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2176 |  |  |  | HR2175 (Lo-16bits)
2177 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2178 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2179 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2180 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2181 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2182 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2183 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2184 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2185 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2186 |  |  |  | HR2185 (Lo-16bits)
2187 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2188 |  |  |  | HR2187 (Lo-16bits)
2189 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2190 |  |  |  | HR2189 (Lo-16bits)
2191 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2192 |  |  |  | HR2191 (Lo-16bits)
2193 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2194 |  |  |  | HR2193 (Lo-16bits)
2195 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2196 |  |  |  | HR2195 (Lo-16bits)
2197 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2198 |  |  |  | HR2197 (Lo-16bits)
2199 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2200 |  |  |  | HR2199 (Lo-16bits)
2201 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2202 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2203 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2204 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2205 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2206 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2207 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2208 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2209 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2210 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2211 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2212 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2213 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2214 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2215 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2216 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2217 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2218 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2219 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2220 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2221 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2222 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2223 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2224 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2225 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2226 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2227 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2228 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2229 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2230 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2231 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2232 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2233 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2234 |  |  |  | HR2233 (Lo-16bits)
2235 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2236 |  |  |  | HR2235 (Lo-16bits)
2237 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2238 |  |  |  | HR2237 (Lo-16bits)
2239 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2240 |  |  |  | HR2239 (Lo-16bits)
2241 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2242 |  |  |  | HR2241 (Lo-16bits)
2243 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2244 |  |  |  | HR2243 (Lo-16bits)
2245 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2246 |  |  |  | HR2245 (Lo-16bits)
2247 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2248 |  |  |  | HR2247 (Lo-16bits)
2249 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2250 |  |  |  | HR2249 (Lo-16bits)
2251 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2252 |  |  |  | HR2251 (Lo-16bits)
2253 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2254 |  |  |  | HR2253 (Lo-16bits)
2255 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2256 |  |  |  | HR2255 (Lo-16bits)
2257 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2258 |  |  |  | HR2257 (Lo-16bits)
2259 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2260 |  |  |  | HR2259 (Lo-16bits)
2261 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2262 |  |  |  | HR2261 (Lo-16bits)
2263 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2264 |  |  |  | HR2263 (Lo-16bits)
2265 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2266 |  |  |  | HR2265 (Lo-16bits)
2267 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2268 |  |  |  | HR2267 (Lo-16bits)
2269 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2270 |  |  |  | HR2269 (Lo-16bits)
2271 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2272 |  |  |  | HR2271 (Lo-16bits)
2273 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2274 |  |  |  | HR2273 (Lo-16bits)
2275 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2276 |  |  |  | HR2275 (Lo-16bits)
2277 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2278 |  |  |  | HR2277 (Lo-16bits)
2279 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2280 |  |  |  | HR2279 (Lo-16bits)
2281 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2282 |  |  |  | HR2281 (Lo-16bits)
2283 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2284 |  |  |  | HR2283 (Lo-16bits)
2285 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2286 |  |  |  | HR2285 (Lo-16bits)
2287 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2288 |  |  |  | HR2287 (Lo-16bits)
2289 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2290 |  |  |  | HR2289 (Lo-16bits)
2291 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2292 |  |  |  | HR2291 (Lo-16bits)
2293 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2294 |  |  |  | HR2293 (Lo-16bits)
2295 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2296 |  |  |  | HR2295 (Lo-16bits)
2297 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2298 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2299 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2300 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2301 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2302 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2303 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2304 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2305 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2306 |  |  |  | HR2305 (Lo-16bits)
2307 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2308 |  |  |  | HR2307 (Lo-16bits)
2309 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2310 |  |  |  | HR2309 (Lo-16bits)
2311 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2312 |  |  |  | HR2311 (Lo-16bits)
2313 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2314 |  |  |  | HR2313 (Lo-16bits)
2315 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2316 |  |  |  | HR2315 (Lo-16bits)
2317 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2318 |  |  |  | HR2317 (Lo-16bits)
2319 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2320 |  |  |  | HR2319 (Lo-16bits)
2321 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2322 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2323 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2324 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2325 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2326 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2327 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2328 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2329 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2330 |  |  |  | HR2329 (Lo-16bits)
2331 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2332 |  |  |  | HR2331 (Lo-16bits)
2333 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2334 |  |  |  | HR2333 (Lo-16bits)
2335 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2336 |  |  |  | HR2335 (Lo-16bits)
2337 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2338 |  |  |  | HR2337 (Lo-16bits)
2339 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2340 |  |  |  | HR2339 (Lo-16bits)
2341 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2342 |  |  |  | HR2341 (Lo-16bits)
2343 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2344 |  |  |  | HR2343 (Lo-16bits)
2345 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2346 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2347 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2348 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2349 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2350 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2351 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2352 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2353 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2354 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2355 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2356 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2357 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2358 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2359 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2360 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2361 | NOC3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2362 |  |  |  | HR2361 (Lo-16bits)
2363 | NOC3:Delay type | RW | 1 | 0=DT;1=IDMT
2364 | NOC3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2365 |  |  |  | HR2364 (Lo-16bits)
2366 | NOC3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2367 | NOC3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2368 | NOC3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2369 | NOC3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2370 | NOC3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2371 |  |  |  | HR2370 (Lo-16bits)
2372 | NOC3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2373 |  |  |  | HR2372 (Lo-16bits)
2374 | NOC3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2375 |  |  |  | HR2374 (Lo-16bits)
2376 | NOC3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2377 |  |  |  | HR2376 (Lo-16bits)
2378 | NOC3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2379 | NOC3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2380 | NOC4:I>>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2381 | NOC4:I>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2382 | NOC4:I>>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2383 | NOC4:I>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2384 | NOC4:I>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2385 | NOC4:I>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2386 |  |  |  | HR2385 (Lo-16bits)
2387 | NOC4:I>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2388 |  |  |  | HR2387 (Lo-16bits)
2389 | NOC4:I>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2390 |  |  |  | HR2389 (Lo-16bits)
2391 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2392 |  |  |  | HR2391 (Lo-16bits)
2393 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2394 |  |  |  | HR2393 (Lo-16bits)
2395 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2396 |  |  |  | HR2395 (Lo-16bits)
2397 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2398 |  |  |  | HR2397 (Lo-16bits)
2399 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2400 |  |  |  | HR2399 (Lo-16bits)
2401 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2402 |  |  |  | HR2401 (Lo-16bits)
2403 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2404 |  |  |  | HR2403 (Lo-16bits)
2405 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2406 |  |  |  | HR2405 (Lo-16bits)
2407 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2408 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2409 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2410 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2411 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2412 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2413 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2414 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2415 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2416 |  |  |  | HR2415 (Lo-16bits)
2417 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2418 |  |  |  | HR2417 (Lo-16bits)
2419 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2420 |  |  |  | HR2419 (Lo-16bits)
2421 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2422 |  |  |  | HR2421 (Lo-16bits)
2423 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2424 |  |  |  | HR2423 (Lo-16bits)
2425 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2426 |  |  |  | HR2425 (Lo-16bits)
2427 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2428 |  |  |  | HR2427 (Lo-16bits)
2429 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2430 |  |  |  | HR2429 (Lo-16bits)
2431 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2432 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2433 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2434 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2435 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2436 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2437 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2438 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2439 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2440 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2441 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2442 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2443 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2444 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2445 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2446 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2447 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2448 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2449 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2450 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2451 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2452 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2453 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2454 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2455 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2456 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2457 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2458 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2459 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2460 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2461 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2462 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2463 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2464 |  |  |  | HR2463 (Lo-16bits)
2465 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2466 |  |  |  | HR2465 (Lo-16bits)
2467 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2468 |  |  |  | HR2467 (Lo-16bits)
2469 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2470 |  |  |  | HR2469 (Lo-16bits)
2471 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2472 |  |  |  | HR2471 (Lo-16bits)
2473 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2474 |  |  |  | HR2473 (Lo-16bits)
2475 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2476 |  |  |  | HR2475 (Lo-16bits)
2477 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2478 |  |  |  | HR2477 (Lo-16bits)
2479 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2480 |  |  |  | HR2479 (Lo-16bits)
2481 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2482 |  |  |  | HR2481 (Lo-16bits)
2483 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2484 |  |  |  | HR2483 (Lo-16bits)
2485 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2486 |  |  |  | HR2485 (Lo-16bits)
2487 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2488 |  |  |  | HR2487 (Lo-16bits)
2489 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2490 |  |  |  | HR2489 (Lo-16bits)
2491 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2492 |  |  |  | HR2491 (Lo-16bits)
2493 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2494 |  |  |  | HR2493 (Lo-16bits)
2495 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2496 |  |  |  | HR2495 (Lo-16bits)
2497 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2498 |  |  |  | HR2497 (Lo-16bits)
2499 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2500 |  |  |  | HR2499 (Lo-16bits)
2501 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2502 |  |  |  | HR2501 (Lo-16bits)
2503 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2504 |  |  |  | HR2503 (Lo-16bits)
2505 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2506 |  |  |  | HR2505 (Lo-16bits)
2507 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2508 |  |  |  | HR2507 (Lo-16bits)
2509 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2510 |  |  |  | HR2509 (Lo-16bits)
2511 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2512 |  |  |  | HR2511 (Lo-16bits)
2513 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2514 |  |  |  | HR2513 (Lo-16bits)
2515 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2516 |  |  |  | HR2515 (Lo-16bits)
2517 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2518 |  |  |  | HR2517 (Lo-16bits)
2519 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2520 |  |  |  | HR2519 (Lo-16bits)
2521 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2522 |  |  |  | HR2521 (Lo-16bits)
2523 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2524 |  |  |  | HR2523 (Lo-16bits)
2525 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2526 |  |  |  | HR2525 (Lo-16bits)
2527 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2528 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2529 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2530 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2531 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2532 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2533 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2534 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2535 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2536 |  |  |  | HR2535 (Lo-16bits)
2537 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2538 |  |  |  | HR2537 (Lo-16bits)
2539 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2540 |  |  |  | HR2539 (Lo-16bits)
2541 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2542 |  |  |  | HR2541 (Lo-16bits)
2543 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2544 |  |  |  | HR2543 (Lo-16bits)
2545 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2546 |  |  |  | HR2545 (Lo-16bits)
2547 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2548 |  |  |  | HR2547 (Lo-16bits)
2549 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2550 |  |  |  | HR2549 (Lo-16bits)
2551 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2552 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2553 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2554 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2555 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2556 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2557 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2558 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2559 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2560 |  |  |  | HR2559 (Lo-16bits)
2561 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2562 |  |  |  | HR2561 (Lo-16bits)
2563 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2564 |  |  |  | HR2563 (Lo-16bits)
2565 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2566 |  |  |  | HR2565 (Lo-16bits)
2567 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2568 |  |  |  | HR2567 (Lo-16bits)
2569 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2570 |  |  |  | HR2569 (Lo-16bits)
2571 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2572 |  |  |  | HR2571 (Lo-16bits)
2573 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2574 |  |  |  | HR2573 (Lo-16bits)
2575 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2576 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2577 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2578 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2579 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2580 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2581 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2582 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2583 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2584 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2585 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2586 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2587 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2588 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2589 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2590 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2591 | NOC4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2592 |  |  |  | HR2591 (Lo-16bits)
2593 | NOC4:Delay type | RW | 1 | 0=DT;1=IDMT
2594 | NOC4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2595 |  |  |  | HR2594 (Lo-16bits)
2596 | NOC4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2597 | NOC4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2598 | NOC4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2599 | NOC4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2600 | NOC4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2601 |  |  |  | HR2600 (Lo-16bits)
2602 | NOC4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2603 |  |  |  | HR2602 (Lo-16bits)
2604 | NOC4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2605 |  |  |  | HR2604 (Lo-16bits)
2606 | NOC4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2607 |  |  |  | HR2606 (Lo-16bits)
2608 | NOC4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2609 | NOC4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2610 | ROC1:Idrw> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2611 | ROC1:Idrw> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2612 | ROC2:Idrw>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2613 | ROC2:Idrw>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2614 | ROC3:Idrw>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2615 | ROC3:Idrw>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2616 | ROC4:Idrw>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2617 | ROC4:Idrw>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2618 | ROC5:Idrw>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2619 | ROC5:Idrw>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2620 | ROC6:Idrw>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2621 | ROC6:Idrw>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2622 | ROC7:Idrw>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2623 | ROC7:Idrw>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2624 | ROC8:Idrw>>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2625 | ROC8:Idrw>>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2626 | ROV1:Urw>/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2627 | ROV2:Urw>>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2628 | ROV3:Urw>>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2629 | ROV4:Urw>>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2630 | COL1:ICOL> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2631 | COL2:ICOL>> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2632 | CNU1:CNU> (50UB) mode | R(W) | 1 | 0=Disabled;1=Activated
2633 | UCP1:IUC> condition | R | 1 | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
2634 | DOC1:Idir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2635 | DOC1:Idir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2636 | DOC1:Idir> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2637 | DOC1:Idir> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2638 |  |  |  | HR2637 (Lo-16bits)
2639 | DOC1:Idir> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2640 |  |  |  | HR2639 (Lo-16bits)
2641 | DOC1:Idir> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2642 |  |  |  | HR2641 (Lo-16bits)
2643 | DOC1:Idir> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2644 |  |  |  | HR2643 (Lo-16bits)
2645 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2646 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2647 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2648 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2649 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2650 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2651 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2652 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2653 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2654 |  |  |  | HR2653 (Lo-16bits)
2655 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2656 |  |  |  | HR2655 (Lo-16bits)
2657 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2658 |  |  |  | HR2657 (Lo-16bits)
2659 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2660 |  |  |  | HR2659 (Lo-16bits)
2661 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2662 |  |  |  | HR2661 (Lo-16bits)
2663 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2664 |  |  |  | HR2663 (Lo-16bits)
2665 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2666 |  |  |  | HR2665 (Lo-16bits)
2667 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2668 |  |  |  | HR2667 (Lo-16bits)
2669 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2670 |  |  |  | HR2669 (Lo-16bits)
2671 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2672 |  |  |  | HR2671 (Lo-16bits)
2673 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2674 |  |  |  | HR2673 (Lo-16bits)
2675 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2676 |  |  |  | HR2675 (Lo-16bits)
2677 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2678 |  |  |  | HR2677 (Lo-16bits)
2679 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2680 |  |  |  | HR2679 (Lo-16bits)
2681 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2682 |  |  |  | HR2681 (Lo-16bits)
2683 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2684 |  |  |  | HR2683 (Lo-16bits)
2685 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2686 |  |  |  | HR2685 (Lo-16bits)
2687 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2688 |  |  |  | HR2687 (Lo-16bits)
2689 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2690 |  |  |  | HR2689 (Lo-16bits)
2691 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2692 |  |  |  | HR2691 (Lo-16bits)
2693 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2694 |  |  |  | HR2693 (Lo-16bits)
2695 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2696 |  |  |  | HR2695 (Lo-16bits)
2697 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2698 |  |  |  | HR2697 (Lo-16bits)
2699 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2700 |  |  |  | HR2699 (Lo-16bits)
2701 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2702 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2703 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2704 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2705 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2706 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2707 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2708 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2709 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2710 |  |  |  | HR2709 (Lo-16bits)
2711 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2712 |  |  |  | HR2711 (Lo-16bits)
2713 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2714 |  |  |  | HR2713 (Lo-16bits)
2715 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2716 |  |  |  | HR2715 (Lo-16bits)
2717 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2718 |  |  |  | HR2717 (Lo-16bits)
2719 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2720 |  |  |  | HR2719 (Lo-16bits)
2721 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2722 |  |  |  | HR2721 (Lo-16bits)
2723 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2724 |  |  |  | HR2723 (Lo-16bits)
2725 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2726 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2727 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2728 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2729 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2730 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2731 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2732 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2733 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2734 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2735 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2736 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2737 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2738 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2739 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2740 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2741 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2742 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2743 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2744 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2745 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2746 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2747 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2748 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2749 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2750 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2751 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2752 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2753 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2754 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2755 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2756 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2757 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2758 |  |  |  | HR2757 (Lo-16bits)
2759 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2760 |  |  |  | HR2759 (Lo-16bits)
2761 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2762 |  |  |  | HR2761 (Lo-16bits)
2763 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2764 |  |  |  | HR2763 (Lo-16bits)
2765 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2766 |  |  |  | HR2765 (Lo-16bits)
2767 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2768 |  |  |  | HR2767 (Lo-16bits)
2769 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2770 |  |  |  | HR2769 (Lo-16bits)
2771 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2772 |  |  |  | HR2771 (Lo-16bits)
2773 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2774 |  |  |  | HR2773 (Lo-16bits)
2775 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2776 |  |  |  | HR2775 (Lo-16bits)
2777 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2778 |  |  |  | HR2777 (Lo-16bits)
2779 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2780 |  |  |  | HR2779 (Lo-16bits)
2781 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2782 |  |  |  | HR2781 (Lo-16bits)
2783 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2784 |  |  |  | HR2783 (Lo-16bits)
2785 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2786 |  |  |  | HR2785 (Lo-16bits)
2787 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2788 |  |  |  | HR2787 (Lo-16bits)
2789 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2790 |  |  |  | HR2789 (Lo-16bits)
2791 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2792 |  |  |  | HR2791 (Lo-16bits)
2793 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2794 |  |  |  | HR2793 (Lo-16bits)
2795 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2796 |  |  |  | HR2795 (Lo-16bits)
2797 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2798 |  |  |  | HR2797 (Lo-16bits)
2799 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2800 |  |  |  | HR2799 (Lo-16bits)
2801 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2802 |  |  |  | HR2801 (Lo-16bits)
2803 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2804 |  |  |  | HR2803 (Lo-16bits)
2805 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2806 |  |  |  | HR2805 (Lo-16bits)
2807 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2808 |  |  |  | HR2807 (Lo-16bits)
2809 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2810 |  |  |  | HR2809 (Lo-16bits)
2811 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2812 |  |  |  | HR2811 (Lo-16bits)
2813 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2814 |  |  |  | HR2813 (Lo-16bits)
2815 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2816 |  |  |  | HR2815 (Lo-16bits)
2817 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2818 |  |  |  | HR2817 (Lo-16bits)
2819 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2820 |  |  |  | HR2819 (Lo-16bits)
2821 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2822 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2823 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2824 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2825 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2826 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2827 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2828 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2829 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2830 |  |  |  | HR2829 (Lo-16bits)
2831 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2832 |  |  |  | HR2831 (Lo-16bits)
2833 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2834 |  |  |  | HR2833 (Lo-16bits)
2835 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2836 |  |  |  | HR2835 (Lo-16bits)
2837 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2838 |  |  |  | HR2837 (Lo-16bits)
2839 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2840 |  |  |  | HR2839 (Lo-16bits)
2841 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2842 |  |  |  | HR2841 (Lo-16bits)
2843 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2844 |  |  |  | HR2843 (Lo-16bits)
2845 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2846 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2847 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2848 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2849 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2850 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2851 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2852 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2853 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2854 |  |  |  | HR2853 (Lo-16bits)
2855 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2856 |  |  |  | HR2855 (Lo-16bits)
2857 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2858 |  |  |  | HR2857 (Lo-16bits)
2859 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2860 |  |  |  | HR2859 (Lo-16bits)
2861 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2862 |  |  |  | HR2861 (Lo-16bits)
2863 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2864 |  |  |  | HR2863 (Lo-16bits)
2865 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2866 |  |  |  | HR2865 (Lo-16bits)
2867 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2868 |  |  |  | HR2867 (Lo-16bits)
2869 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2870 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2871 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2872 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2873 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2874 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2875 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2876 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2877 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2878 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2879 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2880 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2881 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2882 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2883 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2884 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2885 | DOC2:Idir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2886 | DOC2:Idir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2887 | DOC2:Idir>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2888 | DOC2:Idir>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2889 |  |  |  | HR2888 (Lo-16bits)
2890 | DOC2:Idir>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2891 |  |  |  | HR2890 (Lo-16bits)
2892 | DOC2:Idir>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2893 |  |  |  | HR2892 (Lo-16bits)
2894 | DOC2:Idir>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2895 |  |  |  | HR2894 (Lo-16bits)
2896 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2897 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2898 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2899 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2900 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2901 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2902 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2903 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2904 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2905 |  |  |  | HR2904 (Lo-16bits)
2906 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2907 |  |  |  | HR2906 (Lo-16bits)
2908 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2909 |  |  |  | HR2908 (Lo-16bits)
2910 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2911 |  |  |  | HR2910 (Lo-16bits)
2912 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2913 |  |  |  | HR2912 (Lo-16bits)
2914 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2915 |  |  |  | HR2914 (Lo-16bits)
2916 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2917 |  |  |  | HR2916 (Lo-16bits)
2918 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2919 |  |  |  | HR2918 (Lo-16bits)
2920 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2921 |  |  |  | HR2920 (Lo-16bits)
2922 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2923 |  |  |  | HR2922 (Lo-16bits)
2924 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2925 |  |  |  | HR2924 (Lo-16bits)
2926 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2927 |  |  |  | HR2926 (Lo-16bits)
2928 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2929 |  |  |  | HR2928 (Lo-16bits)
2930 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2931 |  |  |  | HR2930 (Lo-16bits)
2932 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2933 |  |  |  | HR2932 (Lo-16bits)
2934 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2935 |  |  |  | HR2934 (Lo-16bits)
2936 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2937 |  |  |  | HR2936 (Lo-16bits)
2938 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2939 |  |  |  | HR2938 (Lo-16bits)
2940 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2941 |  |  |  | HR2940 (Lo-16bits)
2942 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2943 |  |  |  | HR2942 (Lo-16bits)
2944 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2945 |  |  |  | HR2944 (Lo-16bits)
2946 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2947 |  |  |  | HR2946 (Lo-16bits)
2948 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2949 |  |  |  | HR2948 (Lo-16bits)
2950 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2951 |  |  |  | HR2950 (Lo-16bits)
2952 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2953 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2954 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2955 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2956 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2957 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2958 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2959 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2960 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2961 |  |  |  | HR2960 (Lo-16bits)
2962 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2963 |  |  |  | HR2962 (Lo-16bits)
2964 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2965 |  |  |  | HR2964 (Lo-16bits)
2966 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2967 |  |  |  | HR2966 (Lo-16bits)
2968 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2969 |  |  |  | HR2968 (Lo-16bits)
2970 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2971 |  |  |  | HR2970 (Lo-16bits)
2972 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2973 |  |  |  | HR2972 (Lo-16bits)
2974 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2975 |  |  |  | HR2974 (Lo-16bits)
2976 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2977 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2978 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2979 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2980 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2981 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2982 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2983 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2984 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2985 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2986 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2987 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2988 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2989 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2990 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2991 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2992 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2993 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2994 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2995 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2996 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2997 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2998 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2999 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3000 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3001 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3002 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3003 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3004 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3005 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3006 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3007 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3008 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3009 |  |  |  | HR3008 (Lo-16bits)
3010 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3011 |  |  |  | HR3010 (Lo-16bits)
3012 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3013 |  |  |  | HR3012 (Lo-16bits)
3014 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3015 |  |  |  | HR3014 (Lo-16bits)
3016 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3017 |  |  |  | HR3016 (Lo-16bits)
3018 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3019 |  |  |  | HR3018 (Lo-16bits)
3020 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3021 |  |  |  | HR3020 (Lo-16bits)
3022 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3023 |  |  |  | HR3022 (Lo-16bits)
3024 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3025 |  |  |  | HR3024 (Lo-16bits)
3026 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3027 |  |  |  | HR3026 (Lo-16bits)
3028 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3029 |  |  |  | HR3028 (Lo-16bits)
3030 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3031 |  |  |  | HR3030 (Lo-16bits)
3032 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3033 |  |  |  | HR3032 (Lo-16bits)
3034 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3035 |  |  |  | HR3034 (Lo-16bits)
3036 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3037 |  |  |  | HR3036 (Lo-16bits)
3038 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3039 |  |  |  | HR3038 (Lo-16bits)
3040 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3041 |  |  |  | HR3040 (Lo-16bits)
3042 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3043 |  |  |  | HR3042 (Lo-16bits)
3044 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3045 |  |  |  | HR3044 (Lo-16bits)
3046 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3047 |  |  |  | HR3046 (Lo-16bits)
3048 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3049 |  |  |  | HR3048 (Lo-16bits)
3050 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3051 |  |  |  | HR3050 (Lo-16bits)
3052 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3053 |  |  |  | HR3052 (Lo-16bits)
3054 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3055 |  |  |  | HR3054 (Lo-16bits)
3056 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3057 |  |  |  | HR3056 (Lo-16bits)
3058 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3059 |  |  |  | HR3058 (Lo-16bits)
3060 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3061 |  |  |  | HR3060 (Lo-16bits)
3062 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3063 |  |  |  | HR3062 (Lo-16bits)
3064 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3065 |  |  |  | HR3064 (Lo-16bits)
3066 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3067 |  |  |  | HR3066 (Lo-16bits)
3068 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3069 |  |  |  | HR3068 (Lo-16bits)
3070 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3071 |  |  |  | HR3070 (Lo-16bits)
3072 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3073 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3074 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3075 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3076 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3077 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3078 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3079 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3080 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3081 |  |  |  | HR3080 (Lo-16bits)
3082 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3083 |  |  |  | HR3082 (Lo-16bits)
3084 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3085 |  |  |  | HR3084 (Lo-16bits)
3086 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3087 |  |  |  | HR3086 (Lo-16bits)
3088 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3089 |  |  |  | HR3088 (Lo-16bits)
3090 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3091 |  |  |  | HR3090 (Lo-16bits)
3092 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3093 |  |  |  | HR3092 (Lo-16bits)
3094 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3095 |  |  |  | HR3094 (Lo-16bits)
3096 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3097 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3098 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3099 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3100 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3101 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3102 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3103 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3104 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3105 |  |  |  | HR3104 (Lo-16bits)
3106 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3107 |  |  |  | HR3106 (Lo-16bits)
3108 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3109 |  |  |  | HR3108 (Lo-16bits)
3110 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3111 |  |  |  | HR3110 (Lo-16bits)
3112 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3113 |  |  |  | HR3112 (Lo-16bits)
3114 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3115 |  |  |  | HR3114 (Lo-16bits)
3116 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3117 |  |  |  | HR3116 (Lo-16bits)
3118 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3119 |  |  |  | HR3118 (Lo-16bits)
3120 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3121 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3122 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3123 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3124 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3125 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3126 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3127 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3128 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3129 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3130 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3131 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3132 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3133 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3134 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3135 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3136 | DOC3:Idir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3137 | DOC3:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3138 | DOC3:Idir>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3139 | DOC3:Idir>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3140 |  |  |  | HR3139 (Lo-16bits)
3141 | DOC3:Idir>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3142 |  |  |  | HR3141 (Lo-16bits)
3143 | DOC3:Idir>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3144 |  |  |  | HR3143 (Lo-16bits)
3145 | DOC3:Idir>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3146 |  |  |  | HR3145 (Lo-16bits)
3147 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3148 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3149 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3150 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3151 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3152 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3153 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3154 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3155 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3156 |  |  |  | HR3155 (Lo-16bits)
3157 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3158 |  |  |  | HR3157 (Lo-16bits)
3159 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3160 |  |  |  | HR3159 (Lo-16bits)
3161 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3162 |  |  |  | HR3161 (Lo-16bits)
3163 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3164 |  |  |  | HR3163 (Lo-16bits)
3165 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3166 |  |  |  | HR3165 (Lo-16bits)
3167 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3168 |  |  |  | HR3167 (Lo-16bits)
3169 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3170 |  |  |  | HR3169 (Lo-16bits)
3171 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3172 |  |  |  | HR3171 (Lo-16bits)
3173 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3174 |  |  |  | HR3173 (Lo-16bits)
3175 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3176 |  |  |  | HR3175 (Lo-16bits)
3177 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3178 |  |  |  | HR3177 (Lo-16bits)
3179 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3180 |  |  |  | HR3179 (Lo-16bits)
3181 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3182 |  |  |  | HR3181 (Lo-16bits)
3183 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3184 |  |  |  | HR3183 (Lo-16bits)
3185 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3186 |  |  |  | HR3185 (Lo-16bits)
3187 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3188 |  |  |  | HR3187 (Lo-16bits)
3189 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3190 |  |  |  | HR3189 (Lo-16bits)
3191 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3192 |  |  |  | HR3191 (Lo-16bits)
3193 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3194 |  |  |  | HR3193 (Lo-16bits)
3195 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3196 |  |  |  | HR3195 (Lo-16bits)
3197 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3198 |  |  |  | HR3197 (Lo-16bits)
3199 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3200 |  |  |  | HR3199 (Lo-16bits)
3201 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3202 |  |  |  | HR3201 (Lo-16bits)
3203 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3204 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3205 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3206 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3207 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3208 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3209 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3210 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3211 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3212 |  |  |  | HR3211 (Lo-16bits)
3213 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3214 |  |  |  | HR3213 (Lo-16bits)
3215 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3216 |  |  |  | HR3215 (Lo-16bits)
3217 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3218 |  |  |  | HR3217 (Lo-16bits)
3219 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3220 |  |  |  | HR3219 (Lo-16bits)
3221 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3222 |  |  |  | HR3221 (Lo-16bits)
3223 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3224 |  |  |  | HR3223 (Lo-16bits)
3225 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3226 |  |  |  | HR3225 (Lo-16bits)
3227 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3228 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3229 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3230 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3231 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3232 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3233 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3234 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3235 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3236 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3237 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3238 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3239 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3240 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3241 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3242 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3243 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3244 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3245 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3246 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3247 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3248 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3249 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3250 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3251 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3252 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3253 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3254 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3255 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3256 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3257 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3258 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3259 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3260 |  |  |  | HR3259 (Lo-16bits)
3261 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3262 |  |  |  | HR3261 (Lo-16bits)
3263 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3264 |  |  |  | HR3263 (Lo-16bits)
3265 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3266 |  |  |  | HR3265 (Lo-16bits)
3267 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3268 |  |  |  | HR3267 (Lo-16bits)
3269 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3270 |  |  |  | HR3269 (Lo-16bits)
3271 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3272 |  |  |  | HR3271 (Lo-16bits)
3273 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3274 |  |  |  | HR3273 (Lo-16bits)
3275 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3276 |  |  |  | HR3275 (Lo-16bits)
3277 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3278 |  |  |  | HR3277 (Lo-16bits)
3279 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3280 |  |  |  | HR3279 (Lo-16bits)
3281 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3282 |  |  |  | HR3281 (Lo-16bits)
3283 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3284 |  |  |  | HR3283 (Lo-16bits)
3285 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3286 |  |  |  | HR3285 (Lo-16bits)
3287 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3288 |  |  |  | HR3287 (Lo-16bits)
3289 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3290 |  |  |  | HR3289 (Lo-16bits)
3291 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3292 |  |  |  | HR3291 (Lo-16bits)
3293 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3294 |  |  |  | HR3293 (Lo-16bits)
3295 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3296 |  |  |  | HR3295 (Lo-16bits)
3297 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3298 |  |  |  | HR3297 (Lo-16bits)
3299 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3300 |  |  |  | HR3299 (Lo-16bits)
3301 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3302 |  |  |  | HR3301 (Lo-16bits)
3303 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3304 |  |  |  | HR3303 (Lo-16bits)
3305 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3306 |  |  |  | HR3305 (Lo-16bits)
3307 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3308 |  |  |  | HR3307 (Lo-16bits)
3309 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3310 |  |  |  | HR3309 (Lo-16bits)
3311 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3312 |  |  |  | HR3311 (Lo-16bits)
3313 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3314 |  |  |  | HR3313 (Lo-16bits)
3315 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3316 |  |  |  | HR3315 (Lo-16bits)
3317 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3318 |  |  |  | HR3317 (Lo-16bits)
3319 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3320 |  |  |  | HR3319 (Lo-16bits)
3321 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3322 |  |  |  | HR3321 (Lo-16bits)
3323 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3324 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3325 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3326 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3327 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3328 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3329 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3330 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3331 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3332 |  |  |  | HR3331 (Lo-16bits)
3333 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3334 |  |  |  | HR3333 (Lo-16bits)
3335 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3336 |  |  |  | HR3335 (Lo-16bits)
3337 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3338 |  |  |  | HR3337 (Lo-16bits)
3339 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3340 |  |  |  | HR3339 (Lo-16bits)
3341 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3342 |  |  |  | HR3341 (Lo-16bits)
3343 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3344 |  |  |  | HR3343 (Lo-16bits)
3345 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3346 |  |  |  | HR3345 (Lo-16bits)
3347 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3348 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3349 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3350 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3351 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3352 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3353 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3354 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3355 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3356 |  |  |  | HR3355 (Lo-16bits)
3357 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3358 |  |  |  | HR3357 (Lo-16bits)
3359 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3360 |  |  |  | HR3359 (Lo-16bits)
3361 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3362 |  |  |  | HR3361 (Lo-16bits)
3363 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3364 |  |  |  | HR3363 (Lo-16bits)
3365 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3366 |  |  |  | HR3365 (Lo-16bits)
3367 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3368 |  |  |  | HR3367 (Lo-16bits)
3369 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3370 |  |  |  | HR3369 (Lo-16bits)
3371 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3372 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3373 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3374 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3375 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3376 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3377 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3378 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3379 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3380 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3381 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3382 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3383 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3384 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3385 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3386 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3387 | DOC4:Idir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3388 | DOC4:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3389 | DOC4:Idir>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3390 | DOC4:Idir>>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3391 |  |  |  | HR3390 (Lo-16bits)
3392 | DOC4:Idir>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3393 |  |  |  | HR3392 (Lo-16bits)
3394 | DOC4:Idir>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3395 |  |  |  | HR3394 (Lo-16bits)
3396 | DOC4:Idir>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3397 |  |  |  | HR3396 (Lo-16bits)
3398 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3399 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3400 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3401 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3402 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3403 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3404 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3405 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3406 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3407 |  |  |  | HR3406 (Lo-16bits)
3408 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3409 |  |  |  | HR3408 (Lo-16bits)
3410 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3411 |  |  |  | HR3410 (Lo-16bits)
3412 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3413 |  |  |  | HR3412 (Lo-16bits)
3414 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3415 |  |  |  | HR3414 (Lo-16bits)
3416 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3417 |  |  |  | HR3416 (Lo-16bits)
3418 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3419 |  |  |  | HR3418 (Lo-16bits)
3420 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3421 |  |  |  | HR3420 (Lo-16bits)
3422 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3423 |  |  |  | HR3422 (Lo-16bits)
3424 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3425 |  |  |  | HR3424 (Lo-16bits)
3426 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3427 |  |  |  | HR3426 (Lo-16bits)
3428 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3429 |  |  |  | HR3428 (Lo-16bits)
3430 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3431 |  |  |  | HR3430 (Lo-16bits)
3432 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3433 |  |  |  | HR3432 (Lo-16bits)
3434 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3435 |  |  |  | HR3434 (Lo-16bits)
3436 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3437 |  |  |  | HR3436 (Lo-16bits)
3438 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3439 |  |  |  | HR3438 (Lo-16bits)
3440 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3441 |  |  |  | HR3440 (Lo-16bits)
3442 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3443 |  |  |  | HR3442 (Lo-16bits)
3444 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3445 |  |  |  | HR3444 (Lo-16bits)
3446 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3447 |  |  |  | HR3446 (Lo-16bits)
3448 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3449 |  |  |  | HR3448 (Lo-16bits)
3450 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3451 |  |  |  | HR3450 (Lo-16bits)
3452 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3453 |  |  |  | HR3452 (Lo-16bits)
3454 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3455 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3456 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3457 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3458 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3459 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3460 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3461 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3462 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3463 |  |  |  | HR3462 (Lo-16bits)
3464 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3465 |  |  |  | HR3464 (Lo-16bits)
3466 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3467 |  |  |  | HR3466 (Lo-16bits)
3468 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3469 |  |  |  | HR3468 (Lo-16bits)
3470 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3471 |  |  |  | HR3470 (Lo-16bits)
3472 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3473 |  |  |  | HR3472 (Lo-16bits)
3474 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3475 |  |  |  | HR3474 (Lo-16bits)
3476 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3477 |  |  |  | HR3476 (Lo-16bits)
3478 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3479 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3480 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3481 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3482 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3483 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3484 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3485 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3486 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3487 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3488 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3489 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3490 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3491 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3492 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3493 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3494 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3495 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3496 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3497 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3498 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3499 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3500 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3501 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3502 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3503 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3504 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3505 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3506 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3507 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3508 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3509 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3510 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3511 |  |  |  | HR3510 (Lo-16bits)
3512 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3513 |  |  |  | HR3512 (Lo-16bits)
3514 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3515 |  |  |  | HR3514 (Lo-16bits)
3516 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3517 |  |  |  | HR3516 (Lo-16bits)
3518 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3519 |  |  |  | HR3518 (Lo-16bits)
3520 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3521 |  |  |  | HR3520 (Lo-16bits)
3522 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3523 |  |  |  | HR3522 (Lo-16bits)
3524 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3525 |  |  |  | HR3524 (Lo-16bits)
3526 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3527 |  |  |  | HR3526 (Lo-16bits)
3528 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3529 |  |  |  | HR3528 (Lo-16bits)
3530 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3531 |  |  |  | HR3530 (Lo-16bits)
3532 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3533 |  |  |  | HR3532 (Lo-16bits)
3534 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3535 |  |  |  | HR3534 (Lo-16bits)
3536 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3537 |  |  |  | HR3536 (Lo-16bits)
3538 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3539 |  |  |  | HR3538 (Lo-16bits)
3540 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3541 |  |  |  | HR3540 (Lo-16bits)
3542 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3543 |  |  |  | HR3542 (Lo-16bits)
3544 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3545 |  |  |  | HR3544 (Lo-16bits)
3546 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3547 |  |  |  | HR3546 (Lo-16bits)
3548 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3549 |  |  |  | HR3548 (Lo-16bits)
3550 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3551 |  |  |  | HR3550 (Lo-16bits)
3552 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3553 |  |  |  | HR3552 (Lo-16bits)
3554 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3555 |  |  |  | HR3554 (Lo-16bits)
3556 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3557 |  |  |  | HR3556 (Lo-16bits)
3558 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3559 |  |  |  | HR3558 (Lo-16bits)
3560 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3561 |  |  |  | HR3560 (Lo-16bits)
3562 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3563 |  |  |  | HR3562 (Lo-16bits)
3564 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3565 |  |  |  | HR3564 (Lo-16bits)
3566 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3567 |  |  |  | HR3566 (Lo-16bits)
3568 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3569 |  |  |  | HR3568 (Lo-16bits)
3570 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3571 |  |  |  | HR3570 (Lo-16bits)
3572 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3573 |  |  |  | HR3572 (Lo-16bits)
3574 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3575 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3576 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3577 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3578 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3579 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3580 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3581 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3582 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3583 |  |  |  | HR3582 (Lo-16bits)
3584 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3585 |  |  |  | HR3584 (Lo-16bits)
3586 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3587 |  |  |  | HR3586 (Lo-16bits)
3588 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3589 |  |  |  | HR3588 (Lo-16bits)
3590 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3591 |  |  |  | HR3590 (Lo-16bits)
3592 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3593 |  |  |  | HR3592 (Lo-16bits)
3594 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3595 |  |  |  | HR3594 (Lo-16bits)
3596 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3597 |  |  |  | HR3596 (Lo-16bits)
3598 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3599 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3600 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3601 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3602 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3603 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3604 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3605 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3606 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3607 |  |  |  | HR3606 (Lo-16bits)
3608 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3609 |  |  |  | HR3608 (Lo-16bits)
3610 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3611 |  |  |  | HR3610 (Lo-16bits)
3612 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3613 |  |  |  | HR3612 (Lo-16bits)
3614 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3615 |  |  |  | HR3614 (Lo-16bits)
3616 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3617 |  |  |  | HR3616 (Lo-16bits)
3618 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3619 |  |  |  | HR3618 (Lo-16bits)
3620 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3621 |  |  |  | HR3620 (Lo-16bits)
3622 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3623 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3624 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3625 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3626 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3627 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3628 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3629 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3630 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3631 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3632 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3633 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3634 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3635 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3636 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3637 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3638 | NEF1:I0> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3639 | NEF1:I0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3640 | NEF1:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3641 | NEF1:I0> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3642 | NEF1:I0> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3643 |  |  |  | HR3642 (Lo-16bits)
3644 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3645 |  |  |  | HR3644 (Lo-16bits)
3646 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3647 |  |  |  | HR3646 (Lo-16bits)
3648 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3649 |  |  |  | HR3648 (Lo-16bits)
3650 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3651 |  |  |  | HR3650 (Lo-16bits)
3652 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3653 |  |  |  | HR3652 (Lo-16bits)
3654 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3655 |  |  |  | HR3654 (Lo-16bits)
3656 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3657 |  |  |  | HR3656 (Lo-16bits)
3658 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3659 |  |  |  | HR3658 (Lo-16bits)
3660 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3661 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3662 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3663 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3664 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3665 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3666 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3667 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3668 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3669 |  |  |  | HR3668 (Lo-16bits)
3670 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3671 |  |  |  | HR3670 (Lo-16bits)
3672 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3673 |  |  |  | HR3672 (Lo-16bits)
3674 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3675 |  |  |  | HR3674 (Lo-16bits)
3676 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3677 |  |  |  | HR3676 (Lo-16bits)
3678 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3679 |  |  |  | HR3678 (Lo-16bits)
3680 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3681 |  |  |  | HR3680 (Lo-16bits)
3682 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3683 |  |  |  | HR3682 (Lo-16bits)
3684 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3685 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3686 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3687 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3688 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3689 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3690 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3691 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3692 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3693 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3694 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3695 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3696 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3697 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3698 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3699 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3700 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3701 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3702 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3703 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3704 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3705 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3706 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3707 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3708 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3709 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3710 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3711 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3712 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3713 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3714 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3715 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3716 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3717 |  |  |  | HR3716 (Lo-16bits)
3718 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3719 |  |  |  | HR3718 (Lo-16bits)
3720 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3721 |  |  |  | HR3720 (Lo-16bits)
3722 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3723 |  |  |  | HR3722 (Lo-16bits)
3724 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3725 |  |  |  | HR3724 (Lo-16bits)
3726 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3727 |  |  |  | HR3726 (Lo-16bits)
3728 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3729 |  |  |  | HR3728 (Lo-16bits)
3730 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3731 |  |  |  | HR3730 (Lo-16bits)
3732 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3733 |  |  |  | HR3732 (Lo-16bits)
3734 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3735 |  |  |  | HR3734 (Lo-16bits)
3736 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3737 |  |  |  | HR3736 (Lo-16bits)
3738 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3739 |  |  |  | HR3738 (Lo-16bits)
3740 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3741 |  |  |  | HR3740 (Lo-16bits)
3742 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3743 |  |  |  | HR3742 (Lo-16bits)
3744 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3745 |  |  |  | HR3744 (Lo-16bits)
3746 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3747 |  |  |  | HR3746 (Lo-16bits)
3748 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3749 |  |  |  | HR3748 (Lo-16bits)
3750 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3751 |  |  |  | HR3750 (Lo-16bits)
3752 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3753 |  |  |  | HR3752 (Lo-16bits)
3754 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3755 |  |  |  | HR3754 (Lo-16bits)
3756 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3757 |  |  |  | HR3756 (Lo-16bits)
3758 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3759 |  |  |  | HR3758 (Lo-16bits)
3760 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3761 |  |  |  | HR3760 (Lo-16bits)
3762 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3763 |  |  |  | HR3762 (Lo-16bits)
3764 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3765 |  |  |  | HR3764 (Lo-16bits)
3766 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3767 |  |  |  | HR3766 (Lo-16bits)
3768 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3769 |  |  |  | HR3768 (Lo-16bits)
3770 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3771 |  |  |  | HR3770 (Lo-16bits)
3772 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3773 |  |  |  | HR3772 (Lo-16bits)
3774 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3775 |  |  |  | HR3774 (Lo-16bits)
3776 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3777 |  |  |  | HR3776 (Lo-16bits)
3778 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3779 |  |  |  | HR3778 (Lo-16bits)
3780 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3781 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3782 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3783 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3784 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3785 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3786 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3787 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3788 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3789 |  |  |  | HR3788 (Lo-16bits)
3790 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3791 |  |  |  | HR3790 (Lo-16bits)
3792 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3793 |  |  |  | HR3792 (Lo-16bits)
3794 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3795 |  |  |  | HR3794 (Lo-16bits)
3796 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3797 |  |  |  | HR3796 (Lo-16bits)
3798 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3799 |  |  |  | HR3798 (Lo-16bits)
3800 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3801 |  |  |  | HR3800 (Lo-16bits)
3802 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3803 |  |  |  | HR3802 (Lo-16bits)
3804 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3805 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3806 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3807 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3808 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3809 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3810 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3811 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3812 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3813 |  |  |  | HR3812 (Lo-16bits)
3814 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3815 |  |  |  | HR3814 (Lo-16bits)
3816 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3817 |  |  |  | HR3816 (Lo-16bits)
3818 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3819 |  |  |  | HR3818 (Lo-16bits)
3820 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3821 |  |  |  | HR3820 (Lo-16bits)
3822 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3823 |  |  |  | HR3822 (Lo-16bits)
3824 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3825 |  |  |  | HR3824 (Lo-16bits)
3826 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3827 |  |  |  | HR3826 (Lo-16bits)
3828 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3829 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3830 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3831 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3832 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3833 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3834 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3835 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3836 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3837 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3838 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3839 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3840 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3841 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3842 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3843 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3844 | NEF1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
3845 |  |  |  | HR3844 (Lo-16bits)
3846 | NEF1:Delay type | RW | 1 | 0=DT;1=IDMT
3847 | NEF1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
3848 |  |  |  | HR3847 (Lo-16bits)
3849 | NEF1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
3850 | NEF1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3851 | NEF1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3852 | NEF1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
3853 | NEF1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
3854 |  |  |  | HR3853 (Lo-16bits)
3855 | NEF1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
3856 |  |  |  | HR3855 (Lo-16bits)
3857 | NEF1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
3858 |  |  |  | HR3857 (Lo-16bits)
3859 | NEF1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
3860 |  |  |  | HR3859 (Lo-16bits)
3861 | NEF1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
3862 | NEF1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
3863 | NEF2:I0>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3864 | NEF2:I0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3865 | NEF2:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3866 | NEF2:I0>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3867 | NEF2:I0>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3868 |  |  |  | HR3867 (Lo-16bits)
3869 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3870 |  |  |  | HR3869 (Lo-16bits)
3871 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3872 |  |  |  | HR3871 (Lo-16bits)
3873 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3874 |  |  |  | HR3873 (Lo-16bits)
3875 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3876 |  |  |  | HR3875 (Lo-16bits)
3877 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3878 |  |  |  | HR3877 (Lo-16bits)
3879 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3880 |  |  |  | HR3879 (Lo-16bits)
3881 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3882 |  |  |  | HR3881 (Lo-16bits)
3883 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3884 |  |  |  | HR3883 (Lo-16bits)
3885 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3886 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3887 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3888 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3889 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3890 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3891 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3892 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3893 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3894 |  |  |  | HR3893 (Lo-16bits)
3895 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3896 |  |  |  | HR3895 (Lo-16bits)
3897 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3898 |  |  |  | HR3897 (Lo-16bits)
3899 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3900 |  |  |  | HR3899 (Lo-16bits)
3901 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3902 |  |  |  | HR3901 (Lo-16bits)
3903 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3904 |  |  |  | HR3903 (Lo-16bits)
3905 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3906 |  |  |  | HR3905 (Lo-16bits)
3907 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3908 |  |  |  | HR3907 (Lo-16bits)
3909 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3910 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3911 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3912 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3913 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3914 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3915 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3916 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3917 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3918 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3919 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3920 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3921 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3922 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3923 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3924 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3925 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3926 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3927 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3928 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3929 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3930 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3931 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3932 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3933 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3934 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3935 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3936 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3937 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3938 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3939 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3940 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3941 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3942 |  |  |  | HR3941 (Lo-16bits)
3943 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3944 |  |  |  | HR3943 (Lo-16bits)
3945 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3946 |  |  |  | HR3945 (Lo-16bits)
3947 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3948 |  |  |  | HR3947 (Lo-16bits)
3949 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3950 |  |  |  | HR3949 (Lo-16bits)
3951 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3952 |  |  |  | HR3951 (Lo-16bits)
3953 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3954 |  |  |  | HR3953 (Lo-16bits)
3955 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3956 |  |  |  | HR3955 (Lo-16bits)
3957 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3958 |  |  |  | HR3957 (Lo-16bits)
3959 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3960 |  |  |  | HR3959 (Lo-16bits)
3961 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3962 |  |  |  | HR3961 (Lo-16bits)
3963 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3964 |  |  |  | HR3963 (Lo-16bits)
3965 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3966 |  |  |  | HR3965 (Lo-16bits)
3967 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3968 |  |  |  | HR3967 (Lo-16bits)
3969 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3970 |  |  |  | HR3969 (Lo-16bits)
3971 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3972 |  |  |  | HR3971 (Lo-16bits)
3973 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3974 |  |  |  | HR3973 (Lo-16bits)
3975 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3976 |  |  |  | HR3975 (Lo-16bits)
3977 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3978 |  |  |  | HR3977 (Lo-16bits)
3979 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3980 |  |  |  | HR3979 (Lo-16bits)
3981 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3982 |  |  |  | HR3981 (Lo-16bits)
3983 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3984 |  |  |  | HR3983 (Lo-16bits)
3985 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3986 |  |  |  | HR3985 (Lo-16bits)
3987 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3988 |  |  |  | HR3987 (Lo-16bits)
3989 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3990 |  |  |  | HR3989 (Lo-16bits)
3991 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3992 |  |  |  | HR3991 (Lo-16bits)
3993 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3994 |  |  |  | HR3993 (Lo-16bits)
3995 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3996 |  |  |  | HR3995 (Lo-16bits)
3997 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3998 |  |  |  | HR3997 (Lo-16bits)
3999 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4000 |  |  |  | HR3999 (Lo-16bits)
4001 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4002 |  |  |  | HR4001 (Lo-16bits)
4003 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4004 |  |  |  | HR4003 (Lo-16bits)
4005 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4006 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4007 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4008 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4009 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4010 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4011 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4012 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4013 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4014 |  |  |  | HR4013 (Lo-16bits)
4015 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4016 |  |  |  | HR4015 (Lo-16bits)
4017 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4018 |  |  |  | HR4017 (Lo-16bits)
4019 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4020 |  |  |  | HR4019 (Lo-16bits)
4021 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4022 |  |  |  | HR4021 (Lo-16bits)
4023 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4024 |  |  |  | HR4023 (Lo-16bits)
4025 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4026 |  |  |  | HR4025 (Lo-16bits)
4027 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4028 |  |  |  | HR4027 (Lo-16bits)
4029 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4030 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4031 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4032 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4033 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4034 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4035 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4036 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4037 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4038 |  |  |  | HR4037 (Lo-16bits)
4039 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4040 |  |  |  | HR4039 (Lo-16bits)
4041 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4042 |  |  |  | HR4041 (Lo-16bits)
4043 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4044 |  |  |  | HR4043 (Lo-16bits)
4045 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4046 |  |  |  | HR4045 (Lo-16bits)
4047 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4048 |  |  |  | HR4047 (Lo-16bits)
4049 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4050 |  |  |  | HR4049 (Lo-16bits)
4051 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4052 |  |  |  | HR4051 (Lo-16bits)
4053 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4054 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4055 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4056 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4057 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4058 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4059 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4060 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4061 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4062 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4063 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4064 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4065 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4066 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4067 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4068 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4069 | NEF2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4070 |  |  |  | HR4069 (Lo-16bits)
4071 | NEF2:Delay type | RW | 1 | 0=DT;1=IDMT
4072 | NEF2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4073 |  |  |  | HR4072 (Lo-16bits)
4074 | NEF2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4075 | NEF2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4076 | NEF2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4077 | NEF2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4078 | NEF2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4079 |  |  |  | HR4078 (Lo-16bits)
4080 | NEF2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4081 |  |  |  | HR4080 (Lo-16bits)
4082 | NEF2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4083 |  |  |  | HR4082 (Lo-16bits)
4084 | NEF2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4085 |  |  |  | HR4084 (Lo-16bits)
4086 | NEF2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4087 | NEF2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4088 | NEF3:I0>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4089 | NEF3:I0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4090 | NEF3:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4091 | NEF3:I0>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4092 | NEF3:I0>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4093 |  |  |  | HR4092 (Lo-16bits)
4094 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4095 |  |  |  | HR4094 (Lo-16bits)
4096 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4097 |  |  |  | HR4096 (Lo-16bits)
4098 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4099 |  |  |  | HR4098 (Lo-16bits)
4100 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4101 |  |  |  | HR4100 (Lo-16bits)
4102 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4103 |  |  |  | HR4102 (Lo-16bits)
4104 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4105 |  |  |  | HR4104 (Lo-16bits)
4106 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4107 |  |  |  | HR4106 (Lo-16bits)
4108 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4109 |  |  |  | HR4108 (Lo-16bits)
4110 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4111 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4112 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4113 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4114 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4115 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4116 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4117 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4118 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4119 |  |  |  | HR4118 (Lo-16bits)
4120 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4121 |  |  |  | HR4120 (Lo-16bits)
4122 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4123 |  |  |  | HR4122 (Lo-16bits)
4124 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4125 |  |  |  | HR4124 (Lo-16bits)
4126 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4127 |  |  |  | HR4126 (Lo-16bits)
4128 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4129 |  |  |  | HR4128 (Lo-16bits)
4130 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4131 |  |  |  | HR4130 (Lo-16bits)
4132 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4133 |  |  |  | HR4132 (Lo-16bits)
4134 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4135 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4136 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4137 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4138 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4139 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4140 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4141 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4142 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4143 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4144 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4145 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4146 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4147 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4148 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4149 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4150 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4151 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4152 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4153 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4154 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4155 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4156 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4157 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4158 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4159 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4160 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4161 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4162 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4163 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4164 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4165 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4166 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4167 |  |  |  | HR4166 (Lo-16bits)
4168 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4169 |  |  |  | HR4168 (Lo-16bits)
4170 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4171 |  |  |  | HR4170 (Lo-16bits)
4172 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4173 |  |  |  | HR4172 (Lo-16bits)
4174 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4175 |  |  |  | HR4174 (Lo-16bits)
4176 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4177 |  |  |  | HR4176 (Lo-16bits)
4178 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4179 |  |  |  | HR4178 (Lo-16bits)
4180 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4181 |  |  |  | HR4180 (Lo-16bits)
4182 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4183 |  |  |  | HR4182 (Lo-16bits)
4184 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4185 |  |  |  | HR4184 (Lo-16bits)
4186 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4187 |  |  |  | HR4186 (Lo-16bits)
4188 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4189 |  |  |  | HR4188 (Lo-16bits)
4190 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4191 |  |  |  | HR4190 (Lo-16bits)
4192 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4193 |  |  |  | HR4192 (Lo-16bits)
4194 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4195 |  |  |  | HR4194 (Lo-16bits)
4196 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4197 |  |  |  | HR4196 (Lo-16bits)
4198 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4199 |  |  |  | HR4198 (Lo-16bits)
4200 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4201 |  |  |  | HR4200 (Lo-16bits)
4202 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4203 |  |  |  | HR4202 (Lo-16bits)
4204 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4205 |  |  |  | HR4204 (Lo-16bits)
4206 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4207 |  |  |  | HR4206 (Lo-16bits)
4208 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4209 |  |  |  | HR4208 (Lo-16bits)
4210 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4211 |  |  |  | HR4210 (Lo-16bits)
4212 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4213 |  |  |  | HR4212 (Lo-16bits)
4214 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4215 |  |  |  | HR4214 (Lo-16bits)
4216 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4217 |  |  |  | HR4216 (Lo-16bits)
4218 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4219 |  |  |  | HR4218 (Lo-16bits)
4220 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4221 |  |  |  | HR4220 (Lo-16bits)
4222 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4223 |  |  |  | HR4222 (Lo-16bits)
4224 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4225 |  |  |  | HR4224 (Lo-16bits)
4226 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4227 |  |  |  | HR4226 (Lo-16bits)
4228 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4229 |  |  |  | HR4228 (Lo-16bits)
4230 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4231 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4232 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4233 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4234 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4235 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4236 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4237 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4238 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4239 |  |  |  | HR4238 (Lo-16bits)
4240 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4241 |  |  |  | HR4240 (Lo-16bits)
4242 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4243 |  |  |  | HR4242 (Lo-16bits)
4244 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4245 |  |  |  | HR4244 (Lo-16bits)
4246 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4247 |  |  |  | HR4246 (Lo-16bits)
4248 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4249 |  |  |  | HR4248 (Lo-16bits)
4250 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4251 |  |  |  | HR4250 (Lo-16bits)
4252 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4253 |  |  |  | HR4252 (Lo-16bits)
4254 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4255 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4256 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4257 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4258 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4259 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4260 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4261 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4262 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4263 |  |  |  | HR4262 (Lo-16bits)
4264 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4265 |  |  |  | HR4264 (Lo-16bits)
4266 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4267 |  |  |  | HR4266 (Lo-16bits)
4268 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4269 |  |  |  | HR4268 (Lo-16bits)
4270 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4271 |  |  |  | HR4270 (Lo-16bits)
4272 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4273 |  |  |  | HR4272 (Lo-16bits)
4274 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4275 |  |  |  | HR4274 (Lo-16bits)
4276 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4277 |  |  |  | HR4276 (Lo-16bits)
4278 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4279 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4280 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4281 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4282 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4283 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4284 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4285 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4286 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4287 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4288 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4289 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4290 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4291 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4292 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4293 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4294 | NEF3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4295 |  |  |  | HR4294 (Lo-16bits)
4296 | NEF3:Delay type | RW | 1 | 0=DT;1=IDMT
4297 | NEF3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4298 |  |  |  | HR4297 (Lo-16bits)
4299 | NEF3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4300 | NEF3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4301 | NEF3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4302 | NEF3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4303 | NEF3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4304 |  |  |  | HR4303 (Lo-16bits)
4305 | NEF3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4306 |  |  |  | HR4305 (Lo-16bits)
4307 | NEF3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4308 |  |  |  | HR4307 (Lo-16bits)
4309 | NEF3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4310 |  |  |  | HR4309 (Lo-16bits)
4311 | NEF3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4312 | NEF3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4313 | NEF4:I0>>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4314 | NEF4:I0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4315 | NEF4:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4316 | NEF4:I0>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4317 | NEF4:I0>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4318 |  |  |  | HR4317 (Lo-16bits)
4319 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4320 |  |  |  | HR4319 (Lo-16bits)
4321 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4322 |  |  |  | HR4321 (Lo-16bits)
4323 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4324 |  |  |  | HR4323 (Lo-16bits)
4325 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4326 |  |  |  | HR4325 (Lo-16bits)
4327 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4328 |  |  |  | HR4327 (Lo-16bits)
4329 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4330 |  |  |  | HR4329 (Lo-16bits)
4331 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4332 |  |  |  | HR4331 (Lo-16bits)
4333 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4334 |  |  |  | HR4333 (Lo-16bits)
4335 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4336 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4337 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4338 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4339 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4340 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4341 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4342 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4343 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4344 |  |  |  | HR4343 (Lo-16bits)
4345 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4346 |  |  |  | HR4345 (Lo-16bits)
4347 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4348 |  |  |  | HR4347 (Lo-16bits)
4349 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4350 |  |  |  | HR4349 (Lo-16bits)
4351 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4352 |  |  |  | HR4351 (Lo-16bits)
4353 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4354 |  |  |  | HR4353 (Lo-16bits)
4355 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4356 |  |  |  | HR4355 (Lo-16bits)
4357 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4358 |  |  |  | HR4357 (Lo-16bits)
4359 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4360 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4361 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4362 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4363 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4364 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4365 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4366 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4367 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4368 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4369 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4370 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4371 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4372 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4373 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4374 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4375 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4376 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4377 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4378 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4379 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4380 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4381 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4382 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4383 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4384 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4385 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4386 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4387 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4388 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4389 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4390 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4391 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4392 |  |  |  | HR4391 (Lo-16bits)
4393 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4394 |  |  |  | HR4393 (Lo-16bits)
4395 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4396 |  |  |  | HR4395 (Lo-16bits)
4397 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4398 |  |  |  | HR4397 (Lo-16bits)
4399 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4400 |  |  |  | HR4399 (Lo-16bits)
4401 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4402 |  |  |  | HR4401 (Lo-16bits)
4403 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4404 |  |  |  | HR4403 (Lo-16bits)
4405 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4406 |  |  |  | HR4405 (Lo-16bits)
4407 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4408 |  |  |  | HR4407 (Lo-16bits)
4409 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4410 |  |  |  | HR4409 (Lo-16bits)
4411 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4412 |  |  |  | HR4411 (Lo-16bits)
4413 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4414 |  |  |  | HR4413 (Lo-16bits)
4415 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4416 |  |  |  | HR4415 (Lo-16bits)
4417 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4418 |  |  |  | HR4417 (Lo-16bits)
4419 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4420 |  |  |  | HR4419 (Lo-16bits)
4421 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4422 |  |  |  | HR4421 (Lo-16bits)
4423 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4424 |  |  |  | HR4423 (Lo-16bits)
4425 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4426 |  |  |  | HR4425 (Lo-16bits)
4427 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4428 |  |  |  | HR4427 (Lo-16bits)
4429 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4430 |  |  |  | HR4429 (Lo-16bits)
4431 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4432 |  |  |  | HR4431 (Lo-16bits)
4433 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4434 |  |  |  | HR4433 (Lo-16bits)
4435 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4436 |  |  |  | HR4435 (Lo-16bits)
4437 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4438 |  |  |  | HR4437 (Lo-16bits)
4439 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4440 |  |  |  | HR4439 (Lo-16bits)
4441 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4442 |  |  |  | HR4441 (Lo-16bits)
4443 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4444 |  |  |  | HR4443 (Lo-16bits)
4445 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4446 |  |  |  | HR4445 (Lo-16bits)
4447 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4448 |  |  |  | HR4447 (Lo-16bits)
4449 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4450 |  |  |  | HR4449 (Lo-16bits)
4451 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4452 |  |  |  | HR4451 (Lo-16bits)
4453 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4454 |  |  |  | HR4453 (Lo-16bits)
4455 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4456 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4457 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4458 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4459 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4460 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4461 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4462 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4463 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4464 |  |  |  | HR4463 (Lo-16bits)
4465 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4466 |  |  |  | HR4465 (Lo-16bits)
4467 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4468 |  |  |  | HR4467 (Lo-16bits)
4469 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4470 |  |  |  | HR4469 (Lo-16bits)
4471 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4472 |  |  |  | HR4471 (Lo-16bits)
4473 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4474 |  |  |  | HR4473 (Lo-16bits)
4475 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4476 |  |  |  | HR4475 (Lo-16bits)
4477 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4478 |  |  |  | HR4477 (Lo-16bits)
4479 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4480 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4481 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4482 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4483 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4484 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4485 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4486 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4487 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4488 |  |  |  | HR4487 (Lo-16bits)
4489 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4490 |  |  |  | HR4489 (Lo-16bits)
4491 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4492 |  |  |  | HR4491 (Lo-16bits)
4493 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4494 |  |  |  | HR4493 (Lo-16bits)
4495 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4496 |  |  |  | HR4495 (Lo-16bits)
4497 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4498 |  |  |  | HR4497 (Lo-16bits)
4499 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4500 |  |  |  | HR4499 (Lo-16bits)
4501 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4502 |  |  |  | HR4501 (Lo-16bits)
4503 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4504 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4505 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4506 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4507 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4508 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4509 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4510 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4511 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4512 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4513 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4514 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4515 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4516 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4517 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4518 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4519 | NEF4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4520 |  |  |  | HR4519 (Lo-16bits)
4521 | NEF4:Delay type | RW | 1 | 0=DT;1=IDMT
4522 | NEF4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4523 |  |  |  | HR4522 (Lo-16bits)
4524 | NEF4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4525 | NEF4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4526 | NEF4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4527 | NEF4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4528 | NEF4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4529 |  |  |  | HR4528 (Lo-16bits)
4530 | NEF4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4531 |  |  |  | HR4530 (Lo-16bits)
4532 | NEF4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4533 |  |  |  | HR4532 (Lo-16bits)
4534 | NEF4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4535 |  |  |  | HR4534 (Lo-16bits)
4536 | NEF4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4537 | NEF4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4538 | DEF1:I0dir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4539 | DEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4540 | DEF1:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4541 | DEF1:I0dir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4542 | DEF1:I0dir> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4543 |  |  |  | HR4542 (Lo-16bits)
4544 | DEF1:I0dir> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4545 |  |  |  | HR4544 (Lo-16bits)
4546 | DEF1:I0dir> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4547 |  |  |  | HR4546 (Lo-16bits)
4548 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4549 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4550 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4551 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4552 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4553 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4554 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4555 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4556 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4557 |  |  |  | HR4556 (Lo-16bits)
4558 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4559 |  |  |  | HR4558 (Lo-16bits)
4560 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4561 |  |  |  | HR4560 (Lo-16bits)
4562 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4563 |  |  |  | HR4562 (Lo-16bits)
4564 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4565 |  |  |  | HR4564 (Lo-16bits)
4566 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4567 |  |  |  | HR4566 (Lo-16bits)
4568 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4569 |  |  |  | HR4568 (Lo-16bits)
4570 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4571 |  |  |  | HR4570 (Lo-16bits)
4572 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4573 |  |  |  | HR4572 (Lo-16bits)
4574 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4575 |  |  |  | HR4574 (Lo-16bits)
4576 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4577 |  |  |  | HR4576 (Lo-16bits)
4578 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4579 |  |  |  | HR4578 (Lo-16bits)
4580 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4581 |  |  |  | HR4580 (Lo-16bits)
4582 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4583 |  |  |  | HR4582 (Lo-16bits)
4584 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4585 |  |  |  | HR4584 (Lo-16bits)
4586 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4587 |  |  |  | HR4586 (Lo-16bits)
4588 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4589 |  |  |  | HR4588 (Lo-16bits)
4590 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4591 |  |  |  | HR4590 (Lo-16bits)
4592 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4593 |  |  |  | HR4592 (Lo-16bits)
4594 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4595 |  |  |  | HR4594 (Lo-16bits)
4596 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4597 |  |  |  | HR4596 (Lo-16bits)
4598 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4599 |  |  |  | HR4598 (Lo-16bits)
4600 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4601 |  |  |  | HR4600 (Lo-16bits)
4602 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4603 |  |  |  | HR4602 (Lo-16bits)
4604 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4605 |  |  |  | HR4604 (Lo-16bits)
4606 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4607 |  |  |  | HR4606 (Lo-16bits)
4608 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4609 |  |  |  | HR4608 (Lo-16bits)
4610 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4611 |  |  |  | HR4610 (Lo-16bits)
4612 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4613 |  |  |  | HR4612 (Lo-16bits)
4614 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4615 |  |  |  | HR4614 (Lo-16bits)
4616 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4617 |  |  |  | HR4616 (Lo-16bits)
4618 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4619 |  |  |  | HR4618 (Lo-16bits)
4620 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4621 |  |  |  | HR4620 (Lo-16bits)
4622 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4623 |  |  |  | HR4622 (Lo-16bits)
4624 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4625 |  |  |  | HR4624 (Lo-16bits)
4626 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4627 |  |  |  | HR4626 (Lo-16bits)
4628 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4629 |  |  |  | HR4628 (Lo-16bits)
4630 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4631 |  |  |  | HR4630 (Lo-16bits)
4632 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4633 |  |  |  | HR4632 (Lo-16bits)
4634 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4635 |  |  |  | HR4634 (Lo-16bits)
4636 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4637 |  |  |  | HR4636 (Lo-16bits)
4638 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4639 |  |  |  | HR4638 (Lo-16bits)
4640 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4641 |  |  |  | HR4640 (Lo-16bits)
4642 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4643 |  |  |  | HR4642 (Lo-16bits)
4644 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4645 |  |  |  | HR4644 (Lo-16bits)
4646 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4647 |  |  |  | HR4646 (Lo-16bits)
4648 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4649 |  |  |  | HR4648 (Lo-16bits)
4650 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4651 |  |  |  | HR4650 (Lo-16bits)
4652 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4653 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4654 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4655 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4656 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4657 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4658 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4659 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4660 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4661 |  |  |  | HR4660 (Lo-16bits)
4662 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4663 |  |  |  | HR4662 (Lo-16bits)
4664 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4665 |  |  |  | HR4664 (Lo-16bits)
4666 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4667 |  |  |  | HR4666 (Lo-16bits)
4668 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4669 |  |  |  | HR4668 (Lo-16bits)
4670 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4671 |  |  |  | HR4670 (Lo-16bits)
4672 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4673 |  |  |  | HR4672 (Lo-16bits)
4674 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4675 |  |  |  | HR4674 (Lo-16bits)
4676 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4677 |  |  |  | HR4676 (Lo-16bits)
4678 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4679 |  |  |  | HR4678 (Lo-16bits)
4680 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4681 |  |  |  | HR4680 (Lo-16bits)
4682 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4683 |  |  |  | HR4682 (Lo-16bits)
4684 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4685 |  |  |  | HR4684 (Lo-16bits)
4686 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4687 |  |  |  | HR4686 (Lo-16bits)
4688 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4689 |  |  |  | HR4688 (Lo-16bits)
4690 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4691 |  |  |  | HR4690 (Lo-16bits)
4692 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4693 |  |  |  | HR4692 (Lo-16bits)
4694 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4695 |  |  |  | HR4694 (Lo-16bits)
4696 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4697 |  |  |  | HR4696 (Lo-16bits)
4698 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4699 |  |  |  | HR4698 (Lo-16bits)
4700 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4701 |  |  |  | HR4700 (Lo-16bits)
4702 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4703 |  |  |  | HR4702 (Lo-16bits)
4704 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4705 |  |  |  | HR4704 (Lo-16bits)
4706 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4707 |  |  |  | HR4706 (Lo-16bits)
4708 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4709 |  |  |  | HR4708 (Lo-16bits)
4710 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4711 |  |  |  | HR4710 (Lo-16bits)
4712 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4713 |  |  |  | HR4712 (Lo-16bits)
4714 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4715 |  |  |  | HR4714 (Lo-16bits)
4716 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4717 |  |  |  | HR4716 (Lo-16bits)
4718 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4719 |  |  |  | HR4718 (Lo-16bits)
4720 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4721 |  |  |  | HR4720 (Lo-16bits)
4722 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4723 |  |  |  | HR4722 (Lo-16bits)
4724 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4725 |  |  |  | HR4724 (Lo-16bits)
4726 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4727 |  |  |  | HR4726 (Lo-16bits)
4728 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4729 |  |  |  | HR4728 (Lo-16bits)
4730 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4731 |  |  |  | HR4730 (Lo-16bits)
4732 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4733 |  |  |  | HR4732 (Lo-16bits)
4734 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4735 |  |  |  | HR4734 (Lo-16bits)
4736 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4737 |  |  |  | HR4736 (Lo-16bits)
4738 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4739 |  |  |  | HR4738 (Lo-16bits)
4740 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4741 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4742 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4743 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4744 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4745 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4746 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4747 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4748 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4749 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4750 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4751 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4752 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4753 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4754 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4755 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4756 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4757 |  |  |  | HR4756 (Lo-16bits)
4758 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4759 |  |  |  | HR4758 (Lo-16bits)
4760 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4761 |  |  |  | HR4760 (Lo-16bits)
4762 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4763 |  |  |  | HR4762 (Lo-16bits)
4764 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4765 |  |  |  | HR4764 (Lo-16bits)
4766 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4767 |  |  |  | HR4766 (Lo-16bits)
4768 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4769 |  |  |  | HR4768 (Lo-16bits)
4770 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4771 |  |  |  | HR4770 (Lo-16bits)
4772 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4773 |  |  |  | HR4772 (Lo-16bits)
4774 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4775 |  |  |  | HR4774 (Lo-16bits)
4776 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4777 |  |  |  | HR4776 (Lo-16bits)
4778 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4779 |  |  |  | HR4778 (Lo-16bits)
4780 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4781 |  |  |  | HR4780 (Lo-16bits)
4782 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4783 |  |  |  | HR4782 (Lo-16bits)
4784 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4785 |  |  |  | HR4784 (Lo-16bits)
4786 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4787 |  |  |  | HR4786 (Lo-16bits)
4788 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4789 |  |  |  | HR4788 (Lo-16bits)
4790 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4791 |  |  |  | HR4790 (Lo-16bits)
4792 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4793 |  |  |  | HR4792 (Lo-16bits)
4794 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4795 |  |  |  | HR4794 (Lo-16bits)
4796 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4797 |  |  |  | HR4796 (Lo-16bits)
4798 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4799 |  |  |  | HR4798 (Lo-16bits)
4800 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4801 |  |  |  | HR4800 (Lo-16bits)
4802 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4803 |  |  |  | HR4802 (Lo-16bits)
4804 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4805 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4806 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4807 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4808 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4809 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4810 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4811 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4812 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4813 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4814 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4815 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4816 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4817 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4818 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4819 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4820 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4821 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4822 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4823 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4824 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4825 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4826 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4827 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4828 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4829 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4830 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4831 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4832 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4833 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4834 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4835 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4836 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4837 |  |  |  | HR4836 (Lo-16bits)
4838 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4839 |  |  |  | HR4838 (Lo-16bits)
4840 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4841 |  |  |  | HR4840 (Lo-16bits)
4842 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4843 |  |  |  | HR4842 (Lo-16bits)
4844 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4845 |  |  |  | HR4844 (Lo-16bits)
4846 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4847 |  |  |  | HR4846 (Lo-16bits)
4848 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4849 |  |  |  | HR4848 (Lo-16bits)
4850 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4851 |  |  |  | HR4850 (Lo-16bits)
4852 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4853 |  |  |  | HR4852 (Lo-16bits)
4854 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4855 |  |  |  | HR4854 (Lo-16bits)
4856 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4857 |  |  |  | HR4856 (Lo-16bits)
4858 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4859 |  |  |  | HR4858 (Lo-16bits)
4860 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4861 |  |  |  | HR4860 (Lo-16bits)
4862 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4863 |  |  |  | HR4862 (Lo-16bits)
4864 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4865 |  |  |  | HR4864 (Lo-16bits)
4866 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4867 |  |  |  | HR4866 (Lo-16bits)
4868 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4869 |  |  |  | HR4868 (Lo-16bits)
4870 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4871 |  |  |  | HR4870 (Lo-16bits)
4872 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4873 |  |  |  | HR4872 (Lo-16bits)
4874 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4875 |  |  |  | HR4874 (Lo-16bits)
4876 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4877 |  |  |  | HR4876 (Lo-16bits)
4878 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4879 |  |  |  | HR4878 (Lo-16bits)
4880 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4881 |  |  |  | HR4880 (Lo-16bits)
4882 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4883 |  |  |  | HR4882 (Lo-16bits)
4884 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4885 |  |  |  | HR4884 (Lo-16bits)
4886 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4887 |  |  |  | HR4886 (Lo-16bits)
4888 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4889 |  |  |  | HR4888 (Lo-16bits)
4890 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4891 |  |  |  | HR4890 (Lo-16bits)
4892 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4893 |  |  |  | HR4892 (Lo-16bits)
4894 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4895 |  |  |  | HR4894 (Lo-16bits)
4896 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4897 |  |  |  | HR4896 (Lo-16bits)
4898 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4899 |  |  |  | HR4898 (Lo-16bits)
4900 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4901 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4902 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4903 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4904 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4905 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4906 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4907 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4908 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4909 |  |  |  | HR4908 (Lo-16bits)
4910 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4911 |  |  |  | HR4910 (Lo-16bits)
4912 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4913 |  |  |  | HR4912 (Lo-16bits)
4914 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4915 |  |  |  | HR4914 (Lo-16bits)
4916 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4917 |  |  |  | HR4916 (Lo-16bits)
4918 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4919 |  |  |  | HR4918 (Lo-16bits)
4920 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4921 |  |  |  | HR4920 (Lo-16bits)
4922 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4923 |  |  |  | HR4922 (Lo-16bits)
4924 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4925 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4926 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4927 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4928 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4929 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4930 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4931 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4932 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4933 |  |  |  | HR4932 (Lo-16bits)
4934 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4935 |  |  |  | HR4934 (Lo-16bits)
4936 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4937 |  |  |  | HR4936 (Lo-16bits)
4938 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4939 |  |  |  | HR4938 (Lo-16bits)
4940 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4941 |  |  |  | HR4940 (Lo-16bits)
4942 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4943 |  |  |  | HR4942 (Lo-16bits)
4944 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4945 |  |  |  | HR4944 (Lo-16bits)
4946 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4947 |  |  |  | HR4946 (Lo-16bits)
4948 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4949 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4950 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4951 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4952 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4953 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4954 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4955 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4956 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4957 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4958 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4959 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4960 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4961 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4962 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4963 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4964 | DEF2:I0dir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4965 | DEF2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4966 | DEF2:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4967 | DEF2:I0dir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4968 | DEF2:I0dir>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4969 |  |  |  | HR4968 (Lo-16bits)
4970 | DEF2:I0dir>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4971 |  |  |  | HR4970 (Lo-16bits)
4972 | DEF2:I0dir>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4973 |  |  |  | HR4972 (Lo-16bits)
4974 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4975 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4976 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4977 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4978 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4979 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4980 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4981 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4982 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4983 |  |  |  | HR4982 (Lo-16bits)
4984 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4985 |  |  |  | HR4984 (Lo-16bits)
4986 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4987 |  |  |  | HR4986 (Lo-16bits)
4988 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4989 |  |  |  | HR4988 (Lo-16bits)
4990 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4991 |  |  |  | HR4990 (Lo-16bits)
4992 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4993 |  |  |  | HR4992 (Lo-16bits)
4994 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4995 |  |  |  | HR4994 (Lo-16bits)
4996 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4997 |  |  |  | HR4996 (Lo-16bits)
4998 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4999 |  |  |  | HR4998 (Lo-16bits)
5000 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5001 |  |  |  | HR5000 (Lo-16bits)
5002 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5003 |  |  |  | HR5002 (Lo-16bits)
5004 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5005 |  |  |  | HR5004 (Lo-16bits)
5006 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5007 |  |  |  | HR5006 (Lo-16bits)
5008 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5009 |  |  |  | HR5008 (Lo-16bits)
5010 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5011 |  |  |  | HR5010 (Lo-16bits)
5012 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5013 |  |  |  | HR5012 (Lo-16bits)
5014 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5015 |  |  |  | HR5014 (Lo-16bits)
5016 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5017 |  |  |  | HR5016 (Lo-16bits)
5018 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5019 |  |  |  | HR5018 (Lo-16bits)
5020 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5021 |  |  |  | HR5020 (Lo-16bits)
5022 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5023 |  |  |  | HR5022 (Lo-16bits)
5024 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5025 |  |  |  | HR5024 (Lo-16bits)
5026 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5027 |  |  |  | HR5026 (Lo-16bits)
5028 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5029 |  |  |  | HR5028 (Lo-16bits)
5030 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5031 |  |  |  | HR5030 (Lo-16bits)
5032 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5033 |  |  |  | HR5032 (Lo-16bits)
5034 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5035 |  |  |  | HR5034 (Lo-16bits)
5036 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5037 |  |  |  | HR5036 (Lo-16bits)
5038 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5039 |  |  |  | HR5038 (Lo-16bits)
5040 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5041 |  |  |  | HR5040 (Lo-16bits)
5042 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5043 |  |  |  | HR5042 (Lo-16bits)
5044 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5045 |  |  |  | HR5044 (Lo-16bits)
5046 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5047 |  |  |  | HR5046 (Lo-16bits)
5048 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5049 |  |  |  | HR5048 (Lo-16bits)
5050 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5051 |  |  |  | HR5050 (Lo-16bits)
5052 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5053 |  |  |  | HR5052 (Lo-16bits)
5054 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5055 |  |  |  | HR5054 (Lo-16bits)
5056 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5057 |  |  |  | HR5056 (Lo-16bits)
5058 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5059 |  |  |  | HR5058 (Lo-16bits)
5060 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5061 |  |  |  | HR5060 (Lo-16bits)
5062 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5063 |  |  |  | HR5062 (Lo-16bits)
5064 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5065 |  |  |  | HR5064 (Lo-16bits)
5066 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5067 |  |  |  | HR5066 (Lo-16bits)
5068 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5069 |  |  |  | HR5068 (Lo-16bits)
5070 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5071 |  |  |  | HR5070 (Lo-16bits)
5072 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5073 |  |  |  | HR5072 (Lo-16bits)
5074 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5075 |  |  |  | HR5074 (Lo-16bits)
5076 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5077 |  |  |  | HR5076 (Lo-16bits)
5078 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5079 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5080 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5081 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5082 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5083 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5084 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5085 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5086 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5087 |  |  |  | HR5086 (Lo-16bits)
5088 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5089 |  |  |  | HR5088 (Lo-16bits)
5090 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5091 |  |  |  | HR5090 (Lo-16bits)
5092 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5093 |  |  |  | HR5092 (Lo-16bits)
5094 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5095 |  |  |  | HR5094 (Lo-16bits)
5096 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5097 |  |  |  | HR5096 (Lo-16bits)
5098 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5099 |  |  |  | HR5098 (Lo-16bits)
5100 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5101 |  |  |  | HR5100 (Lo-16bits)
5102 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5103 |  |  |  | HR5102 (Lo-16bits)
5104 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5105 |  |  |  | HR5104 (Lo-16bits)
5106 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5107 |  |  |  | HR5106 (Lo-16bits)
5108 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5109 |  |  |  | HR5108 (Lo-16bits)
5110 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5111 |  |  |  | HR5110 (Lo-16bits)
5112 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5113 |  |  |  | HR5112 (Lo-16bits)
5114 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5115 |  |  |  | HR5114 (Lo-16bits)
5116 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5117 |  |  |  | HR5116 (Lo-16bits)
5118 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5119 |  |  |  | HR5118 (Lo-16bits)
5120 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5121 |  |  |  | HR5120 (Lo-16bits)
5122 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5123 |  |  |  | HR5122 (Lo-16bits)
5124 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5125 |  |  |  | HR5124 (Lo-16bits)
5126 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5127 |  |  |  | HR5126 (Lo-16bits)
5128 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5129 |  |  |  | HR5128 (Lo-16bits)
5130 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5131 |  |  |  | HR5130 (Lo-16bits)
5132 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5133 |  |  |  | HR5132 (Lo-16bits)
5134 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5135 |  |  |  | HR5134 (Lo-16bits)
5136 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5137 |  |  |  | HR5136 (Lo-16bits)
5138 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5139 |  |  |  | HR5138 (Lo-16bits)
5140 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5141 |  |  |  | HR5140 (Lo-16bits)
5142 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5143 |  |  |  | HR5142 (Lo-16bits)
5144 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5145 |  |  |  | HR5144 (Lo-16bits)
5146 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5147 |  |  |  | HR5146 (Lo-16bits)
5148 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5149 |  |  |  | HR5148 (Lo-16bits)
5150 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5151 |  |  |  | HR5150 (Lo-16bits)
5152 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5153 |  |  |  | HR5152 (Lo-16bits)
5154 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5155 |  |  |  | HR5154 (Lo-16bits)
5156 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5157 |  |  |  | HR5156 (Lo-16bits)
5158 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5159 |  |  |  | HR5158 (Lo-16bits)
5160 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5161 |  |  |  | HR5160 (Lo-16bits)
5162 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5163 |  |  |  | HR5162 (Lo-16bits)
5164 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5165 |  |  |  | HR5164 (Lo-16bits)
5166 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5167 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5168 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5169 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5170 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5171 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5172 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5173 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5174 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5175 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5176 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5177 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5178 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5179 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5180 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5181 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5182 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5183 |  |  |  | HR5182 (Lo-16bits)
5184 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5185 |  |  |  | HR5184 (Lo-16bits)
5186 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5187 |  |  |  | HR5186 (Lo-16bits)
5188 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5189 |  |  |  | HR5188 (Lo-16bits)
5190 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5191 |  |  |  | HR5190 (Lo-16bits)
5192 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5193 |  |  |  | HR5192 (Lo-16bits)
5194 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5195 |  |  |  | HR5194 (Lo-16bits)
5196 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5197 |  |  |  | HR5196 (Lo-16bits)
5198 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5199 |  |  |  | HR5198 (Lo-16bits)
5200 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5201 |  |  |  | HR5200 (Lo-16bits)
5202 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5203 |  |  |  | HR5202 (Lo-16bits)
5204 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5205 |  |  |  | HR5204 (Lo-16bits)
5206 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5207 |  |  |  | HR5206 (Lo-16bits)
5208 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5209 |  |  |  | HR5208 (Lo-16bits)
5210 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5211 |  |  |  | HR5210 (Lo-16bits)
5212 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5213 |  |  |  | HR5212 (Lo-16bits)
5214 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5215 |  |  |  | HR5214 (Lo-16bits)
5216 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5217 |  |  |  | HR5216 (Lo-16bits)
5218 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5219 |  |  |  | HR5218 (Lo-16bits)
5220 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5221 |  |  |  | HR5220 (Lo-16bits)
5222 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5223 |  |  |  | HR5222 (Lo-16bits)
5224 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5225 |  |  |  | HR5224 (Lo-16bits)
5226 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5227 |  |  |  | HR5226 (Lo-16bits)
5228 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5229 |  |  |  | HR5228 (Lo-16bits)
5230 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5231 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5232 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5233 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5234 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5235 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5236 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5237 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5238 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5239 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5240 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5241 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5242 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5243 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5244 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5245 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5246 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5247 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5248 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5249 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5250 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5251 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5252 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5253 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5254 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5255 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5256 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5257 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5258 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5259 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5260 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5261 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5262 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5263 |  |  |  | HR5262 (Lo-16bits)
5264 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5265 |  |  |  | HR5264 (Lo-16bits)
5266 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5267 |  |  |  | HR5266 (Lo-16bits)
5268 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5269 |  |  |  | HR5268 (Lo-16bits)
5270 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5271 |  |  |  | HR5270 (Lo-16bits)
5272 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5273 |  |  |  | HR5272 (Lo-16bits)
5274 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5275 |  |  |  | HR5274 (Lo-16bits)
5276 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5277 |  |  |  | HR5276 (Lo-16bits)
5278 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5279 |  |  |  | HR5278 (Lo-16bits)
5280 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5281 |  |  |  | HR5280 (Lo-16bits)
5282 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5283 |  |  |  | HR5282 (Lo-16bits)
5284 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5285 |  |  |  | HR5284 (Lo-16bits)
5286 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5287 |  |  |  | HR5286 (Lo-16bits)
5288 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5289 |  |  |  | HR5288 (Lo-16bits)
5290 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5291 |  |  |  | HR5290 (Lo-16bits)
5292 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5293 |  |  |  | HR5292 (Lo-16bits)
5294 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5295 |  |  |  | HR5294 (Lo-16bits)
5296 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5297 |  |  |  | HR5296 (Lo-16bits)
5298 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5299 |  |  |  | HR5298 (Lo-16bits)
5300 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5301 |  |  |  | HR5300 (Lo-16bits)
5302 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5303 |  |  |  | HR5302 (Lo-16bits)
5304 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5305 |  |  |  | HR5304 (Lo-16bits)
5306 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5307 |  |  |  | HR5306 (Lo-16bits)
5308 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5309 |  |  |  | HR5308 (Lo-16bits)
5310 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5311 |  |  |  | HR5310 (Lo-16bits)
5312 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5313 |  |  |  | HR5312 (Lo-16bits)
5314 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5315 |  |  |  | HR5314 (Lo-16bits)
5316 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5317 |  |  |  | HR5316 (Lo-16bits)
5318 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5319 |  |  |  | HR5318 (Lo-16bits)
5320 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5321 |  |  |  | HR5320 (Lo-16bits)
5322 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5323 |  |  |  | HR5322 (Lo-16bits)
5324 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5325 |  |  |  | HR5324 (Lo-16bits)
5326 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5327 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5328 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5329 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5330 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5331 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5332 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5333 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5334 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5335 |  |  |  | HR5334 (Lo-16bits)
5336 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5337 |  |  |  | HR5336 (Lo-16bits)
5338 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5339 |  |  |  | HR5338 (Lo-16bits)
5340 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5341 |  |  |  | HR5340 (Lo-16bits)
5342 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5343 |  |  |  | HR5342 (Lo-16bits)
5344 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5345 |  |  |  | HR5344 (Lo-16bits)
5346 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5347 |  |  |  | HR5346 (Lo-16bits)
5348 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5349 |  |  |  | HR5348 (Lo-16bits)
5350 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5351 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5352 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5353 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5354 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5355 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5356 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5357 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5358 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5359 |  |  |  | HR5358 (Lo-16bits)
5360 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5361 |  |  |  | HR5360 (Lo-16bits)
5362 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5363 |  |  |  | HR5362 (Lo-16bits)
5364 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5365 |  |  |  | HR5364 (Lo-16bits)
5366 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5367 |  |  |  | HR5366 (Lo-16bits)
5368 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5369 |  |  |  | HR5368 (Lo-16bits)
5370 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5371 |  |  |  | HR5370 (Lo-16bits)
5372 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5373 |  |  |  | HR5372 (Lo-16bits)
5374 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5375 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5376 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5377 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5378 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5379 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5380 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5381 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5382 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5383 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5384 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5385 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5386 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5387 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5388 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5389 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5390 | DEF3:I0dir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5391 | DEF3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5392 | DEF3:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5393 | DEF3:I0dir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5394 | DEF3:I0dir>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5395 |  |  |  | HR5394 (Lo-16bits)
5396 | DEF3:I0dir>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5397 |  |  |  | HR5396 (Lo-16bits)
5398 | DEF3:I0dir>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5399 |  |  |  | HR5398 (Lo-16bits)
5400 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5401 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5402 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5403 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5404 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5405 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5406 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5407 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5408 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5409 |  |  |  | HR5408 (Lo-16bits)
5410 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5411 |  |  |  | HR5410 (Lo-16bits)
5412 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5413 |  |  |  | HR5412 (Lo-16bits)
5414 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5415 |  |  |  | HR5414 (Lo-16bits)
5416 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5417 |  |  |  | HR5416 (Lo-16bits)
5418 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5419 |  |  |  | HR5418 (Lo-16bits)
5420 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5421 |  |  |  | HR5420 (Lo-16bits)
5422 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5423 |  |  |  | HR5422 (Lo-16bits)
5424 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5425 |  |  |  | HR5424 (Lo-16bits)
5426 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5427 |  |  |  | HR5426 (Lo-16bits)
5428 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5429 |  |  |  | HR5428 (Lo-16bits)
5430 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5431 |  |  |  | HR5430 (Lo-16bits)
5432 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5433 |  |  |  | HR5432 (Lo-16bits)
5434 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5435 |  |  |  | HR5434 (Lo-16bits)
5436 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5437 |  |  |  | HR5436 (Lo-16bits)
5438 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5439 |  |  |  | HR5438 (Lo-16bits)
5440 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5441 |  |  |  | HR5440 (Lo-16bits)
5442 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5443 |  |  |  | HR5442 (Lo-16bits)
5444 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5445 |  |  |  | HR5444 (Lo-16bits)
5446 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5447 |  |  |  | HR5446 (Lo-16bits)
5448 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5449 |  |  |  | HR5448 (Lo-16bits)
5450 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5451 |  |  |  | HR5450 (Lo-16bits)
5452 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5453 |  |  |  | HR5452 (Lo-16bits)
5454 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5455 |  |  |  | HR5454 (Lo-16bits)
5456 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5457 |  |  |  | HR5456 (Lo-16bits)
5458 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5459 |  |  |  | HR5458 (Lo-16bits)
5460 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5461 |  |  |  | HR5460 (Lo-16bits)
5462 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5463 |  |  |  | HR5462 (Lo-16bits)
5464 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5465 |  |  |  | HR5464 (Lo-16bits)
5466 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5467 |  |  |  | HR5466 (Lo-16bits)
5468 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5469 |  |  |  | HR5468 (Lo-16bits)
5470 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5471 |  |  |  | HR5470 (Lo-16bits)
5472 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5473 |  |  |  | HR5472 (Lo-16bits)
5474 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5475 |  |  |  | HR5474 (Lo-16bits)
5476 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5477 |  |  |  | HR5476 (Lo-16bits)
5478 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5479 |  |  |  | HR5478 (Lo-16bits)
5480 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5481 |  |  |  | HR5480 (Lo-16bits)
5482 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5483 |  |  |  | HR5482 (Lo-16bits)
5484 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5485 |  |  |  | HR5484 (Lo-16bits)
5486 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5487 |  |  |  | HR5486 (Lo-16bits)
5488 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5489 |  |  |  | HR5488 (Lo-16bits)
5490 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5491 |  |  |  | HR5490 (Lo-16bits)
5492 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5493 |  |  |  | HR5492 (Lo-16bits)
5494 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5495 |  |  |  | HR5494 (Lo-16bits)
5496 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5497 |  |  |  | HR5496 (Lo-16bits)
5498 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5499 |  |  |  | HR5498 (Lo-16bits)
5500 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5501 |  |  |  | HR5500 (Lo-16bits)
5502 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5503 |  |  |  | HR5502 (Lo-16bits)
5504 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5505 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5506 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5507 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5508 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5509 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5510 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5511 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5512 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5513 |  |  |  | HR5512 (Lo-16bits)
5514 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5515 |  |  |  | HR5514 (Lo-16bits)
5516 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5517 |  |  |  | HR5516 (Lo-16bits)
5518 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5519 |  |  |  | HR5518 (Lo-16bits)
5520 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5521 |  |  |  | HR5520 (Lo-16bits)
5522 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5523 |  |  |  | HR5522 (Lo-16bits)
5524 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5525 |  |  |  | HR5524 (Lo-16bits)
5526 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5527 |  |  |  | HR5526 (Lo-16bits)
5528 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5529 |  |  |  | HR5528 (Lo-16bits)
5530 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5531 |  |  |  | HR5530 (Lo-16bits)
5532 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5533 |  |  |  | HR5532 (Lo-16bits)
5534 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5535 |  |  |  | HR5534 (Lo-16bits)
5536 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5537 |  |  |  | HR5536 (Lo-16bits)
5538 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5539 |  |  |  | HR5538 (Lo-16bits)
5540 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5541 |  |  |  | HR5540 (Lo-16bits)
5542 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5543 |  |  |  | HR5542 (Lo-16bits)
5544 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5545 |  |  |  | HR5544 (Lo-16bits)
5546 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5547 |  |  |  | HR5546 (Lo-16bits)
5548 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5549 |  |  |  | HR5548 (Lo-16bits)
5550 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5551 |  |  |  | HR5550 (Lo-16bits)
5552 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5553 |  |  |  | HR5552 (Lo-16bits)
5554 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5555 |  |  |  | HR5554 (Lo-16bits)
5556 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5557 |  |  |  | HR5556 (Lo-16bits)
5558 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5559 |  |  |  | HR5558 (Lo-16bits)
5560 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5561 |  |  |  | HR5560 (Lo-16bits)
5562 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5563 |  |  |  | HR5562 (Lo-16bits)
5564 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5565 |  |  |  | HR5564 (Lo-16bits)
5566 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5567 |  |  |  | HR5566 (Lo-16bits)
5568 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5569 |  |  |  | HR5568 (Lo-16bits)
5570 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5571 |  |  |  | HR5570 (Lo-16bits)
5572 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5573 |  |  |  | HR5572 (Lo-16bits)
5574 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5575 |  |  |  | HR5574 (Lo-16bits)
5576 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5577 |  |  |  | HR5576 (Lo-16bits)
5578 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5579 |  |  |  | HR5578 (Lo-16bits)
5580 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5581 |  |  |  | HR5580 (Lo-16bits)
5582 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5583 |  |  |  | HR5582 (Lo-16bits)
5584 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5585 |  |  |  | HR5584 (Lo-16bits)
5586 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5587 |  |  |  | HR5586 (Lo-16bits)
5588 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5589 |  |  |  | HR5588 (Lo-16bits)
5590 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5591 |  |  |  | HR5590 (Lo-16bits)
5592 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5593 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5594 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5595 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5596 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5597 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5598 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5599 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5600 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5601 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5602 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5603 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5604 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5605 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5606 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5607 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5608 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5609 |  |  |  | HR5608 (Lo-16bits)
5610 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5611 |  |  |  | HR5610 (Lo-16bits)
5612 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5613 |  |  |  | HR5612 (Lo-16bits)
5614 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5615 |  |  |  | HR5614 (Lo-16bits)
5616 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5617 |  |  |  | HR5616 (Lo-16bits)
5618 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5619 |  |  |  | HR5618 (Lo-16bits)
5620 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5621 |  |  |  | HR5620 (Lo-16bits)
5622 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5623 |  |  |  | HR5622 (Lo-16bits)
5624 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5625 |  |  |  | HR5624 (Lo-16bits)
5626 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5627 |  |  |  | HR5626 (Lo-16bits)
5628 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5629 |  |  |  | HR5628 (Lo-16bits)
5630 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5631 |  |  |  | HR5630 (Lo-16bits)
5632 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5633 |  |  |  | HR5632 (Lo-16bits)
5634 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5635 |  |  |  | HR5634 (Lo-16bits)
5636 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5637 |  |  |  | HR5636 (Lo-16bits)
5638 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5639 |  |  |  | HR5638 (Lo-16bits)
5640 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5641 |  |  |  | HR5640 (Lo-16bits)
5642 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5643 |  |  |  | HR5642 (Lo-16bits)
5644 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5645 |  |  |  | HR5644 (Lo-16bits)
5646 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5647 |  |  |  | HR5646 (Lo-16bits)
5648 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5649 |  |  |  | HR5648 (Lo-16bits)
5650 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5651 |  |  |  | HR5650 (Lo-16bits)
5652 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5653 |  |  |  | HR5652 (Lo-16bits)
5654 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5655 |  |  |  | HR5654 (Lo-16bits)
5656 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5657 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5658 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5659 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5660 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5661 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5662 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5663 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5664 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5665 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5666 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5667 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5668 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5669 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5670 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5671 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5672 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5673 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5674 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5675 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5676 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5677 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5678 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5679 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5680 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5681 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5682 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5683 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5684 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5685 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5686 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5687 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5688 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5689 |  |  |  | HR5688 (Lo-16bits)
5690 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5691 |  |  |  | HR5690 (Lo-16bits)
5692 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5693 |  |  |  | HR5692 (Lo-16bits)
5694 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5695 |  |  |  | HR5694 (Lo-16bits)
5696 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5697 |  |  |  | HR5696 (Lo-16bits)
5698 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5699 |  |  |  | HR5698 (Lo-16bits)
5700 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5701 |  |  |  | HR5700 (Lo-16bits)
5702 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5703 |  |  |  | HR5702 (Lo-16bits)
5704 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5705 |  |  |  | HR5704 (Lo-16bits)
5706 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5707 |  |  |  | HR5706 (Lo-16bits)
5708 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5709 |  |  |  | HR5708 (Lo-16bits)
5710 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5711 |  |  |  | HR5710 (Lo-16bits)
5712 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5713 |  |  |  | HR5712 (Lo-16bits)
5714 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5715 |  |  |  | HR5714 (Lo-16bits)
5716 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5717 |  |  |  | HR5716 (Lo-16bits)
5718 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5719 |  |  |  | HR5718 (Lo-16bits)
5720 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5721 |  |  |  | HR5720 (Lo-16bits)
5722 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5723 |  |  |  | HR5722 (Lo-16bits)
5724 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5725 |  |  |  | HR5724 (Lo-16bits)
5726 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5727 |  |  |  | HR5726 (Lo-16bits)
5728 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5729 |  |  |  | HR5728 (Lo-16bits)
5730 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5731 |  |  |  | HR5730 (Lo-16bits)
5732 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5733 |  |  |  | HR5732 (Lo-16bits)
5734 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5735 |  |  |  | HR5734 (Lo-16bits)
5736 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5737 |  |  |  | HR5736 (Lo-16bits)
5738 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5739 |  |  |  | HR5738 (Lo-16bits)
5740 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5741 |  |  |  | HR5740 (Lo-16bits)
5742 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5743 |  |  |  | HR5742 (Lo-16bits)
5744 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5745 |  |  |  | HR5744 (Lo-16bits)
5746 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5747 |  |  |  | HR5746 (Lo-16bits)
5748 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5749 |  |  |  | HR5748 (Lo-16bits)
5750 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5751 |  |  |  | HR5750 (Lo-16bits)
5752 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5753 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5754 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5755 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5756 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5757 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5758 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5759 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5760 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5761 |  |  |  | HR5760 (Lo-16bits)
5762 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5763 |  |  |  | HR5762 (Lo-16bits)
5764 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5765 |  |  |  | HR5764 (Lo-16bits)
5766 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5767 |  |  |  | HR5766 (Lo-16bits)
5768 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5769 |  |  |  | HR5768 (Lo-16bits)
5770 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5771 |  |  |  | HR5770 (Lo-16bits)
5772 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5773 |  |  |  | HR5772 (Lo-16bits)
5774 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5775 |  |  |  | HR5774 (Lo-16bits)
5776 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5777 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5778 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5779 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5780 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5781 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5782 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5783 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5784 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5785 |  |  |  | HR5784 (Lo-16bits)
5786 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5787 |  |  |  | HR5786 (Lo-16bits)
5788 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5789 |  |  |  | HR5788 (Lo-16bits)
5790 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5791 |  |  |  | HR5790 (Lo-16bits)
5792 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5793 |  |  |  | HR5792 (Lo-16bits)
5794 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5795 |  |  |  | HR5794 (Lo-16bits)
5796 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5797 |  |  |  | HR5796 (Lo-16bits)
5798 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5799 |  |  |  | HR5798 (Lo-16bits)
5800 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5801 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5802 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5803 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5804 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5805 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5806 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5807 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5808 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5809 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5810 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5811 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5812 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5813 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5814 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5815 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5816 | DEF4:I0dir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5817 | DEF4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5818 | DEF4:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5819 | DEF4:I0dir>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5820 | DEF4:I0dir>>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5821 |  |  |  | HR5820 (Lo-16bits)
5822 | DEF4:I0dir>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5823 |  |  |  | HR5822 (Lo-16bits)
5824 | DEF4:I0dir>>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5825 |  |  |  | HR5824 (Lo-16bits)
5826 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5827 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5828 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5829 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5830 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5831 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5832 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5833 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5834 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5835 |  |  |  | HR5834 (Lo-16bits)
5836 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5837 |  |  |  | HR5836 (Lo-16bits)
5838 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5839 |  |  |  | HR5838 (Lo-16bits)
5840 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5841 |  |  |  | HR5840 (Lo-16bits)
5842 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5843 |  |  |  | HR5842 (Lo-16bits)
5844 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5845 |  |  |  | HR5844 (Lo-16bits)
5846 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5847 |  |  |  | HR5846 (Lo-16bits)
5848 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5849 |  |  |  | HR5848 (Lo-16bits)
5850 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5851 |  |  |  | HR5850 (Lo-16bits)
5852 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5853 |  |  |  | HR5852 (Lo-16bits)
5854 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5855 |  |  |  | HR5854 (Lo-16bits)
5856 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5857 |  |  |  | HR5856 (Lo-16bits)
5858 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5859 |  |  |  | HR5858 (Lo-16bits)
5860 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5861 |  |  |  | HR5860 (Lo-16bits)
5862 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5863 |  |  |  | HR5862 (Lo-16bits)
5864 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5865 |  |  |  | HR5864 (Lo-16bits)
5866 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5867 |  |  |  | HR5866 (Lo-16bits)
5868 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5869 |  |  |  | HR5868 (Lo-16bits)
5870 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5871 |  |  |  | HR5870 (Lo-16bits)
5872 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5873 |  |  |  | HR5872 (Lo-16bits)
5874 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5875 |  |  |  | HR5874 (Lo-16bits)
5876 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5877 |  |  |  | HR5876 (Lo-16bits)
5878 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5879 |  |  |  | HR5878 (Lo-16bits)
5880 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5881 |  |  |  | HR5880 (Lo-16bits)
5882 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5883 |  |  |  | HR5882 (Lo-16bits)
5884 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5885 |  |  |  | HR5884 (Lo-16bits)
5886 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5887 |  |  |  | HR5886 (Lo-16bits)
5888 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5889 |  |  |  | HR5888 (Lo-16bits)
5890 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5891 |  |  |  | HR5890 (Lo-16bits)
5892 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5893 |  |  |  | HR5892 (Lo-16bits)
5894 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5895 |  |  |  | HR5894 (Lo-16bits)
5896 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5897 |  |  |  | HR5896 (Lo-16bits)
5898 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5899 |  |  |  | HR5898 (Lo-16bits)
5900 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5901 |  |  |  | HR5900 (Lo-16bits)
5902 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5903 |  |  |  | HR5902 (Lo-16bits)
5904 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5905 |  |  |  | HR5904 (Lo-16bits)
5906 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5907 |  |  |  | HR5906 (Lo-16bits)
5908 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5909 |  |  |  | HR5908 (Lo-16bits)
5910 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5911 |  |  |  | HR5910 (Lo-16bits)
5912 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5913 |  |  |  | HR5912 (Lo-16bits)
5914 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5915 |  |  |  | HR5914 (Lo-16bits)
5916 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5917 |  |  |  | HR5916 (Lo-16bits)
5918 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5919 |  |  |  | HR5918 (Lo-16bits)
5920 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5921 |  |  |  | HR5920 (Lo-16bits)
5922 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5923 |  |  |  | HR5922 (Lo-16bits)
5924 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5925 |  |  |  | HR5924 (Lo-16bits)
5926 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5927 |  |  |  | HR5926 (Lo-16bits)
5928 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5929 |  |  |  | HR5928 (Lo-16bits)
5930 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5931 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5932 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5933 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5934 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5935 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5936 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5937 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5938 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5939 |  |  |  | HR5938 (Lo-16bits)
5940 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5941 |  |  |  | HR5940 (Lo-16bits)
5942 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5943 |  |  |  | HR5942 (Lo-16bits)
5944 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5945 |  |  |  | HR5944 (Lo-16bits)
5946 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5947 |  |  |  | HR5946 (Lo-16bits)
5948 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5949 |  |  |  | HR5948 (Lo-16bits)
5950 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5951 |  |  |  | HR5950 (Lo-16bits)
5952 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5953 |  |  |  | HR5952 (Lo-16bits)
5954 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5955 |  |  |  | HR5954 (Lo-16bits)
5956 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5957 |  |  |  | HR5956 (Lo-16bits)
5958 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5959 |  |  |  | HR5958 (Lo-16bits)
5960 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5961 |  |  |  | HR5960 (Lo-16bits)
5962 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5963 |  |  |  | HR5962 (Lo-16bits)
5964 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5965 |  |  |  | HR5964 (Lo-16bits)
5966 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5967 |  |  |  | HR5966 (Lo-16bits)
5968 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5969 |  |  |  | HR5968 (Lo-16bits)
5970 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5971 |  |  |  | HR5970 (Lo-16bits)
5972 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5973 |  |  |  | HR5972 (Lo-16bits)
5974 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5975 |  |  |  | HR5974 (Lo-16bits)
5976 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5977 |  |  |  | HR5976 (Lo-16bits)
5978 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5979 |  |  |  | HR5978 (Lo-16bits)
5980 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5981 |  |  |  | HR5980 (Lo-16bits)
5982 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5983 |  |  |  | HR5982 (Lo-16bits)
5984 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5985 |  |  |  | HR5984 (Lo-16bits)
5986 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5987 |  |  |  | HR5986 (Lo-16bits)
5988 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5989 |  |  |  | HR5988 (Lo-16bits)
5990 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5991 |  |  |  | HR5990 (Lo-16bits)
5992 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5993 |  |  |  | HR5992 (Lo-16bits)
5994 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5995 |  |  |  | HR5994 (Lo-16bits)
5996 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5997 |  |  |  | HR5996 (Lo-16bits)
5998 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5999 |  |  |  | HR5998 (Lo-16bits)
6000 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6001 |  |  |  | HR6000 (Lo-16bits)
6002 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6003 |  |  |  | HR6002 (Lo-16bits)
6004 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6005 |  |  |  | HR6004 (Lo-16bits)
6006 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6007 |  |  |  | HR6006 (Lo-16bits)
6008 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6009 |  |  |  | HR6008 (Lo-16bits)
6010 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6011 |  |  |  | HR6010 (Lo-16bits)
6012 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6013 |  |  |  | HR6012 (Lo-16bits)
6014 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6015 |  |  |  | HR6014 (Lo-16bits)
6016 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6017 |  |  |  | HR6016 (Lo-16bits)
6018 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6019 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6020 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6021 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6022 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6023 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6024 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6025 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6026 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6027 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6028 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6029 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6030 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6031 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6032 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6033 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6034 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6035 |  |  |  | HR6034 (Lo-16bits)
6036 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6037 |  |  |  | HR6036 (Lo-16bits)
6038 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6039 |  |  |  | HR6038 (Lo-16bits)
6040 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6041 |  |  |  | HR6040 (Lo-16bits)
6042 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6043 |  |  |  | HR6042 (Lo-16bits)
6044 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6045 |  |  |  | HR6044 (Lo-16bits)
6046 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6047 |  |  |  | HR6046 (Lo-16bits)
6048 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6049 |  |  |  | HR6048 (Lo-16bits)
6050 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6051 |  |  |  | HR6050 (Lo-16bits)
6052 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6053 |  |  |  | HR6052 (Lo-16bits)
6054 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6055 |  |  |  | HR6054 (Lo-16bits)
6056 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6057 |  |  |  | HR6056 (Lo-16bits)
6058 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6059 |  |  |  | HR6058 (Lo-16bits)
6060 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6061 |  |  |  | HR6060 (Lo-16bits)
6062 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6063 |  |  |  | HR6062 (Lo-16bits)
6064 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6065 |  |  |  | HR6064 (Lo-16bits)
6066 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6067 |  |  |  | HR6066 (Lo-16bits)
6068 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6069 |  |  |  | HR6068 (Lo-16bits)
6070 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6071 |  |  |  | HR6070 (Lo-16bits)
6072 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6073 |  |  |  | HR6072 (Lo-16bits)
6074 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6075 |  |  |  | HR6074 (Lo-16bits)
6076 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6077 |  |  |  | HR6076 (Lo-16bits)
6078 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6079 |  |  |  | HR6078 (Lo-16bits)
6080 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6081 |  |  |  | HR6080 (Lo-16bits)
6082 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6083 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6084 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6085 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6086 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6087 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6088 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6089 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6090 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6091 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6092 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6093 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6094 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6095 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6096 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6097 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6098 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6099 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6100 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6101 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6102 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6103 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6104 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6105 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6106 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6107 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6108 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6109 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6110 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6111 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6112 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6113 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6114 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6115 |  |  |  | HR6114 (Lo-16bits)
6116 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6117 |  |  |  | HR6116 (Lo-16bits)
6118 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6119 |  |  |  | HR6118 (Lo-16bits)
6120 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6121 |  |  |  | HR6120 (Lo-16bits)
6122 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6123 |  |  |  | HR6122 (Lo-16bits)
6124 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6125 |  |  |  | HR6124 (Lo-16bits)
6126 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6127 |  |  |  | HR6126 (Lo-16bits)
6128 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6129 |  |  |  | HR6128 (Lo-16bits)
6130 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6131 |  |  |  | HR6130 (Lo-16bits)
6132 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6133 |  |  |  | HR6132 (Lo-16bits)
6134 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6135 |  |  |  | HR6134 (Lo-16bits)
6136 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6137 |  |  |  | HR6136 (Lo-16bits)
6138 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6139 |  |  |  | HR6138 (Lo-16bits)
6140 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6141 |  |  |  | HR6140 (Lo-16bits)
6142 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6143 |  |  |  | HR6142 (Lo-16bits)
6144 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6145 |  |  |  | HR6144 (Lo-16bits)
6146 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6147 |  |  |  | HR6146 (Lo-16bits)
6148 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6149 |  |  |  | HR6148 (Lo-16bits)
6150 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6151 |  |  |  | HR6150 (Lo-16bits)
6152 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6153 |  |  |  | HR6152 (Lo-16bits)
6154 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6155 |  |  |  | HR6154 (Lo-16bits)
6156 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6157 |  |  |  | HR6156 (Lo-16bits)
6158 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6159 |  |  |  | HR6158 (Lo-16bits)
6160 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6161 |  |  |  | HR6160 (Lo-16bits)
6162 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6163 |  |  |  | HR6162 (Lo-16bits)
6164 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6165 |  |  |  | HR6164 (Lo-16bits)
6166 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6167 |  |  |  | HR6166 (Lo-16bits)
6168 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6169 |  |  |  | HR6168 (Lo-16bits)
6170 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6171 |  |  |  | HR6170 (Lo-16bits)
6172 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6173 |  |  |  | HR6172 (Lo-16bits)
6174 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6175 |  |  |  | HR6174 (Lo-16bits)
6176 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6177 |  |  |  | HR6176 (Lo-16bits)
6178 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6179 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6180 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6181 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6182 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6183 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6184 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6185 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6186 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6187 |  |  |  | HR6186 (Lo-16bits)
6188 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6189 |  |  |  | HR6188 (Lo-16bits)
6190 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6191 |  |  |  | HR6190 (Lo-16bits)
6192 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6193 |  |  |  | HR6192 (Lo-16bits)
6194 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6195 |  |  |  | HR6194 (Lo-16bits)
6196 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6197 |  |  |  | HR6196 (Lo-16bits)
6198 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6199 |  |  |  | HR6198 (Lo-16bits)
6200 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6201 |  |  |  | HR6200 (Lo-16bits)
6202 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6203 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6204 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6205 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6206 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6207 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6208 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6209 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6210 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6211 |  |  |  | HR6210 (Lo-16bits)
6212 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6213 |  |  |  | HR6212 (Lo-16bits)
6214 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6215 |  |  |  | HR6214 (Lo-16bits)
6216 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6217 |  |  |  | HR6216 (Lo-16bits)
6218 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6219 |  |  |  | HR6218 (Lo-16bits)
6220 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6221 |  |  |  | HR6220 (Lo-16bits)
6222 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6223 |  |  |  | HR6222 (Lo-16bits)
6224 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6225 |  |  |  | HR6224 (Lo-16bits)
6226 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6227 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6228 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6229 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6230 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6231 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6232 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6233 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6234 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6235 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6236 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6237 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6238 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6239 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6240 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6241 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6242 | IEF1:I0Int> condition | R | 1 | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
6243 | IEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
6244 | CUB1:I2> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6245 | CUB1:I2> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6246 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6247 |  |  |  | HR6246 (Lo-16bits)
6248 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6249 |  |  |  | HR6248 (Lo-16bits)
6250 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6251 |  |  |  | HR6250 (Lo-16bits)
6252 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6253 |  |  |  | HR6252 (Lo-16bits)
6254 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6255 |  |  |  | HR6254 (Lo-16bits)
6256 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6257 |  |  |  | HR6256 (Lo-16bits)
6258 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6259 |  |  |  | HR6258 (Lo-16bits)
6260 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6261 |  |  |  | HR6260 (Lo-16bits)
6262 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6263 |  |  |  | HR6262 (Lo-16bits)
6264 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6265 |  |  |  | HR6264 (Lo-16bits)
6266 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6267 |  |  |  | HR6266 (Lo-16bits)
6268 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6269 |  |  |  | HR6268 (Lo-16bits)
6270 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6271 |  |  |  | HR6270 (Lo-16bits)
6272 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6273 |  |  |  | HR6272 (Lo-16bits)
6274 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6275 |  |  |  | HR6274 (Lo-16bits)
6276 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6277 |  |  |  | HR6276 (Lo-16bits)
6278 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6279 |  |  |  | HR6278 (Lo-16bits)
6280 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6281 |  |  |  | HR6280 (Lo-16bits)
6282 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6283 |  |  |  | HR6282 (Lo-16bits)
6284 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6285 |  |  |  | HR6284 (Lo-16bits)
6286 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6287 |  |  |  | HR6286 (Lo-16bits)
6288 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6289 |  |  |  | HR6288 (Lo-16bits)
6290 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6291 |  |  |  | HR6290 (Lo-16bits)
6292 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6293 |  |  |  | HR6292 (Lo-16bits)
6294 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6295 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6296 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6297 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6298 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6299 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6300 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6301 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6302 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6303 |  |  |  | HR6302 (Lo-16bits)
6304 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6305 |  |  |  | HR6304 (Lo-16bits)
6306 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6307 |  |  |  | HR6306 (Lo-16bits)
6308 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6309 |  |  |  | HR6308 (Lo-16bits)
6310 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6311 |  |  |  | HR6310 (Lo-16bits)
6312 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6313 |  |  |  | HR6312 (Lo-16bits)
6314 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6315 |  |  |  | HR6314 (Lo-16bits)
6316 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6317 |  |  |  | HR6316 (Lo-16bits)
6318 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6319 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6320 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6321 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6322 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6323 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6324 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6325 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6326 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6327 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6328 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6329 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6330 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6331 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6332 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6333 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6334 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6335 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6336 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6337 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6338 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6339 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6340 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6341 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6342 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6343 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6344 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6345 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6346 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6347 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6348 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6349 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6350 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6351 |  |  |  | HR6350 (Lo-16bits)
6352 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6353 |  |  |  | HR6352 (Lo-16bits)
6354 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6355 |  |  |  | HR6354 (Lo-16bits)
6356 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6357 |  |  |  | HR6356 (Lo-16bits)
6358 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6359 |  |  |  | HR6358 (Lo-16bits)
6360 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6361 |  |  |  | HR6360 (Lo-16bits)
6362 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6363 |  |  |  | HR6362 (Lo-16bits)
6364 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6365 |  |  |  | HR6364 (Lo-16bits)
6366 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6367 |  |  |  | HR6366 (Lo-16bits)
6368 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6369 |  |  |  | HR6368 (Lo-16bits)
6370 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6371 |  |  |  | HR6370 (Lo-16bits)
6372 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6373 |  |  |  | HR6372 (Lo-16bits)
6374 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6375 |  |  |  | HR6374 (Lo-16bits)
6376 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6377 |  |  |  | HR6376 (Lo-16bits)
6378 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6379 |  |  |  | HR6378 (Lo-16bits)
6380 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6381 |  |  |  | HR6380 (Lo-16bits)
6382 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6383 |  |  |  | HR6382 (Lo-16bits)
6384 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6385 |  |  |  | HR6384 (Lo-16bits)
6386 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6387 |  |  |  | HR6386 (Lo-16bits)
6388 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6389 |  |  |  | HR6388 (Lo-16bits)
6390 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6391 |  |  |  | HR6390 (Lo-16bits)
6392 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6393 |  |  |  | HR6392 (Lo-16bits)
6394 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6395 |  |  |  | HR6394 (Lo-16bits)
6396 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6397 |  |  |  | HR6396 (Lo-16bits)
6398 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6399 |  |  |  | HR6398 (Lo-16bits)
6400 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6401 |  |  |  | HR6400 (Lo-16bits)
6402 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6403 |  |  |  | HR6402 (Lo-16bits)
6404 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6405 |  |  |  | HR6404 (Lo-16bits)
6406 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6407 |  |  |  | HR6406 (Lo-16bits)
6408 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6409 |  |  |  | HR6408 (Lo-16bits)
6410 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6411 |  |  |  | HR6410 (Lo-16bits)
6412 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6413 |  |  |  | HR6412 (Lo-16bits)
6414 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6415 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6416 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6417 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6418 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6419 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6420 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6421 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6422 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6423 |  |  |  | HR6422 (Lo-16bits)
6424 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6425 |  |  |  | HR6424 (Lo-16bits)
6426 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6427 |  |  |  | HR6426 (Lo-16bits)
6428 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6429 |  |  |  | HR6428 (Lo-16bits)
6430 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6431 |  |  |  | HR6430 (Lo-16bits)
6432 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6433 |  |  |  | HR6432 (Lo-16bits)
6434 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6435 |  |  |  | HR6434 (Lo-16bits)
6436 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6437 |  |  |  | HR6436 (Lo-16bits)
6438 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6439 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6440 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6441 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6442 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6443 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6444 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6445 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6446 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6447 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6448 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6449 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6450 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6451 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6452 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6453 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6454 | CUB2:I2>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6455 | CUB2:I2>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6456 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6457 |  |  |  | HR6456 (Lo-16bits)
6458 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6459 |  |  |  | HR6458 (Lo-16bits)
6460 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6461 |  |  |  | HR6460 (Lo-16bits)
6462 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6463 |  |  |  | HR6462 (Lo-16bits)
6464 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6465 |  |  |  | HR6464 (Lo-16bits)
6466 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6467 |  |  |  | HR6466 (Lo-16bits)
6468 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6469 |  |  |  | HR6468 (Lo-16bits)
6470 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6471 |  |  |  | HR6470 (Lo-16bits)
6472 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6473 |  |  |  | HR6472 (Lo-16bits)
6474 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6475 |  |  |  | HR6474 (Lo-16bits)
6476 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6477 |  |  |  | HR6476 (Lo-16bits)
6478 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6479 |  |  |  | HR6478 (Lo-16bits)
6480 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6481 |  |  |  | HR6480 (Lo-16bits)
6482 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6483 |  |  |  | HR6482 (Lo-16bits)
6484 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6485 |  |  |  | HR6484 (Lo-16bits)
6486 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6487 |  |  |  | HR6486 (Lo-16bits)
6488 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6489 |  |  |  | HR6488 (Lo-16bits)
6490 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6491 |  |  |  | HR6490 (Lo-16bits)
6492 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6493 |  |  |  | HR6492 (Lo-16bits)
6494 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6495 |  |  |  | HR6494 (Lo-16bits)
6496 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6497 |  |  |  | HR6496 (Lo-16bits)
6498 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6499 |  |  |  | HR6498 (Lo-16bits)
6500 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6501 |  |  |  | HR6500 (Lo-16bits)
6502 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6503 |  |  |  | HR6502 (Lo-16bits)
6504 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6505 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6506 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6507 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6508 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6509 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6510 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6511 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6512 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6513 |  |  |  | HR6512 (Lo-16bits)
6514 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6515 |  |  |  | HR6514 (Lo-16bits)
6516 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6517 |  |  |  | HR6516 (Lo-16bits)
6518 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6519 |  |  |  | HR6518 (Lo-16bits)
6520 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6521 |  |  |  | HR6520 (Lo-16bits)
6522 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6523 |  |  |  | HR6522 (Lo-16bits)
6524 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6525 |  |  |  | HR6524 (Lo-16bits)
6526 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6527 |  |  |  | HR6526 (Lo-16bits)
6528 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6529 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6530 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6531 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6532 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6533 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6534 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6535 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6536 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6537 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6538 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6539 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6540 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6541 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6542 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6543 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6544 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6545 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6546 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6547 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6548 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6549 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6550 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6551 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6552 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6553 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6554 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6555 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6556 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6557 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6558 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6559 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6560 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6561 |  |  |  | HR6560 (Lo-16bits)
6562 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6563 |  |  |  | HR6562 (Lo-16bits)
6564 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6565 |  |  |  | HR6564 (Lo-16bits)
6566 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6567 |  |  |  | HR6566 (Lo-16bits)
6568 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6569 |  |  |  | HR6568 (Lo-16bits)
6570 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6571 |  |  |  | HR6570 (Lo-16bits)
6572 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6573 |  |  |  | HR6572 (Lo-16bits)
6574 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6575 |  |  |  | HR6574 (Lo-16bits)
6576 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6577 |  |  |  | HR6576 (Lo-16bits)
6578 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6579 |  |  |  | HR6578 (Lo-16bits)
6580 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6581 |  |  |  | HR6580 (Lo-16bits)
6582 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6583 |  |  |  | HR6582 (Lo-16bits)
6584 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6585 |  |  |  | HR6584 (Lo-16bits)
6586 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6587 |  |  |  | HR6586 (Lo-16bits)
6588 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6589 |  |  |  | HR6588 (Lo-16bits)
6590 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6591 |  |  |  | HR6590 (Lo-16bits)
6592 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6593 |  |  |  | HR6592 (Lo-16bits)
6594 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6595 |  |  |  | HR6594 (Lo-16bits)
6596 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6597 |  |  |  | HR6596 (Lo-16bits)
6598 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6599 |  |  |  | HR6598 (Lo-16bits)
6600 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6601 |  |  |  | HR6600 (Lo-16bits)
6602 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6603 |  |  |  | HR6602 (Lo-16bits)
6604 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6605 |  |  |  | HR6604 (Lo-16bits)
6606 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6607 |  |  |  | HR6606 (Lo-16bits)
6608 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6609 |  |  |  | HR6608 (Lo-16bits)
6610 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6611 |  |  |  | HR6610 (Lo-16bits)
6612 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6613 |  |  |  | HR6612 (Lo-16bits)
6614 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6615 |  |  |  | HR6614 (Lo-16bits)
6616 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6617 |  |  |  | HR6616 (Lo-16bits)
6618 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6619 |  |  |  | HR6618 (Lo-16bits)
6620 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6621 |  |  |  | HR6620 (Lo-16bits)
6622 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6623 |  |  |  | HR6622 (Lo-16bits)
6624 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6625 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6626 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6627 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6628 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6629 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6630 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6631 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6632 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6633 |  |  |  | HR6632 (Lo-16bits)
6634 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6635 |  |  |  | HR6634 (Lo-16bits)
6636 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6637 |  |  |  | HR6636 (Lo-16bits)
6638 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6639 |  |  |  | HR6638 (Lo-16bits)
6640 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6641 |  |  |  | HR6640 (Lo-16bits)
6642 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6643 |  |  |  | HR6642 (Lo-16bits)
6644 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6645 |  |  |  | HR6644 (Lo-16bits)
6646 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6647 |  |  |  | HR6646 (Lo-16bits)
6648 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6649 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6650 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6651 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6652 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6653 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6654 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6655 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6656 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6657 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6658 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6659 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6660 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6661 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6662 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6663 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6664 | CUB3:I2>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6665 | CUB3:I2>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6666 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6667 |  |  |  | HR6666 (Lo-16bits)
6668 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6669 |  |  |  | HR6668 (Lo-16bits)
6670 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6671 |  |  |  | HR6670 (Lo-16bits)
6672 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6673 |  |  |  | HR6672 (Lo-16bits)
6674 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6675 |  |  |  | HR6674 (Lo-16bits)
6676 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6677 |  |  |  | HR6676 (Lo-16bits)
6678 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6679 |  |  |  | HR6678 (Lo-16bits)
6680 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6681 |  |  |  | HR6680 (Lo-16bits)
6682 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6683 |  |  |  | HR6682 (Lo-16bits)
6684 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6685 |  |  |  | HR6684 (Lo-16bits)
6686 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6687 |  |  |  | HR6686 (Lo-16bits)
6688 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6689 |  |  |  | HR6688 (Lo-16bits)
6690 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6691 |  |  |  | HR6690 (Lo-16bits)
6692 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6693 |  |  |  | HR6692 (Lo-16bits)
6694 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6695 |  |  |  | HR6694 (Lo-16bits)
6696 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6697 |  |  |  | HR6696 (Lo-16bits)
6698 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6699 |  |  |  | HR6698 (Lo-16bits)
6700 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6701 |  |  |  | HR6700 (Lo-16bits)
6702 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6703 |  |  |  | HR6702 (Lo-16bits)
6704 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6705 |  |  |  | HR6704 (Lo-16bits)
6706 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6707 |  |  |  | HR6706 (Lo-16bits)
6708 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6709 |  |  |  | HR6708 (Lo-16bits)
6710 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6711 |  |  |  | HR6710 (Lo-16bits)
6712 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6713 |  |  |  | HR6712 (Lo-16bits)
6714 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6715 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6716 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6717 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6718 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6719 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6720 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6721 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6722 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6723 |  |  |  | HR6722 (Lo-16bits)
6724 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6725 |  |  |  | HR6724 (Lo-16bits)
6726 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6727 |  |  |  | HR6726 (Lo-16bits)
6728 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6729 |  |  |  | HR6728 (Lo-16bits)
6730 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6731 |  |  |  | HR6730 (Lo-16bits)
6732 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6733 |  |  |  | HR6732 (Lo-16bits)
6734 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6735 |  |  |  | HR6734 (Lo-16bits)
6736 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6737 |  |  |  | HR6736 (Lo-16bits)
6738 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6739 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6740 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6741 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6742 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6743 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6744 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6745 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6746 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6747 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6748 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6749 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6750 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6751 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6752 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6753 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6754 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6755 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6756 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6757 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6758 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6759 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6760 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6761 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6762 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6763 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6764 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6765 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6766 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6767 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6768 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6769 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6770 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6771 |  |  |  | HR6770 (Lo-16bits)
6772 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6773 |  |  |  | HR6772 (Lo-16bits)
6774 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6775 |  |  |  | HR6774 (Lo-16bits)
6776 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6777 |  |  |  | HR6776 (Lo-16bits)
6778 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6779 |  |  |  | HR6778 (Lo-16bits)
6780 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6781 |  |  |  | HR6780 (Lo-16bits)
6782 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6783 |  |  |  | HR6782 (Lo-16bits)
6784 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6785 |  |  |  | HR6784 (Lo-16bits)
6786 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6787 |  |  |  | HR6786 (Lo-16bits)
6788 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6789 |  |  |  | HR6788 (Lo-16bits)
6790 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6791 |  |  |  | HR6790 (Lo-16bits)
6792 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6793 |  |  |  | HR6792 (Lo-16bits)
6794 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6795 |  |  |  | HR6794 (Lo-16bits)
6796 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6797 |  |  |  | HR6796 (Lo-16bits)
6798 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6799 |  |  |  | HR6798 (Lo-16bits)
6800 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6801 |  |  |  | HR6800 (Lo-16bits)
6802 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6803 |  |  |  | HR6802 (Lo-16bits)
6804 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6805 |  |  |  | HR6804 (Lo-16bits)
6806 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6807 |  |  |  | HR6806 (Lo-16bits)
6808 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6809 |  |  |  | HR6808 (Lo-16bits)
6810 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6811 |  |  |  | HR6810 (Lo-16bits)
6812 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6813 |  |  |  | HR6812 (Lo-16bits)
6814 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6815 |  |  |  | HR6814 (Lo-16bits)
6816 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6817 |  |  |  | HR6816 (Lo-16bits)
6818 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6819 |  |  |  | HR6818 (Lo-16bits)
6820 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6821 |  |  |  | HR6820 (Lo-16bits)
6822 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6823 |  |  |  | HR6822 (Lo-16bits)
6824 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6825 |  |  |  | HR6824 (Lo-16bits)
6826 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6827 |  |  |  | HR6826 (Lo-16bits)
6828 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6829 |  |  |  | HR6828 (Lo-16bits)
6830 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6831 |  |  |  | HR6830 (Lo-16bits)
6832 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6833 |  |  |  | HR6832 (Lo-16bits)
6834 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6835 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6836 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6837 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6838 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6839 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6840 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6841 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6842 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6843 |  |  |  | HR6842 (Lo-16bits)
6844 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6845 |  |  |  | HR6844 (Lo-16bits)
6846 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6847 |  |  |  | HR6846 (Lo-16bits)
6848 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6849 |  |  |  | HR6848 (Lo-16bits)
6850 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6851 |  |  |  | HR6850 (Lo-16bits)
6852 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6853 |  |  |  | HR6852 (Lo-16bits)
6854 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6855 |  |  |  | HR6854 (Lo-16bits)
6856 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6857 |  |  |  | HR6856 (Lo-16bits)
6858 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6859 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6860 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6861 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6862 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6863 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6864 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6865 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6866 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6867 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6868 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6869 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6870 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6871 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6872 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6873 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6874 | CUB4:I2>>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6875 | CUB4:I2>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6876 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6877 |  |  |  | HR6876 (Lo-16bits)
6878 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6879 |  |  |  | HR6878 (Lo-16bits)
6880 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6881 |  |  |  | HR6880 (Lo-16bits)
6882 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6883 |  |  |  | HR6882 (Lo-16bits)
6884 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6885 |  |  |  | HR6884 (Lo-16bits)
6886 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6887 |  |  |  | HR6886 (Lo-16bits)
6888 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6889 |  |  |  | HR6888 (Lo-16bits)
6890 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6891 |  |  |  | HR6890 (Lo-16bits)
6892 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6893 |  |  |  | HR6892 (Lo-16bits)
6894 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6895 |  |  |  | HR6894 (Lo-16bits)
6896 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6897 |  |  |  | HR6896 (Lo-16bits)
6898 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6899 |  |  |  | HR6898 (Lo-16bits)
6900 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6901 |  |  |  | HR6900 (Lo-16bits)
6902 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6903 |  |  |  | HR6902 (Lo-16bits)
6904 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6905 |  |  |  | HR6904 (Lo-16bits)
6906 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6907 |  |  |  | HR6906 (Lo-16bits)
6908 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6909 |  |  |  | HR6908 (Lo-16bits)
6910 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6911 |  |  |  | HR6910 (Lo-16bits)
6912 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6913 |  |  |  | HR6912 (Lo-16bits)
6914 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6915 |  |  |  | HR6914 (Lo-16bits)
6916 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6917 |  |  |  | HR6916 (Lo-16bits)
6918 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6919 |  |  |  | HR6918 (Lo-16bits)
6920 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6921 |  |  |  | HR6920 (Lo-16bits)
6922 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6923 |  |  |  | HR6922 (Lo-16bits)
6924 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6925 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6926 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6927 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6928 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6929 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6930 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6931 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6932 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6933 |  |  |  | HR6932 (Lo-16bits)
6934 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6935 |  |  |  | HR6934 (Lo-16bits)
6936 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6937 |  |  |  | HR6936 (Lo-16bits)
6938 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6939 |  |  |  | HR6938 (Lo-16bits)
6940 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6941 |  |  |  | HR6940 (Lo-16bits)
6942 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6943 |  |  |  | HR6942 (Lo-16bits)
6944 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6945 |  |  |  | HR6944 (Lo-16bits)
6946 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6947 |  |  |  | HR6946 (Lo-16bits)
6948 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6949 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6950 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6951 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6952 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6953 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6954 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6955 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6956 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6957 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6958 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6959 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6960 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6961 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6962 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6963 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6964 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6965 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6966 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6967 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6968 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6969 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6970 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6971 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6972 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6973 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6974 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6975 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6976 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6977 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6978 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6979 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6980 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6981 |  |  |  | HR6980 (Lo-16bits)
6982 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6983 |  |  |  | HR6982 (Lo-16bits)
6984 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6985 |  |  |  | HR6984 (Lo-16bits)
6986 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6987 |  |  |  | HR6986 (Lo-16bits)
6988 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6989 |  |  |  | HR6988 (Lo-16bits)
6990 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6991 |  |  |  | HR6990 (Lo-16bits)
6992 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6993 |  |  |  | HR6992 (Lo-16bits)
6994 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6995 |  |  |  | HR6994 (Lo-16bits)
6996 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6997 |  |  |  | HR6996 (Lo-16bits)
6998 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6999 |  |  |  | HR6998 (Lo-16bits)
7000 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7001 |  |  |  | HR7000 (Lo-16bits)
7002 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7003 |  |  |  | HR7002 (Lo-16bits)
7004 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7005 |  |  |  | HR7004 (Lo-16bits)
7006 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7007 |  |  |  | HR7006 (Lo-16bits)
7008 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7009 |  |  |  | HR7008 (Lo-16bits)
7010 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7011 |  |  |  | HR7010 (Lo-16bits)
7012 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7013 |  |  |  | HR7012 (Lo-16bits)
7014 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7015 |  |  |  | HR7014 (Lo-16bits)
7016 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7017 |  |  |  | HR7016 (Lo-16bits)
7018 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7019 |  |  |  | HR7018 (Lo-16bits)
7020 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7021 |  |  |  | HR7020 (Lo-16bits)
7022 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7023 |  |  |  | HR7022 (Lo-16bits)
7024 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7025 |  |  |  | HR7024 (Lo-16bits)
7026 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7027 |  |  |  | HR7026 (Lo-16bits)
7028 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7029 |  |  |  | HR7028 (Lo-16bits)
7030 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7031 |  |  |  | HR7030 (Lo-16bits)
7032 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7033 |  |  |  | HR7032 (Lo-16bits)
7034 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7035 |  |  |  | HR7034 (Lo-16bits)
7036 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7037 |  |  |  | HR7036 (Lo-16bits)
7038 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7039 |  |  |  | HR7038 (Lo-16bits)
7040 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7041 |  |  |  | HR7040 (Lo-16bits)
7042 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7043 |  |  |  | HR7042 (Lo-16bits)
7044 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7045 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7046 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7047 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7048 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7049 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7050 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7051 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7052 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7053 |  |  |  | HR7052 (Lo-16bits)
7054 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7055 |  |  |  | HR7054 (Lo-16bits)
7056 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7057 |  |  |  | HR7056 (Lo-16bits)
7058 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7059 |  |  |  | HR7058 (Lo-16bits)
7060 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7061 |  |  |  | HR7060 (Lo-16bits)
7062 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7063 |  |  |  | HR7062 (Lo-16bits)
7064 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7065 |  |  |  | HR7064 (Lo-16bits)
7066 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7067 |  |  |  | HR7066 (Lo-16bits)
7068 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7069 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7070 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7071 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7072 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7073 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7074 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7075 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7076 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7077 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7078 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7079 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7080 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7081 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7082 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7083 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7084 | HOC1:Ih> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7085 | HOC1:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7086 |  |  |  | HR7085 (Lo-16bits)
7087 | HOC1:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7088 |  |  |  | HR7087 (Lo-16bits)
7089 | HOC1:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7090 |  |  |  | HR7089 (Lo-16bits)
7091 | HOC1:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7092 |  |  |  | HR7091 (Lo-16bits)
7093 | HOC1:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7094 |  |  |  | HR7093 (Lo-16bits)
7095 | HOC1:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7096 |  |  |  | HR7095 (Lo-16bits)
7097 | HOC1:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7098 |  |  |  | HR7097 (Lo-16bits)
7099 | HOC1:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7100 |  |  |  | HR7099 (Lo-16bits)
7101 | HOC1:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7102 |  |  |  | HR7101 (Lo-16bits)
7103 | HOC1:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7104 |  |  |  | HR7103 (Lo-16bits)
7105 | HOC2:Ih>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7106 | HOC2:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7107 |  |  |  | HR7106 (Lo-16bits)
7108 | HOC2:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7109 |  |  |  | HR7108 (Lo-16bits)
7110 | HOC2:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7111 |  |  |  | HR7110 (Lo-16bits)
7112 | HOC2:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7113 |  |  |  | HR7112 (Lo-16bits)
7114 | HOC2:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7115 |  |  |  | HR7114 (Lo-16bits)
7116 | HOC2:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7117 |  |  |  | HR7116 (Lo-16bits)
7118 | HOC2:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7119 |  |  |  | HR7118 (Lo-16bits)
7120 | HOC2:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7121 |  |  |  | HR7120 (Lo-16bits)
7122 | HOC2:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7123 |  |  |  | HR7122 (Lo-16bits)
7124 | HOC2:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7125 |  |  |  | HR7124 (Lo-16bits)
7126 | HOC3:Ih>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7127 | HOC3:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7128 |  |  |  | HR7127 (Lo-16bits)
7129 | HOC3:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7130 |  |  |  | HR7129 (Lo-16bits)
7131 | HOC3:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7132 |  |  |  | HR7131 (Lo-16bits)
7133 | HOC3:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7134 |  |  |  | HR7133 (Lo-16bits)
7135 | HOC3:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7136 |  |  |  | HR7135 (Lo-16bits)
7137 | HOC3:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7138 |  |  |  | HR7137 (Lo-16bits)
7139 | HOC3:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7140 |  |  |  | HR7139 (Lo-16bits)
7141 | HOC3:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7142 |  |  |  | HR7141 (Lo-16bits)
7143 | HOC3:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7144 |  |  |  | HR7143 (Lo-16bits)
7145 | HOC3:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7146 |  |  |  | HR7145 (Lo-16bits)
7147 | HOC4:Ih>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7148 | HOC4:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7149 |  |  |  | HR7148 (Lo-16bits)
7150 | HOC4:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7151 |  |  |  | HR7150 (Lo-16bits)
7152 | HOC4:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7153 |  |  |  | HR7152 (Lo-16bits)
7154 | HOC4:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7155 |  |  |  | HR7154 (Lo-16bits)
7156 | HOC4:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7157 |  |  |  | HR7156 (Lo-16bits)
7158 | HOC4:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7159 |  |  |  | HR7158 (Lo-16bits)
7160 | HOC4:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7161 |  |  |  | HR7160 (Lo-16bits)
7162 | HOC4:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7163 |  |  |  | HR7162 (Lo-16bits)
7164 | HOC4:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7165 |  |  |  | HR7164 (Lo-16bits)
7166 | HOC4:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7167 |  |  |  | HR7166 (Lo-16bits)
7168 | CLP1:CLP condition | R | 1 | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
7169 | CBF1:CBFP condition | R | 1 | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
7170 | MST1:Motor is now | R | 1 | 0=Stopped;1=Starting;2=Running;3=Stalled
7171 | TRF1:Transformer is now | R | 1 | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
7172 | DIF1:Idx> condition | R | 2 | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On (Hi-16bits)
7173 |  |  |  | HR7172 (Lo-16bits)
7174 | DIF1:REFHV> condition | R | 2 | 0b=HV REF Blocked;1b=HV REF Trip (Hi-16bits)
7175 |  |  |  | HR7174 (Lo-16bits)
7176 | DIF1:REFLV> condition | R | 2 | 0b=LV REF Blocked;1b=LV REF Trip (Hi-16bits)
7177 |  |  |  | HR7176 (Lo-16bits)
7178 | DIF1:L1 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7179 | DIF1:L2 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7180 | DIF1:L3 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7181 | REF1:I0d> condition | R | 1 | 0=Normal;1=Trip;2=Blocked
7182 | TOLT1:TT> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7183 | TOLT1:TT> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7184 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7185 | TOLT1:TT> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7186 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7187 | TOLT1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7188 | TOLT1:Temp C or F deg | RW | 1 | 0=C;1=F
7189 | TOLT1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7190 | TOLT1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7191 | TOLT1:TT> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7192 |  |  |  | HR7191 (Lo-16bits)
7193 | TOLF1:TF> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7194 | TOLF1:TF> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7195 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7196 | TOLF1:TF> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7197 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7198 | TOLF1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7199 | TOLF1:Temp C or F deg | RW | 1 | 0=C;1=F
7200 | TOLF1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7201 | TOLF1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7202 | TOLF1:Set or Estimate tau (t const) | RW | 1 | 0=Set;1=Estimate
7203 | TOLF1:TF> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7204 |  |  |  | HR7203 (Lo-16bits)
7205 | TOLM1:TM> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7206 | TOLM1:TM> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7207 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7208 | TOLM1:TM> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7209 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7210 | TOLM1:Motor status | R | 1 | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
7211 | TOLM1:Temp C or F deg | RW | 1 | 0=C;1=F
7212 | TOLM1:NPS Biasing in use | RW | 1 | 0=No NPS biasing;1=NPS Biasing in use
7213 | TOLM1:Time constants | RW | 1 | 0=Single;1=Multiple
7214 | TOLM1:Estimate Short TC and timings | RW | 1 | 0=Set manually;1=Estimate (on-line)
7215 | TOLM1:T const dyn. balancing | RW | 1 | 0=Fixed;1=Dynamic
7216 | TOLM1:Dev.Temp (tmax) | RW | 1 | 0=A;1=B;2=F;3=H;4=Manual set
7217 | TOLM1:Amb. T Selection | RW | 1 | 0=Manual set;1=RTD
7218 | TOLM1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7219 | TOLM1:TM> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7220 |  |  |  | HR7219 (Lo-16bits)
7221 | LCR1:ISt> condition | R | 1 | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
7222 | FSP1:N> condition | R | 1 | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
7223 | NUC1:I< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7224 | MJP1:Im> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7225 | OV1:U> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7226 | OV1:U> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7227 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7228 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7229 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7230 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7231 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7232 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7233 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7234 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7235 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7236 |  |  |  | HR7235 (Lo-16bits)
7237 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7238 |  |  |  | HR7237 (Lo-16bits)
7239 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7240 |  |  |  | HR7239 (Lo-16bits)
7241 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7242 |  |  |  | HR7241 (Lo-16bits)
7243 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7244 |  |  |  | HR7243 (Lo-16bits)
7245 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7246 |  |  |  | HR7245 (Lo-16bits)
7247 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7248 |  |  |  | HR7247 (Lo-16bits)
7249 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7250 |  |  |  | HR7249 (Lo-16bits)
7251 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7252 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7253 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7254 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7255 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7256 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7257 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7258 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7259 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7260 |  |  |  | HR7259 (Lo-16bits)
7261 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7262 |  |  |  | HR7261 (Lo-16bits)
7263 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7264 |  |  |  | HR7263 (Lo-16bits)
7265 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7266 |  |  |  | HR7265 (Lo-16bits)
7267 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7268 |  |  |  | HR7267 (Lo-16bits)
7269 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7270 |  |  |  | HR7269 (Lo-16bits)
7271 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7272 |  |  |  | HR7271 (Lo-16bits)
7273 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7274 |  |  |  | HR7273 (Lo-16bits)
7275 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7276 |  |  |  | HR7275 (Lo-16bits)
7277 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7278 |  |  |  | HR7277 (Lo-16bits)
7279 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7280 |  |  |  | HR7279 (Lo-16bits)
7281 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7282 |  |  |  | HR7281 (Lo-16bits)
7283 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7284 |  |  |  | HR7283 (Lo-16bits)
7285 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7286 |  |  |  | HR7285 (Lo-16bits)
7287 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7288 |  |  |  | HR7287 (Lo-16bits)
7289 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7290 |  |  |  | HR7289 (Lo-16bits)
7291 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7292 |  |  |  | HR7291 (Lo-16bits)
7293 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7294 |  |  |  | HR7293 (Lo-16bits)
7295 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7296 |  |  |  | HR7295 (Lo-16bits)
7297 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7298 |  |  |  | HR7297 (Lo-16bits)
7299 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7300 |  |  |  | HR7299 (Lo-16bits)
7301 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7302 |  |  |  | HR7301 (Lo-16bits)
7303 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7304 |  |  |  | HR7303 (Lo-16bits)
7305 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7306 |  |  |  | HR7305 (Lo-16bits)
7307 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7308 |  |  |  | HR7307 (Lo-16bits)
7309 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7310 |  |  |  | HR7309 (Lo-16bits)
7311 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7312 |  |  |  | HR7311 (Lo-16bits)
7313 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7314 |  |  |  | HR7313 (Lo-16bits)
7315 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7316 |  |  |  | HR7315 (Lo-16bits)
7317 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7318 |  |  |  | HR7317 (Lo-16bits)
7319 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7320 |  |  |  | HR7319 (Lo-16bits)
7321 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7322 |  |  |  | HR7321 (Lo-16bits)
7323 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7324 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7325 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7326 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7327 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7328 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7329 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7330 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7331 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7332 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7333 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7334 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7335 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7336 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7337 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7338 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7339 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7340 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7341 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7342 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7343 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7344 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7345 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7346 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7347 | OV2:U>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7348 | OV2:U>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7349 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7350 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7351 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7352 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7353 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7354 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7355 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7356 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7357 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7358 |  |  |  | HR7357 (Lo-16bits)
7359 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7360 |  |  |  | HR7359 (Lo-16bits)
7361 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7362 |  |  |  | HR7361 (Lo-16bits)
7363 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7364 |  |  |  | HR7363 (Lo-16bits)
7365 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7366 |  |  |  | HR7365 (Lo-16bits)
7367 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7368 |  |  |  | HR7367 (Lo-16bits)
7369 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7370 |  |  |  | HR7369 (Lo-16bits)
7371 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7372 |  |  |  | HR7371 (Lo-16bits)
7373 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7374 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7375 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7376 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7377 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7378 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7379 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7380 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7381 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7382 |  |  |  | HR7381 (Lo-16bits)
7383 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7384 |  |  |  | HR7383 (Lo-16bits)
7385 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7386 |  |  |  | HR7385 (Lo-16bits)
7387 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7388 |  |  |  | HR7387 (Lo-16bits)
7389 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7390 |  |  |  | HR7389 (Lo-16bits)
7391 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7392 |  |  |  | HR7391 (Lo-16bits)
7393 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7394 |  |  |  | HR7393 (Lo-16bits)
7395 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7396 |  |  |  | HR7395 (Lo-16bits)
7397 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7398 |  |  |  | HR7397 (Lo-16bits)
7399 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7400 |  |  |  | HR7399 (Lo-16bits)
7401 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7402 |  |  |  | HR7401 (Lo-16bits)
7403 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7404 |  |  |  | HR7403 (Lo-16bits)
7405 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7406 |  |  |  | HR7405 (Lo-16bits)
7407 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7408 |  |  |  | HR7407 (Lo-16bits)
7409 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7410 |  |  |  | HR7409 (Lo-16bits)
7411 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7412 |  |  |  | HR7411 (Lo-16bits)
7413 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7414 |  |  |  | HR7413 (Lo-16bits)
7415 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7416 |  |  |  | HR7415 (Lo-16bits)
7417 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7418 |  |  |  | HR7417 (Lo-16bits)
7419 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7420 |  |  |  | HR7419 (Lo-16bits)
7421 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7422 |  |  |  | HR7421 (Lo-16bits)
7423 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7424 |  |  |  | HR7423 (Lo-16bits)
7425 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7426 |  |  |  | HR7425 (Lo-16bits)
7427 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7428 |  |  |  | HR7427 (Lo-16bits)
7429 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7430 |  |  |  | HR7429 (Lo-16bits)
7431 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7432 |  |  |  | HR7431 (Lo-16bits)
7433 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7434 |  |  |  | HR7433 (Lo-16bits)
7435 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7436 |  |  |  | HR7435 (Lo-16bits)
7437 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7438 |  |  |  | HR7437 (Lo-16bits)
7439 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7440 |  |  |  | HR7439 (Lo-16bits)
7441 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7442 |  |  |  | HR7441 (Lo-16bits)
7443 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7444 |  |  |  | HR7443 (Lo-16bits)
7445 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7446 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7447 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7448 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7449 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7450 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7451 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7452 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7453 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7454 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7455 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7456 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7457 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7458 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7459 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7460 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7461 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7462 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7463 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7464 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7465 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7466 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7467 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7468 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7469 | OV3:U>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7470 | OV3:U>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7471 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7472 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7473 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7474 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7475 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7476 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7477 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7478 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7479 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7480 |  |  |  | HR7479 (Lo-16bits)
7481 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7482 |  |  |  | HR7481 (Lo-16bits)
7483 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7484 |  |  |  | HR7483 (Lo-16bits)
7485 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7486 |  |  |  | HR7485 (Lo-16bits)
7487 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7488 |  |  |  | HR7487 (Lo-16bits)
7489 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7490 |  |  |  | HR7489 (Lo-16bits)
7491 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7492 |  |  |  | HR7491 (Lo-16bits)
7493 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7494 |  |  |  | HR7493 (Lo-16bits)
7495 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7496 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7497 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7498 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7499 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7500 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7501 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7502 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7503 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7504 |  |  |  | HR7503 (Lo-16bits)
7505 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7506 |  |  |  | HR7505 (Lo-16bits)
7507 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7508 |  |  |  | HR7507 (Lo-16bits)
7509 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7510 |  |  |  | HR7509 (Lo-16bits)
7511 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7512 |  |  |  | HR7511 (Lo-16bits)
7513 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7514 |  |  |  | HR7513 (Lo-16bits)
7515 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7516 |  |  |  | HR7515 (Lo-16bits)
7517 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7518 |  |  |  | HR7517 (Lo-16bits)
7519 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7520 |  |  |  | HR7519 (Lo-16bits)
7521 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7522 |  |  |  | HR7521 (Lo-16bits)
7523 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7524 |  |  |  | HR7523 (Lo-16bits)
7525 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7526 |  |  |  | HR7525 (Lo-16bits)
7527 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7528 |  |  |  | HR7527 (Lo-16bits)
7529 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7530 |  |  |  | HR7529 (Lo-16bits)
7531 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7532 |  |  |  | HR7531 (Lo-16bits)
7533 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7534 |  |  |  | HR7533 (Lo-16bits)
7535 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7536 |  |  |  | HR7535 (Lo-16bits)
7537 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7538 |  |  |  | HR7537 (Lo-16bits)
7539 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7540 |  |  |  | HR7539 (Lo-16bits)
7541 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7542 |  |  |  | HR7541 (Lo-16bits)
7543 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7544 |  |  |  | HR7543 (Lo-16bits)
7545 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7546 |  |  |  | HR7545 (Lo-16bits)
7547 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7548 |  |  |  | HR7547 (Lo-16bits)
7549 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7550 |  |  |  | HR7549 (Lo-16bits)
7551 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7552 |  |  |  | HR7551 (Lo-16bits)
7553 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7554 |  |  |  | HR7553 (Lo-16bits)
7555 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7556 |  |  |  | HR7555 (Lo-16bits)
7557 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7558 |  |  |  | HR7557 (Lo-16bits)
7559 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7560 |  |  |  | HR7559 (Lo-16bits)
7561 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7562 |  |  |  | HR7561 (Lo-16bits)
7563 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7564 |  |  |  | HR7563 (Lo-16bits)
7565 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7566 |  |  |  | HR7565 (Lo-16bits)
7567 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7568 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7569 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7570 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7571 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7572 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7573 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7574 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7575 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7576 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7577 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7578 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7579 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7580 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7581 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7582 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7583 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7584 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7585 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7586 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7587 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7588 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7589 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7590 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7591 | OV4:U>>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7592 | OV4:U>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7593 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7594 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7595 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7596 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7597 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7598 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7599 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7600 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7601 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7602 |  |  |  | HR7601 (Lo-16bits)
7603 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7604 |  |  |  | HR7603 (Lo-16bits)
7605 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7606 |  |  |  | HR7605 (Lo-16bits)
7607 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7608 |  |  |  | HR7607 (Lo-16bits)
7609 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7610 |  |  |  | HR7609 (Lo-16bits)
7611 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7612 |  |  |  | HR7611 (Lo-16bits)
7613 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7614 |  |  |  | HR7613 (Lo-16bits)
7615 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7616 |  |  |  | HR7615 (Lo-16bits)
7617 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7618 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7619 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7620 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7621 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7622 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7623 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7624 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7625 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7626 |  |  |  | HR7625 (Lo-16bits)
7627 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7628 |  |  |  | HR7627 (Lo-16bits)
7629 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7630 |  |  |  | HR7629 (Lo-16bits)
7631 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7632 |  |  |  | HR7631 (Lo-16bits)
7633 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7634 |  |  |  | HR7633 (Lo-16bits)
7635 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7636 |  |  |  | HR7635 (Lo-16bits)
7637 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7638 |  |  |  | HR7637 (Lo-16bits)
7639 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7640 |  |  |  | HR7639 (Lo-16bits)
7641 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7642 |  |  |  | HR7641 (Lo-16bits)
7643 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7644 |  |  |  | HR7643 (Lo-16bits)
7645 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7646 |  |  |  | HR7645 (Lo-16bits)
7647 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7648 |  |  |  | HR7647 (Lo-16bits)
7649 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7650 |  |  |  | HR7649 (Lo-16bits)
7651 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7652 |  |  |  | HR7651 (Lo-16bits)
7653 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7654 |  |  |  | HR7653 (Lo-16bits)
7655 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7656 |  |  |  | HR7655 (Lo-16bits)
7657 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7658 |  |  |  | HR7657 (Lo-16bits)
7659 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7660 |  |  |  | HR7659 (Lo-16bits)
7661 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7662 |  |  |  | HR7661 (Lo-16bits)
7663 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7664 |  |  |  | HR7663 (Lo-16bits)
7665 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7666 |  |  |  | HR7665 (Lo-16bits)
7667 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7668 |  |  |  | HR7667 (Lo-16bits)
7669 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7670 |  |  |  | HR7669 (Lo-16bits)
7671 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7672 |  |  |  | HR7671 (Lo-16bits)
7673 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7674 |  |  |  | HR7673 (Lo-16bits)
7675 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7676 |  |  |  | HR7675 (Lo-16bits)
7677 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7678 |  |  |  | HR7677 (Lo-16bits)
7679 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7680 |  |  |  | HR7679 (Lo-16bits)
7681 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7682 |  |  |  | HR7681 (Lo-16bits)
7683 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7684 |  |  |  | HR7683 (Lo-16bits)
7685 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7686 |  |  |  | HR7685 (Lo-16bits)
7687 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7688 |  |  |  | HR7687 (Lo-16bits)
7689 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7690 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7691 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7692 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7693 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7694 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7695 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7696 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7697 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7698 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7699 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7700 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7701 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7702 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7703 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7704 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7705 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7706 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7707 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7708 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7709 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7710 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7711 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7712 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7713 | UV1:U< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7714 | UV1:U< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7715 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7716 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7717 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7718 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7719 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7720 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7721 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7722 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7723 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7724 |  |  |  | HR7723 (Lo-16bits)
7725 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7726 |  |  |  | HR7725 (Lo-16bits)
7727 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7728 |  |  |  | HR7727 (Lo-16bits)
7729 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7730 |  |  |  | HR7729 (Lo-16bits)
7731 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7732 |  |  |  | HR7731 (Lo-16bits)
7733 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7734 |  |  |  | HR7733 (Lo-16bits)
7735 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7736 |  |  |  | HR7735 (Lo-16bits)
7737 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7738 |  |  |  | HR7737 (Lo-16bits)
7739 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7740 |  |  |  | HR7739 (Lo-16bits)
7741 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7742 |  |  |  | HR7741 (Lo-16bits)
7743 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7744 |  |  |  | HR7743 (Lo-16bits)
7745 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7746 |  |  |  | HR7745 (Lo-16bits)
7747 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7748 |  |  |  | HR7747 (Lo-16bits)
7749 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7750 |  |  |  | HR7749 (Lo-16bits)
7751 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7752 |  |  |  | HR7751 (Lo-16bits)
7753 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7754 |  |  |  | HR7753 (Lo-16bits)
7755 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7756 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7757 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7758 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7759 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7760 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7761 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7762 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7763 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7764 |  |  |  | HR7763 (Lo-16bits)
7765 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7766 |  |  |  | HR7765 (Lo-16bits)
7767 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7768 |  |  |  | HR7767 (Lo-16bits)
7769 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7770 |  |  |  | HR7769 (Lo-16bits)
7771 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7772 |  |  |  | HR7771 (Lo-16bits)
7773 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7774 |  |  |  | HR7773 (Lo-16bits)
7775 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7776 |  |  |  | HR7775 (Lo-16bits)
7777 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7778 |  |  |  | HR7777 (Lo-16bits)
7779 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7780 |  |  |  | HR7779 (Lo-16bits)
7781 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7782 |  |  |  | HR7781 (Lo-16bits)
7783 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7784 |  |  |  | HR7783 (Lo-16bits)
7785 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7786 |  |  |  | HR7785 (Lo-16bits)
7787 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7788 |  |  |  | HR7787 (Lo-16bits)
7789 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7790 |  |  |  | HR7789 (Lo-16bits)
7791 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7792 |  |  |  | HR7791 (Lo-16bits)
7793 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7794 |  |  |  | HR7793 (Lo-16bits)
7795 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7796 |  |  |  | HR7795 (Lo-16bits)
7797 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7798 |  |  |  | HR7797 (Lo-16bits)
7799 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7800 |  |  |  | HR7799 (Lo-16bits)
7801 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7802 |  |  |  | HR7801 (Lo-16bits)
7803 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7804 |  |  |  | HR7803 (Lo-16bits)
7805 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7806 |  |  |  | HR7805 (Lo-16bits)
7807 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7808 |  |  |  | HR7807 (Lo-16bits)
7809 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7810 |  |  |  | HR7809 (Lo-16bits)
7811 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7812 |  |  |  | HR7811 (Lo-16bits)
7813 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7814 |  |  |  | HR7813 (Lo-16bits)
7815 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7816 |  |  |  | HR7815 (Lo-16bits)
7817 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7818 |  |  |  | HR7817 (Lo-16bits)
7819 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7820 |  |  |  | HR7819 (Lo-16bits)
7821 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7822 |  |  |  | HR7821 (Lo-16bits)
7823 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7824 |  |  |  | HR7823 (Lo-16bits)
7825 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7826 |  |  |  | HR7825 (Lo-16bits)
7827 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7828 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7829 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7830 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7831 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7832 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7833 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7834 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7835 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7836 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7837 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7838 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7839 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7840 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7841 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7842 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7843 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7844 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7845 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7846 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7847 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7848 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7849 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7850 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7851 | UV2:U<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7852 | UV2:U<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7853 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7854 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7855 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7856 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7857 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7858 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7859 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7860 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7861 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7862 |  |  |  | HR7861 (Lo-16bits)
7863 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7864 |  |  |  | HR7863 (Lo-16bits)
7865 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7866 |  |  |  | HR7865 (Lo-16bits)
7867 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7868 |  |  |  | HR7867 (Lo-16bits)
7869 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7870 |  |  |  | HR7869 (Lo-16bits)
7871 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7872 |  |  |  | HR7871 (Lo-16bits)
7873 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7874 |  |  |  | HR7873 (Lo-16bits)
7875 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7876 |  |  |  | HR7875 (Lo-16bits)
7877 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7878 |  |  |  | HR7877 (Lo-16bits)
7879 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7880 |  |  |  | HR7879 (Lo-16bits)
7881 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7882 |  |  |  | HR7881 (Lo-16bits)
7883 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7884 |  |  |  | HR7883 (Lo-16bits)
7885 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7886 |  |  |  | HR7885 (Lo-16bits)
7887 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7888 |  |  |  | HR7887 (Lo-16bits)
7889 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7890 |  |  |  | HR7889 (Lo-16bits)
7891 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7892 |  |  |  | HR7891 (Lo-16bits)
7893 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7894 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7895 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7896 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7897 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7898 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7899 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7900 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7901 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7902 |  |  |  | HR7901 (Lo-16bits)
7903 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7904 |  |  |  | HR7903 (Lo-16bits)
7905 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7906 |  |  |  | HR7905 (Lo-16bits)
7907 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7908 |  |  |  | HR7907 (Lo-16bits)
7909 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7910 |  |  |  | HR7909 (Lo-16bits)
7911 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7912 |  |  |  | HR7911 (Lo-16bits)
7913 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7914 |  |  |  | HR7913 (Lo-16bits)
7915 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7916 |  |  |  | HR7915 (Lo-16bits)
7917 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7918 |  |  |  | HR7917 (Lo-16bits)
7919 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7920 |  |  |  | HR7919 (Lo-16bits)
7921 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7922 |  |  |  | HR7921 (Lo-16bits)
7923 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7924 |  |  |  | HR7923 (Lo-16bits)
7925 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7926 |  |  |  | HR7925 (Lo-16bits)
7927 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7928 |  |  |  | HR7927 (Lo-16bits)
7929 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7930 |  |  |  | HR7929 (Lo-16bits)
7931 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7932 |  |  |  | HR7931 (Lo-16bits)
7933 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7934 |  |  |  | HR7933 (Lo-16bits)
7935 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7936 |  |  |  | HR7935 (Lo-16bits)
7937 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7938 |  |  |  | HR7937 (Lo-16bits)
7939 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7940 |  |  |  | HR7939 (Lo-16bits)
7941 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7942 |  |  |  | HR7941 (Lo-16bits)
7943 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7944 |  |  |  | HR7943 (Lo-16bits)
7945 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7946 |  |  |  | HR7945 (Lo-16bits)
7947 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7948 |  |  |  | HR7947 (Lo-16bits)
7949 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7950 |  |  |  | HR7949 (Lo-16bits)
7951 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7952 |  |  |  | HR7951 (Lo-16bits)
7953 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7954 |  |  |  | HR7953 (Lo-16bits)
7955 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7956 |  |  |  | HR7955 (Lo-16bits)
7957 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7958 |  |  |  | HR7957 (Lo-16bits)
7959 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7960 |  |  |  | HR7959 (Lo-16bits)
7961 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7962 |  |  |  | HR7961 (Lo-16bits)
7963 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7964 |  |  |  | HR7963 (Lo-16bits)
7965 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7966 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7967 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7968 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7969 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7970 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7971 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7972 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7973 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7974 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7975 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7976 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7977 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7978 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7979 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7980 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7981 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7982 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7983 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7984 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7985 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7986 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7987 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7988 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7989 | UV3:U<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7990 | UV3:U<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7991 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7992 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7993 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7994 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7995 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7996 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7997 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7998 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7999 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8000 |  |  |  | HR7999 (Lo-16bits)
8001 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8002 |  |  |  | HR8001 (Lo-16bits)
8003 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8004 |  |  |  | HR8003 (Lo-16bits)
8005 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8006 |  |  |  | HR8005 (Lo-16bits)
8007 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8008 |  |  |  | HR8007 (Lo-16bits)
8009 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8010 |  |  |  | HR8009 (Lo-16bits)
8011 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8012 |  |  |  | HR8011 (Lo-16bits)
8013 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8014 |  |  |  | HR8013 (Lo-16bits)
8015 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8016 |  |  |  | HR8015 (Lo-16bits)
8017 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8018 |  |  |  | HR8017 (Lo-16bits)
8019 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8020 |  |  |  | HR8019 (Lo-16bits)
8021 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8022 |  |  |  | HR8021 (Lo-16bits)
8023 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8024 |  |  |  | HR8023 (Lo-16bits)
8025 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8026 |  |  |  | HR8025 (Lo-16bits)
8027 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8028 |  |  |  | HR8027 (Lo-16bits)
8029 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8030 |  |  |  | HR8029 (Lo-16bits)
8031 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8032 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8033 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8034 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8035 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8036 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8037 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8038 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8039 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8040 |  |  |  | HR8039 (Lo-16bits)
8041 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8042 |  |  |  | HR8041 (Lo-16bits)
8043 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8044 |  |  |  | HR8043 (Lo-16bits)
8045 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8046 |  |  |  | HR8045 (Lo-16bits)
8047 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8048 |  |  |  | HR8047 (Lo-16bits)
8049 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8050 |  |  |  | HR8049 (Lo-16bits)
8051 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8052 |  |  |  | HR8051 (Lo-16bits)
8053 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8054 |  |  |  | HR8053 (Lo-16bits)
8055 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8056 |  |  |  | HR8055 (Lo-16bits)
8057 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8058 |  |  |  | HR8057 (Lo-16bits)
8059 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8060 |  |  |  | HR8059 (Lo-16bits)
8061 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8062 |  |  |  | HR8061 (Lo-16bits)
8063 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8064 |  |  |  | HR8063 (Lo-16bits)
8065 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8066 |  |  |  | HR8065 (Lo-16bits)
8067 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8068 |  |  |  | HR8067 (Lo-16bits)
8069 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8070 |  |  |  | HR8069 (Lo-16bits)
8071 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8072 |  |  |  | HR8071 (Lo-16bits)
8073 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8074 |  |  |  | HR8073 (Lo-16bits)
8075 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8076 |  |  |  | HR8075 (Lo-16bits)
8077 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8078 |  |  |  | HR8077 (Lo-16bits)
8079 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8080 |  |  |  | HR8079 (Lo-16bits)
8081 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8082 |  |  |  | HR8081 (Lo-16bits)
8083 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8084 |  |  |  | HR8083 (Lo-16bits)
8085 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8086 |  |  |  | HR8085 (Lo-16bits)
8087 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8088 |  |  |  | HR8087 (Lo-16bits)
8089 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8090 |  |  |  | HR8089 (Lo-16bits)
8091 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8092 |  |  |  | HR8091 (Lo-16bits)
8093 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8094 |  |  |  | HR8093 (Lo-16bits)
8095 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8096 |  |  |  | HR8095 (Lo-16bits)
8097 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8098 |  |  |  | HR8097 (Lo-16bits)
8099 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8100 |  |  |  | HR8099 (Lo-16bits)
8101 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8102 |  |  |  | HR8101 (Lo-16bits)
8103 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8104 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8105 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8106 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8107 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8108 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8109 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8110 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8111 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8112 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8113 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8114 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8115 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8116 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8117 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8118 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8119 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8120 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8121 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8122 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8123 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8124 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8125 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8126 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8127 | UV4:U<<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
8128 | UV4:U<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
8129 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8130 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8131 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8132 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8133 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8134 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8135 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8136 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8137 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8138 |  |  |  | HR8137 (Lo-16bits)
8139 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8140 |  |  |  | HR8139 (Lo-16bits)
8141 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8142 |  |  |  | HR8141 (Lo-16bits)
8143 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8144 |  |  |  | HR8143 (Lo-16bits)
8145 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8146 |  |  |  | HR8145 (Lo-16bits)
8147 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8148 |  |  |  | HR8147 (Lo-16bits)
8149 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8150 |  |  |  | HR8149 (Lo-16bits)
8151 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8152 |  |  |  | HR8151 (Lo-16bits)
8153 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8154 |  |  |  | HR8153 (Lo-16bits)
8155 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8156 |  |  |  | HR8155 (Lo-16bits)
8157 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8158 |  |  |  | HR8157 (Lo-16bits)
8159 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8160 |  |  |  | HR8159 (Lo-16bits)
8161 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8162 |  |  |  | HR8161 (Lo-16bits)
8163 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8164 |  |  |  | HR8163 (Lo-16bits)
8165 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8166 |  |  |  | HR8165 (Lo-16bits)
8167 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8168 |  |  |  | HR8167 (Lo-16bits)
8169 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8170 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8171 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8172 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8173 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8174 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8175 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8176 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8177 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8178 |  |  |  | HR8177 (Lo-16bits)
8179 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8180 |  |  |  | HR8179 (Lo-16bits)
8181 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8182 |  |  |  | HR8181 (Lo-16bits)
8183 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8184 |  |  |  | HR8183 (Lo-16bits)
8185 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8186 |  |  |  | HR8185 (Lo-16bits)
8187 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8188 |  |  |  | HR8187 (Lo-16bits)
8189 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8190 |  |  |  | HR8189 (Lo-16bits)
8191 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8192 |  |  |  | HR8191 (Lo-16bits)
8193 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8194 |  |  |  | HR8193 (Lo-16bits)
8195 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8196 |  |  |  | HR8195 (Lo-16bits)
8197 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8198 |  |  |  | HR8197 (Lo-16bits)
8199 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8200 |  |  |  | HR8199 (Lo-16bits)
8201 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8202 |  |  |  | HR8201 (Lo-16bits)
8203 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8204 |  |  |  | HR8203 (Lo-16bits)
8205 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8206 |  |  |  | HR8205 (Lo-16bits)
8207 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8208 |  |  |  | HR8207 (Lo-16bits)
8209 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8210 |  |  |  | HR8209 (Lo-16bits)
8211 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8212 |  |  |  | HR8211 (Lo-16bits)
8213 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8214 |  |  |  | HR8213 (Lo-16bits)
8215 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8216 |  |  |  | HR8215 (Lo-16bits)
8217 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8218 |  |  |  | HR8217 (Lo-16bits)
8219 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8220 |  |  |  | HR8219 (Lo-16bits)
8221 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8222 |  |  |  | HR8221 (Lo-16bits)
8223 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8224 |  |  |  | HR8223 (Lo-16bits)
8225 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8226 |  |  |  | HR8225 (Lo-16bits)
8227 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8228 |  |  |  | HR8227 (Lo-16bits)
8229 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8230 |  |  |  | HR8229 (Lo-16bits)
8231 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8232 |  |  |  | HR8231 (Lo-16bits)
8233 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8234 |  |  |  | HR8233 (Lo-16bits)
8235 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8236 |  |  |  | HR8235 (Lo-16bits)
8237 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8238 |  |  |  | HR8237 (Lo-16bits)
8239 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8240 |  |  |  | HR8239 (Lo-16bits)
8241 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8242 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8243 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8244 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8245 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8246 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8247 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8248 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8249 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8250 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8251 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8252 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8253 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8254 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8255 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8256 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8257 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8258 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8259 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8260 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8261 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8262 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8263 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8264 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8265 | NOV1:U0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8266 | NOV1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8267 | NOV2:U0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8268 | NOV2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8269 | NOV3:U0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8270 | NOV3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8271 | NOV4:U0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8272 | NOV4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8273 | VUB1:U1/2 >/< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8274 | VUB1:U1/2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8275 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8276 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8277 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8278 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8279 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8280 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8281 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8282 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8283 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8284 |  |  |  | HR8283 (Lo-16bits)
8285 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8286 |  |  |  | HR8285 (Lo-16bits)
8287 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8288 |  |  |  | HR8287 (Lo-16bits)
8289 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8290 |  |  |  | HR8289 (Lo-16bits)
8291 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8292 |  |  |  | HR8291 (Lo-16bits)
8293 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8294 |  |  |  | HR8293 (Lo-16bits)
8295 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8296 |  |  |  | HR8295 (Lo-16bits)
8297 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8298 |  |  |  | HR8297 (Lo-16bits)
8299 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8300 |  |  |  | HR8299 (Lo-16bits)
8301 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8302 |  |  |  | HR8301 (Lo-16bits)
8303 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8304 |  |  |  | HR8303 (Lo-16bits)
8305 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8306 |  |  |  | HR8305 (Lo-16bits)
8307 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8308 |  |  |  | HR8307 (Lo-16bits)
8309 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8310 |  |  |  | HR8309 (Lo-16bits)
8311 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8312 |  |  |  | HR8311 (Lo-16bits)
8313 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8314 |  |  |  | HR8313 (Lo-16bits)
8315 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8316 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8317 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8318 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8319 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8320 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8321 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8322 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8323 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8324 |  |  |  | HR8323 (Lo-16bits)
8325 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8326 |  |  |  | HR8325 (Lo-16bits)
8327 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8328 |  |  |  | HR8327 (Lo-16bits)
8329 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8330 |  |  |  | HR8329 (Lo-16bits)
8331 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8332 |  |  |  | HR8331 (Lo-16bits)
8333 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8334 |  |  |  | HR8333 (Lo-16bits)
8335 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8336 |  |  |  | HR8335 (Lo-16bits)
8337 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8338 |  |  |  | HR8337 (Lo-16bits)
8339 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8340 |  |  |  | HR8339 (Lo-16bits)
8341 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8342 |  |  |  | HR8341 (Lo-16bits)
8343 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8344 |  |  |  | HR8343 (Lo-16bits)
8345 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8346 |  |  |  | HR8345 (Lo-16bits)
8347 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8348 |  |  |  | HR8347 (Lo-16bits)
8349 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8350 |  |  |  | HR8349 (Lo-16bits)
8351 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8352 |  |  |  | HR8351 (Lo-16bits)
8353 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8354 |  |  |  | HR8353 (Lo-16bits)
8355 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8356 |  |  |  | HR8355 (Lo-16bits)
8357 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8358 |  |  |  | HR8357 (Lo-16bits)
8359 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8360 |  |  |  | HR8359 (Lo-16bits)
8361 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8362 |  |  |  | HR8361 (Lo-16bits)
8363 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8364 |  |  |  | HR8363 (Lo-16bits)
8365 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8366 |  |  |  | HR8365 (Lo-16bits)
8367 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8368 |  |  |  | HR8367 (Lo-16bits)
8369 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8370 |  |  |  | HR8369 (Lo-16bits)
8371 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8372 |  |  |  | HR8371 (Lo-16bits)
8373 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8374 |  |  |  | HR8373 (Lo-16bits)
8375 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8376 |  |  |  | HR8375 (Lo-16bits)
8377 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8378 |  |  |  | HR8377 (Lo-16bits)
8379 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8380 |  |  |  | HR8379 (Lo-16bits)
8381 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8382 |  |  |  | HR8381 (Lo-16bits)
8383 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8384 |  |  |  | HR8383 (Lo-16bits)
8385 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8386 |  |  |  | HR8385 (Lo-16bits)
8387 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8388 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8389 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8390 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8391 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8392 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8393 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8394 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8395 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8396 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8397 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8398 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8399 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8400 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8401 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8402 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8403 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8404 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8405 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8406 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8407 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8408 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8409 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8410 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8411 | VUB2:U1/2 >>/<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8412 | VUB2:U1/2 >>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8413 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8414 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8415 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8416 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8417 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8418 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8419 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8420 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8421 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8422 |  |  |  | HR8421 (Lo-16bits)
8423 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8424 |  |  |  | HR8423 (Lo-16bits)
8425 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8426 |  |  |  | HR8425 (Lo-16bits)
8427 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8428 |  |  |  | HR8427 (Lo-16bits)
8429 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8430 |  |  |  | HR8429 (Lo-16bits)
8431 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8432 |  |  |  | HR8431 (Lo-16bits)
8433 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8434 |  |  |  | HR8433 (Lo-16bits)
8435 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8436 |  |  |  | HR8435 (Lo-16bits)
8437 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8438 |  |  |  | HR8437 (Lo-16bits)
8439 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8440 |  |  |  | HR8439 (Lo-16bits)
8441 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8442 |  |  |  | HR8441 (Lo-16bits)
8443 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8444 |  |  |  | HR8443 (Lo-16bits)
8445 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8446 |  |  |  | HR8445 (Lo-16bits)
8447 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8448 |  |  |  | HR8447 (Lo-16bits)
8449 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8450 |  |  |  | HR8449 (Lo-16bits)
8451 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8452 |  |  |  | HR8451 (Lo-16bits)
8453 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8454 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8455 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8456 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8457 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8458 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8459 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8460 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8461 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8462 |  |  |  | HR8461 (Lo-16bits)
8463 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8464 |  |  |  | HR8463 (Lo-16bits)
8465 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8466 |  |  |  | HR8465 (Lo-16bits)
8467 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8468 |  |  |  | HR8467 (Lo-16bits)
8469 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8470 |  |  |  | HR8469 (Lo-16bits)
8471 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8472 |  |  |  | HR8471 (Lo-16bits)
8473 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8474 |  |  |  | HR8473 (Lo-16bits)
8475 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8476 |  |  |  | HR8475 (Lo-16bits)
8477 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8478 |  |  |  | HR8477 (Lo-16bits)
8479 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8480 |  |  |  | HR8479 (Lo-16bits)
8481 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8482 |  |  |  | HR8481 (Lo-16bits)
8483 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8484 |  |  |  | HR8483 (Lo-16bits)
8485 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8486 |  |  |  | HR8485 (Lo-16bits)
8487 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8488 |  |  |  | HR8487 (Lo-16bits)
8489 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8490 |  |  |  | HR8489 (Lo-16bits)
8491 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8492 |  |  |  | HR8491 (Lo-16bits)
8493 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8494 |  |  |  | HR8493 (Lo-16bits)
8495 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8496 |  |  |  | HR8495 (Lo-16bits)
8497 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8498 |  |  |  | HR8497 (Lo-16bits)
8499 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8500 |  |  |  | HR8499 (Lo-16bits)
8501 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8502 |  |  |  | HR8501 (Lo-16bits)
8503 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8504 |  |  |  | HR8503 (Lo-16bits)
8505 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8506 |  |  |  | HR8505 (Lo-16bits)
8507 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8508 |  |  |  | HR8507 (Lo-16bits)
8509 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8510 |  |  |  | HR8509 (Lo-16bits)
8511 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8512 |  |  |  | HR8511 (Lo-16bits)
8513 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8514 |  |  |  | HR8513 (Lo-16bits)
8515 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8516 |  |  |  | HR8515 (Lo-16bits)
8517 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8518 |  |  |  | HR8517 (Lo-16bits)
8519 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8520 |  |  |  | HR8519 (Lo-16bits)
8521 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8522 |  |  |  | HR8521 (Lo-16bits)
8523 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8524 |  |  |  | HR8523 (Lo-16bits)
8525 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8526 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8527 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8528 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8529 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8530 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8531 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8532 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8533 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8534 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8535 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8536 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8537 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8538 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8539 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8540 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8541 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8542 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8543 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8544 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8545 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8546 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8547 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8548 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8549 | VUB3:U1/2 >>>/<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8550 | VUB3:U1/2 >>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8551 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8552 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8553 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8554 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8555 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8556 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8557 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8558 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8559 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8560 |  |  |  | HR8559 (Lo-16bits)
8561 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8562 |  |  |  | HR8561 (Lo-16bits)
8563 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8564 |  |  |  | HR8563 (Lo-16bits)
8565 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8566 |  |  |  | HR8565 (Lo-16bits)
8567 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8568 |  |  |  | HR8567 (Lo-16bits)
8569 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8570 |  |  |  | HR8569 (Lo-16bits)
8571 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8572 |  |  |  | HR8571 (Lo-16bits)
8573 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8574 |  |  |  | HR8573 (Lo-16bits)
8575 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8576 |  |  |  | HR8575 (Lo-16bits)
8577 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8578 |  |  |  | HR8577 (Lo-16bits)
8579 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8580 |  |  |  | HR8579 (Lo-16bits)
8581 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8582 |  |  |  | HR8581 (Lo-16bits)
8583 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8584 |  |  |  | HR8583 (Lo-16bits)
8585 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8586 |  |  |  | HR8585 (Lo-16bits)
8587 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8588 |  |  |  | HR8587 (Lo-16bits)
8589 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8590 |  |  |  | HR8589 (Lo-16bits)
8591 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8592 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8593 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8594 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8595 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8596 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8597 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8598 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8599 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8600 |  |  |  | HR8599 (Lo-16bits)
8601 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8602 |  |  |  | HR8601 (Lo-16bits)
8603 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8604 |  |  |  | HR8603 (Lo-16bits)
8605 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8606 |  |  |  | HR8605 (Lo-16bits)
8607 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8608 |  |  |  | HR8607 (Lo-16bits)
8609 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8610 |  |  |  | HR8609 (Lo-16bits)
8611 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8612 |  |  |  | HR8611 (Lo-16bits)
8613 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8614 |  |  |  | HR8613 (Lo-16bits)
8615 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8616 |  |  |  | HR8615 (Lo-16bits)
8617 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8618 |  |  |  | HR8617 (Lo-16bits)
8619 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8620 |  |  |  | HR8619 (Lo-16bits)
8621 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8622 |  |  |  | HR8621 (Lo-16bits)
8623 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8624 |  |  |  | HR8623 (Lo-16bits)
8625 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8626 |  |  |  | HR8625 (Lo-16bits)
8627 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8628 |  |  |  | HR8627 (Lo-16bits)
8629 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8630 |  |  |  | HR8629 (Lo-16bits)
8631 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8632 |  |  |  | HR8631 (Lo-16bits)
8633 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8634 |  |  |  | HR8633 (Lo-16bits)
8635 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8636 |  |  |  | HR8635 (Lo-16bits)
8637 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8638 |  |  |  | HR8637 (Lo-16bits)
8639 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8640 |  |  |  | HR8639 (Lo-16bits)
8641 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8642 |  |  |  | HR8641 (Lo-16bits)
8643 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8644 |  |  |  | HR8643 (Lo-16bits)
8645 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8646 |  |  |  | HR8645 (Lo-16bits)
8647 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8648 |  |  |  | HR8647 (Lo-16bits)
8649 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8650 |  |  |  | HR8649 (Lo-16bits)
8651 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8652 |  |  |  | HR8651 (Lo-16bits)
8653 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8654 |  |  |  | HR8653 (Lo-16bits)
8655 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8656 |  |  |  | HR8655 (Lo-16bits)
8657 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8658 |  |  |  | HR8657 (Lo-16bits)
8659 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8660 |  |  |  | HR8659 (Lo-16bits)
8661 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8662 |  |  |  | HR8661 (Lo-16bits)
8663 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8664 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8665 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8666 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8667 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8668 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8669 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8670 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8671 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8672 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8673 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8674 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8675 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8676 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8677 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8678 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8679 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8680 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8681 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8682 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8683 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8684 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8685 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8686 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8687 | VUB4:U1/2 >>>>/<<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8688 | VUB4:U1/2 >>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8689 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8690 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8691 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8692 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8693 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8694 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8695 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8696 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8697 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8698 |  |  |  | HR8697 (Lo-16bits)
8699 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8700 |  |  |  | HR8699 (Lo-16bits)
8701 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8702 |  |  |  | HR8701 (Lo-16bits)
8703 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8704 |  |  |  | HR8703 (Lo-16bits)
8705 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8706 |  |  |  | HR8705 (Lo-16bits)
8707 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8708 |  |  |  | HR8707 (Lo-16bits)
8709 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8710 |  |  |  | HR8709 (Lo-16bits)
8711 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8712 |  |  |  | HR8711 (Lo-16bits)
8713 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8714 |  |  |  | HR8713 (Lo-16bits)
8715 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8716 |  |  |  | HR8715 (Lo-16bits)
8717 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8718 |  |  |  | HR8717 (Lo-16bits)
8719 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8720 |  |  |  | HR8719 (Lo-16bits)
8721 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8722 |  |  |  | HR8721 (Lo-16bits)
8723 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8724 |  |  |  | HR8723 (Lo-16bits)
8725 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8726 |  |  |  | HR8725 (Lo-16bits)
8727 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8728 |  |  |  | HR8727 (Lo-16bits)
8729 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8730 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8731 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8732 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8733 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8734 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8735 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8736 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8737 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8738 |  |  |  | HR8737 (Lo-16bits)
8739 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8740 |  |  |  | HR8739 (Lo-16bits)
8741 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8742 |  |  |  | HR8741 (Lo-16bits)
8743 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8744 |  |  |  | HR8743 (Lo-16bits)
8745 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8746 |  |  |  | HR8745 (Lo-16bits)
8747 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8748 |  |  |  | HR8747 (Lo-16bits)
8749 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8750 |  |  |  | HR8749 (Lo-16bits)
8751 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8752 |  |  |  | HR8751 (Lo-16bits)
8753 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8754 |  |  |  | HR8753 (Lo-16bits)
8755 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8756 |  |  |  | HR8755 (Lo-16bits)
8757 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8758 |  |  |  | HR8757 (Lo-16bits)
8759 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8760 |  |  |  | HR8759 (Lo-16bits)
8761 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8762 |  |  |  | HR8761 (Lo-16bits)
8763 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8764 |  |  |  | HR8763 (Lo-16bits)
8765 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8766 |  |  |  | HR8765 (Lo-16bits)
8767 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8768 |  |  |  | HR8767 (Lo-16bits)
8769 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8770 |  |  |  | HR8769 (Lo-16bits)
8771 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8772 |  |  |  | HR8771 (Lo-16bits)
8773 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8774 |  |  |  | HR8773 (Lo-16bits)
8775 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8776 |  |  |  | HR8775 (Lo-16bits)
8777 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8778 |  |  |  | HR8777 (Lo-16bits)
8779 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8780 |  |  |  | HR8779 (Lo-16bits)
8781 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8782 |  |  |  | HR8781 (Lo-16bits)
8783 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8784 |  |  |  | HR8783 (Lo-16bits)
8785 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8786 |  |  |  | HR8785 (Lo-16bits)
8787 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8788 |  |  |  | HR8787 (Lo-16bits)
8789 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8790 |  |  |  | HR8789 (Lo-16bits)
8791 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8792 |  |  |  | HR8791 (Lo-16bits)
8793 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8794 |  |  |  | HR8793 (Lo-16bits)
8795 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8796 |  |  |  | HR8795 (Lo-16bits)
8797 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8798 |  |  |  | HR8797 (Lo-16bits)
8799 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8800 |  |  |  | HR8799 (Lo-16bits)
8801 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8802 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8803 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8804 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8805 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8806 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8807 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8808 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8809 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8810 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8811 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8812 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8813 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8814 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8815 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8816 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8817 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8818 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8819 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8820 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8821 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8822 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8823 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8824 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8825 | PGS1:PS1 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8826 | PGS1:PS2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8827 | PGS1:PS3 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8828 | PGS1:PS4 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8829 | PGS1:PS5 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8830 | PGS1:PS6 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8831 | PGS1:PS7 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8832 | PGS1:PS8 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8833 | PGS1:PS9 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8834 | PGS1:PS10 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8835 | FRQC1:f> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8836 | FRQC1:f>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8837 | FRQC1:f>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8838 | FRQC1:f>>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8839 | FRQC1:f< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8840 | FRQC1:f<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8841 | FRQC1:f<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8842 | FRQC1:f<<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8843 | FRQV1:f</> [81O/81U] mode | R(W) | 1 | 0=Disabled;1=Activated
8844 | FRQV1:f> Enable | R(W) | 1 | 0=No;1=Yes
8845 | FRQV1:f> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8846 | FRQV1:f>> Enable | R(W) | 1 | 0=No;1=Yes
8847 | FRQV1:f>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8848 | FRQV1:f>>> Enable | R(W) | 1 | 0=No;1=Yes
8849 | FRQV1:f>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8850 | FRQV1:f>>>> Enable | R(W) | 1 | 0=No;1=Yes
8851 | FRQV1:f>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8852 | FRQV1:f< Enable | R(W) | 1 | 0=No;1=Yes
8853 | FRQV1:f< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8854 | FRQV1:f<< Enable | R(W) | 1 | 0=No;1=Yes
8855 | FRQV1:f<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8856 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8857 | FRQV1:f<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8858 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8859 | FRQV1:f<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8860 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8861 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8862 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8863 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8864 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8865 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8866 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8867 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8868 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8869 |  |  |  | HR8868 (Lo-16bits)
8870 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8871 |  |  |  | HR8870 (Lo-16bits)
8872 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8873 |  |  |  | HR8872 (Lo-16bits)
8874 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8875 |  |  |  | HR8874 (Lo-16bits)
8876 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8877 |  |  |  | HR8876 (Lo-16bits)
8878 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8879 |  |  |  | HR8878 (Lo-16bits)
8880 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8881 |  |  |  | HR8880 (Lo-16bits)
8882 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8883 |  |  |  | HR8882 (Lo-16bits)
8884 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8885 |  |  |  | HR8884 (Lo-16bits)
8886 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8887 |  |  |  | HR8886 (Lo-16bits)
8888 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8889 |  |  |  | HR8888 (Lo-16bits)
8890 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8891 |  |  |  | HR8890 (Lo-16bits)
8892 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8893 |  |  |  | HR8892 (Lo-16bits)
8894 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8895 |  |  |  | HR8894 (Lo-16bits)
8896 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8897 |  |  |  | HR8896 (Lo-16bits)
8898 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8899 |  |  |  | HR8898 (Lo-16bits)
8900 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8901 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8902 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8903 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8904 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8905 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8906 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8907 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8908 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8909 |  |  |  | HR8908 (Lo-16bits)
8910 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8911 |  |  |  | HR8910 (Lo-16bits)
8912 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8913 |  |  |  | HR8912 (Lo-16bits)
8914 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8915 |  |  |  | HR8914 (Lo-16bits)
8916 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8917 |  |  |  | HR8916 (Lo-16bits)
8918 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8919 |  |  |  | HR8918 (Lo-16bits)
8920 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8921 |  |  |  | HR8920 (Lo-16bits)
8922 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8923 |  |  |  | HR8922 (Lo-16bits)
8924 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8925 |  |  |  | HR8924 (Lo-16bits)
8926 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8927 |  |  |  | HR8926 (Lo-16bits)
8928 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8929 |  |  |  | HR8928 (Lo-16bits)
8930 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8931 |  |  |  | HR8930 (Lo-16bits)
8932 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8933 |  |  |  | HR8932 (Lo-16bits)
8934 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8935 |  |  |  | HR8934 (Lo-16bits)
8936 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8937 |  |  |  | HR8936 (Lo-16bits)
8938 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8939 |  |  |  | HR8938 (Lo-16bits)
8940 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8941 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8942 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8943 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8944 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8945 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8946 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8947 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8948 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8949 |  |  |  | HR8948 (Lo-16bits)
8950 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8951 |  |  |  | HR8950 (Lo-16bits)
8952 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8953 |  |  |  | HR8952 (Lo-16bits)
8954 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8955 |  |  |  | HR8954 (Lo-16bits)
8956 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8957 |  |  |  | HR8956 (Lo-16bits)
8958 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8959 |  |  |  | HR8958 (Lo-16bits)
8960 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8961 |  |  |  | HR8960 (Lo-16bits)
8962 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8963 |  |  |  | HR8962 (Lo-16bits)
8964 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8965 |  |  |  | HR8964 (Lo-16bits)
8966 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8967 |  |  |  | HR8966 (Lo-16bits)
8968 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8969 |  |  |  | HR8968 (Lo-16bits)
8970 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8971 |  |  |  | HR8970 (Lo-16bits)
8972 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8973 |  |  |  | HR8972 (Lo-16bits)
8974 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8975 |  |  |  | HR8974 (Lo-16bits)
8976 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8977 |  |  |  | HR8976 (Lo-16bits)
8978 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8979 |  |  |  | HR8978 (Lo-16bits)
8980 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8981 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8982 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8983 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8984 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8985 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8986 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8987 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8988 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8989 |  |  |  | HR8988 (Lo-16bits)
8990 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8991 |  |  |  | HR8990 (Lo-16bits)
8992 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8993 |  |  |  | HR8992 (Lo-16bits)
8994 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8995 |  |  |  | HR8994 (Lo-16bits)
8996 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8997 |  |  |  | HR8996 (Lo-16bits)
8998 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8999 |  |  |  | HR8998 (Lo-16bits)
9000 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9001 |  |  |  | HR9000 (Lo-16bits)
9002 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9003 |  |  |  | HR9002 (Lo-16bits)
9004 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9005 |  |  |  | HR9004 (Lo-16bits)
9006 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9007 |  |  |  | HR9006 (Lo-16bits)
9008 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9009 |  |  |  | HR9008 (Lo-16bits)
9010 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9011 |  |  |  | HR9010 (Lo-16bits)
9012 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9013 |  |  |  | HR9012 (Lo-16bits)
9014 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9015 |  |  |  | HR9014 (Lo-16bits)
9016 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9017 |  |  |  | HR9016 (Lo-16bits)
9018 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9019 |  |  |  | HR9018 (Lo-16bits)
9020 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9021 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9022 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9023 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9024 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9025 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9026 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9027 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9028 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9029 |  |  |  | HR9028 (Lo-16bits)
9030 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9031 |  |  |  | HR9030 (Lo-16bits)
9032 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9033 |  |  |  | HR9032 (Lo-16bits)
9034 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9035 |  |  |  | HR9034 (Lo-16bits)
9036 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9037 |  |  |  | HR9036 (Lo-16bits)
9038 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9039 |  |  |  | HR9038 (Lo-16bits)
9040 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9041 |  |  |  | HR9040 (Lo-16bits)
9042 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9043 |  |  |  | HR9042 (Lo-16bits)
9044 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9045 |  |  |  | HR9044 (Lo-16bits)
9046 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9047 |  |  |  | HR9046 (Lo-16bits)
9048 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9049 |  |  |  | HR9048 (Lo-16bits)
9050 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9051 |  |  |  | HR9050 (Lo-16bits)
9052 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9053 |  |  |  | HR9052 (Lo-16bits)
9054 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9055 |  |  |  | HR9054 (Lo-16bits)
9056 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9057 |  |  |  | HR9056 (Lo-16bits)
9058 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9059 |  |  |  | HR9058 (Lo-16bits)
9060 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9061 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9062 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9063 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9064 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9065 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9066 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9067 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9068 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9069 |  |  |  | HR9068 (Lo-16bits)
9070 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9071 |  |  |  | HR9070 (Lo-16bits)
9072 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9073 |  |  |  | HR9072 (Lo-16bits)
9074 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9075 |  |  |  | HR9074 (Lo-16bits)
9076 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9077 |  |  |  | HR9076 (Lo-16bits)
9078 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9079 |  |  |  | HR9078 (Lo-16bits)
9080 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9081 |  |  |  | HR9080 (Lo-16bits)
9082 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9083 |  |  |  | HR9082 (Lo-16bits)
9084 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9085 |  |  |  | HR9084 (Lo-16bits)
9086 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9087 |  |  |  | HR9086 (Lo-16bits)
9088 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9089 |  |  |  | HR9088 (Lo-16bits)
9090 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9091 |  |  |  | HR9090 (Lo-16bits)
9092 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9093 |  |  |  | HR9092 (Lo-16bits)
9094 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9095 |  |  |  | HR9094 (Lo-16bits)
9096 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9097 |  |  |  | HR9096 (Lo-16bits)
9098 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9099 |  |  |  | HR9098 (Lo-16bits)
9100 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9101 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9102 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9103 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9104 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9105 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9106 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9107 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9108 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9109 |  |  |  | HR9108 (Lo-16bits)
9110 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9111 |  |  |  | HR9110 (Lo-16bits)
9112 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9113 |  |  |  | HR9112 (Lo-16bits)
9114 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9115 |  |  |  | HR9114 (Lo-16bits)
9116 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9117 |  |  |  | HR9116 (Lo-16bits)
9118 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9119 |  |  |  | HR9118 (Lo-16bits)
9120 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9121 |  |  |  | HR9120 (Lo-16bits)
9122 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9123 |  |  |  | HR9122 (Lo-16bits)
9124 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9125 |  |  |  | HR9124 (Lo-16bits)
9126 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9127 |  |  |  | HR9126 (Lo-16bits)
9128 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9129 |  |  |  | HR9128 (Lo-16bits)
9130 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9131 |  |  |  | HR9130 (Lo-16bits)
9132 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9133 |  |  |  | HR9132 (Lo-16bits)
9134 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9135 |  |  |  | HR9134 (Lo-16bits)
9136 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9137 |  |  |  | HR9136 (Lo-16bits)
9138 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9139 |  |  |  | HR9138 (Lo-16bits)
9140 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9141 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9142 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9143 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9144 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9145 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9146 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9147 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9148 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9149 |  |  |  | HR9148 (Lo-16bits)
9150 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9151 |  |  |  | HR9150 (Lo-16bits)
9152 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9153 |  |  |  | HR9152 (Lo-16bits)
9154 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9155 |  |  |  | HR9154 (Lo-16bits)
9156 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9157 |  |  |  | HR9156 (Lo-16bits)
9158 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9159 |  |  |  | HR9158 (Lo-16bits)
9160 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9161 |  |  |  | HR9160 (Lo-16bits)
9162 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9163 |  |  |  | HR9162 (Lo-16bits)
9164 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9165 |  |  |  | HR9164 (Lo-16bits)
9166 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9167 |  |  |  | HR9166 (Lo-16bits)
9168 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9169 |  |  |  | HR9168 (Lo-16bits)
9170 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9171 |  |  |  | HR9170 (Lo-16bits)
9172 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9173 |  |  |  | HR9172 (Lo-16bits)
9174 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9175 |  |  |  | HR9174 (Lo-16bits)
9176 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9177 |  |  |  | HR9176 (Lo-16bits)
9178 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9179 |  |  |  | HR9178 (Lo-16bits)
9180 | DFT1:df/dt >/< (1) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9181 | DFT1:df/dt >/< (2) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9182 | DFT1:df/dt >/< (3) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9183 | DFT1:df/dt >/< (4) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9184 | DFT1:df/dt >/< (5) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9185 | DFT1:df/dt >/< (6) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9186 | DFT1:df/dt >/< (7) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9187 | DFT1:df/dt >/< (8) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9188 | RHC1:Counter is now | R | 1 | 0=Idle;1=Counting
9189 | RHC1:Running hours | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9190 |  |  |  | HR9189 (Lo-16bits)
9191 | RHC1:Start count | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9192 |  |  |  | HR9191 (Lo-16bits)
9193 | GST1:Generator is now | R | 1 | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
9194 | PWR1:PQS>/< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9195 | PWR2:PQS>>/<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9196 | PWR3:PQS>>>/<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9197 | PWR4:PQS>>>>/<<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9198 | OPW1:P> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9199 | UPW1:P< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9200 | RPW1:Prev> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9201 | SEF1:U03rd< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9202 | SEF1:U03rd< Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
9203 | UEX1:Q< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9204 | UIM1:Z< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9205 | UIM2:Z<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9206 | VOC1:Iv> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9207 | VOC1:Voltage measurement | R | 1 | 0=Invalid U1 not avail.;1=Ok
9208 | VHZ1:V/Hz(1) > condition | R | 1 | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
9209 | VHZ1:V/Hz(2) > condition | R | 1 | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
9210 | UPF1:PF< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
9211 | RTDIN:S1 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9212 |  |  |  | HR9211 (Lo-16bits)
9213 | RTDIN:S1 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9214 |  |  |  | HR9213 (Lo-16bits)
9215 | RTDIN:S1 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9216 | RTDIN:S1 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9217 |  |  |  | HR9216 (Lo-16bits)
9218 | RTDIN:S2 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9219 |  |  |  | HR9218 (Lo-16bits)
9220 | RTDIN:S2 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9221 |  |  |  | HR9220 (Lo-16bits)
9222 | RTDIN:S2 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9223 | RTDIN:S2 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9224 |  |  |  | HR9223 (Lo-16bits)
9225 | RTDIN:S3 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9226 |  |  |  | HR9225 (Lo-16bits)
9227 | RTDIN:S3 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9228 |  |  |  | HR9227 (Lo-16bits)
9229 | RTDIN:S3 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9230 | RTDIN:S3 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9231 |  |  |  | HR9230 (Lo-16bits)
9232 | RTDIN:S4 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9233 |  |  |  | HR9232 (Lo-16bits)
9234 | RTDIN:S4 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9235 |  |  |  | HR9234 (Lo-16bits)
9236 | RTDIN:S4 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9237 | RTDIN:S4 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9238 |  |  |  | HR9237 (Lo-16bits)
9239 | RTDIN:S5 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9240 |  |  |  | HR9239 (Lo-16bits)
9241 | RTDIN:S5 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9242 |  |  |  | HR9241 (Lo-16bits)
9243 | RTDIN:S5 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9244 | RTDIN:S5 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9245 |  |  |  | HR9244 (Lo-16bits)
9246 | RTDIN:S6 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9247 |  |  |  | HR9246 (Lo-16bits)
9248 | RTDIN:S6 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9249 |  |  |  | HR9248 (Lo-16bits)
9250 | RTDIN:S6 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9251 | RTDIN:S6 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9252 |  |  |  | HR9251 (Lo-16bits)
9253 | RTDIN:S7 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9254 |  |  |  | HR9253 (Lo-16bits)
9255 | RTDIN:S7 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9256 |  |  |  | HR9255 (Lo-16bits)
9257 | RTDIN:S7 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9258 |  |  |  | HR9257 (Lo-16bits)
9259 | RTDIN:S7 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9260 | RTDIN:S7 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9261 |  |  |  | HR9260 (Lo-16bits)
9262 | RTDIN:S8 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9263 |  |  |  | HR9262 (Lo-16bits)
9264 | RTDIN:S8 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9265 |  |  |  | HR9264 (Lo-16bits)
9266 | RTDIN:S8 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9267 |  |  |  | HR9266 (Lo-16bits)
9268 | RTDIN:S8 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9269 | RTDIN:S8 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9270 |  |  |  | HR9269 (Lo-16bits)
9271 | RTDIN:S9 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9272 |  |  |  | HR9271 (Lo-16bits)
9273 | RTDIN:S9 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9274 |  |  |  | HR9273 (Lo-16bits)
9275 | RTDIN:S9 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9276 | RTDIN:S9 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9277 |  |  |  | HR9276 (Lo-16bits)
9278 | RTDIN:S10 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9279 |  |  |  | HR9278 (Lo-16bits)
9280 | RTDIN:S10 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9281 |  |  |  | HR9280 (Lo-16bits)
9282 | RTDIN:S10 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9283 | RTDIN:S10 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9284 |  |  |  | HR9283 (Lo-16bits)
9285 | RTDIN:S11 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9286 |  |  |  | HR9285 (Lo-16bits)
9287 | RTDIN:S11 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9288 |  |  |  | HR9287 (Lo-16bits)
9289 | RTDIN:S11 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9290 | RTDIN:S11 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9291 |  |  |  | HR9290 (Lo-16bits)
9292 | RTDIN:S12 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9293 |  |  |  | HR9292 (Lo-16bits)
9294 | RTDIN:S12 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9295 |  |  |  | HR9294 (Lo-16bits)
9296 | RTDIN:S12 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9297 | RTDIN:S12 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9298 |  |  |  | HR9297 (Lo-16bits)
9299 | RTDIN:S13 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9300 |  |  |  | HR9299 (Lo-16bits)
9301 | RTDIN:S13 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9302 |  |  |  | HR9301 (Lo-16bits)
9303 | RTDIN:S13 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9304 | RTDIN:S13 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9305 |  |  |  | HR9304 (Lo-16bits)
9306 | RTDIN:S14 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9307 |  |  |  | HR9306 (Lo-16bits)
9308 | RTDIN:S14 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9309 |  |  |  | HR9308 (Lo-16bits)
9310 | RTDIN:S14 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9311 | RTDIN:S14 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9312 |  |  |  | HR9311 (Lo-16bits)
9313 | RTDIN:S15 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9314 |  |  |  | HR9313 (Lo-16bits)
9315 | RTDIN:S15 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9316 |  |  |  | HR9315 (Lo-16bits)
9317 | RTDIN:S15 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9318 |  |  |  | HR9317 (Lo-16bits)
9319 | RTDIN:S15 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9320 | RTDIN:S15 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9321 |  |  |  | HR9320 (Lo-16bits)
9322 | RTDIN:S16 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9323 |  |  |  | HR9322 (Lo-16bits)
9324 | RTDIN:S16 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9325 |  |  |  | HR9324 (Lo-16bits)
9326 | RTDIN:S16 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9327 |  |  |  | HR9326 (Lo-16bits)
9328 | RTDIN:S16 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9329 | RTDIN:S16 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9330 |  |  |  | HR9329 (Lo-16bits)
9331 | RTD1:S1 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9332 |  |  |  | HR9331 (Lo-16bits)
9333 | RTD1:S2 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9334 |  |  |  | HR9333 (Lo-16bits)
9335 | RTD1:S3 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9336 |  |  |  | HR9335 (Lo-16bits)
9337 | RTD1:S4 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9338 |  |  |  | HR9337 (Lo-16bits)
9339 | RTD1:S5 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9340 |  |  |  | HR9339 (Lo-16bits)
9341 | RTD1:S6 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9342 |  |  |  | HR9341 (Lo-16bits)
9343 | RTD1:S7 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9344 |  |  |  | HR9343 (Lo-16bits)
9345 | RTD1:S8 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9346 |  |  |  | HR9345 (Lo-16bits)
9347 | RTD1:S9 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9348 |  |  |  | HR9347 (Lo-16bits)
9349 | RTD1:S10 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9350 |  |  |  | HR9349 (Lo-16bits)
9351 | RTD1:S11 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9352 |  |  |  | HR9351 (Lo-16bits)
9353 | RTD1:S12 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9354 |  |  |  | HR9353 (Lo-16bits)
9355 | RTD1:S13 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9356 |  |  |  | HR9355 (Lo-16bits)
9357 | RTD1:S14 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9358 |  |  |  | HR9357 (Lo-16bits)
9359 | RTD1:S15 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9360 |  |  |  | HR9359 (Lo-16bits)
9361 | RTD1:S16 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9362 |  |  |  | HR9361 (Lo-16bits)
9363 | RTD1:S1 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9364 |  |  |  | HR9363 (Lo-16bits)
9365 | RTD1:S1 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9366 |  |  |  | HR9365 (Lo-16bits)
9367 | RTD1:S1 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9368 |  |  |  | HR9367 (Lo-16bits)
9369 | RTD1:S2 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9370 |  |  |  | HR9369 (Lo-16bits)
9371 | RTD1:S2 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9372 |  |  |  | HR9371 (Lo-16bits)
9373 | RTD1:S2 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9374 |  |  |  | HR9373 (Lo-16bits)
9375 | RTD1:S3 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9376 |  |  |  | HR9375 (Lo-16bits)
9377 | RTD1:S3 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9378 |  |  |  | HR9377 (Lo-16bits)
9379 | RTD1:S3 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9380 |  |  |  | HR9379 (Lo-16bits)
9381 | RTD1:S4 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9382 |  |  |  | HR9381 (Lo-16bits)
9383 | RTD1:S4 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9384 |  |  |  | HR9383 (Lo-16bits)
9385 | RTD1:S4 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9386 |  |  |  | HR9385 (Lo-16bits)
9387 | RTD1:S5 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9388 |  |  |  | HR9387 (Lo-16bits)
9389 | RTD1:S5 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9390 |  |  |  | HR9389 (Lo-16bits)
9391 | RTD1:S5 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9392 |  |  |  | HR9391 (Lo-16bits)
9393 | RTD1:S6 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9394 |  |  |  | HR9393 (Lo-16bits)
9395 | RTD1:S6 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9396 |  |  |  | HR9395 (Lo-16bits)
9397 | RTD1:S6 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9398 |  |  |  | HR9397 (Lo-16bits)
9399 | RTD1:S7 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9400 |  |  |  | HR9399 (Lo-16bits)
9401 | RTD1:S7 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9402 |  |  |  | HR9401 (Lo-16bits)
9403 | RTD1:S7 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9404 |  |  |  | HR9403 (Lo-16bits)
9405 | RTD1:S8 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9406 |  |  |  | HR9405 (Lo-16bits)
9407 | RTD1:S8 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9408 |  |  |  | HR9407 (Lo-16bits)
9409 | RTD1:S8 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9410 |  |  |  | HR9409 (Lo-16bits)
9411 | RTD1:S9 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9412 |  |  |  | HR9411 (Lo-16bits)
9413 | RTD1:S9 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9414 |  |  |  | HR9413 (Lo-16bits)
9415 | RTD1:S9 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9416 |  |  |  | HR9415 (Lo-16bits)
9417 | RTD1:S10 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9418 |  |  |  | HR9417 (Lo-16bits)
9419 | RTD1:S10 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9420 |  |  |  | HR9419 (Lo-16bits)
9421 | RTD1:S10 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9422 |  |  |  | HR9421 (Lo-16bits)
9423 | RTD1:S11 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9424 |  |  |  | HR9423 (Lo-16bits)
9425 | RTD1:S11 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9426 |  |  |  | HR9425 (Lo-16bits)
9427 | RTD1:S11 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9428 |  |  |  | HR9427 (Lo-16bits)
9429 | RTD1:S12 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9430 |  |  |  | HR9429 (Lo-16bits)
9431 | RTD1:S12 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9432 |  |  |  | HR9431 (Lo-16bits)
9433 | RTD1:S12 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9434 |  |  |  | HR9433 (Lo-16bits)
9435 | RTD1:S13 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9436 |  |  |  | HR9435 (Lo-16bits)
9437 | RTD1:S13 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9438 |  |  |  | HR9437 (Lo-16bits)
9439 | RTD1:S13 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9440 |  |  |  | HR9439 (Lo-16bits)
9441 | RTD1:S14 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9442 |  |  |  | HR9441 (Lo-16bits)
9443 | RTD1:S14 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9444 |  |  |  | HR9443 (Lo-16bits)
9445 | RTD1:S14 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9446 |  |  |  | HR9445 (Lo-16bits)
9447 | RTD1:S15 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9448 |  |  |  | HR9447 (Lo-16bits)
9449 | RTD1:S15 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9450 |  |  |  | HR9449 (Lo-16bits)
9451 | RTD1:S15 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9452 |  |  |  | HR9451 (Lo-16bits)
9453 | RTD1:S16 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9454 |  |  |  | HR9453 (Lo-16bits)
9455 | RTD1:S16 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9456 |  |  |  | HR9455 (Lo-16bits)
9457 | RTD1:S16 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9458 |  |  |  | HR9457 (Lo-16bits)
9459 | ARC1:I/I0 Arc> condition | R | 1 | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
9460 | ARC1:I/I0 Arc> S1 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9461 |  |  |  | HR9460 (Lo-16bits)
9462 | ARC1:I/I0 Arc> S2 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9463 |  |  |  | HR9462 (Lo-16bits)
9464 | ARC1:I/I0 Arc> S3 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9465 |  |  |  | HR9464 (Lo-16bits)
9466 | ARC1:I/I0 Arc> S4 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9467 |  |  |  | HR9466 (Lo-16bits)
9468 | ARC1:I/I0 Arc> IO unit fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9469 |  |  |  | HR9468 (Lo-16bits)
9470 | CTS1:CTS1 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9471 | CTS2:CTS2 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9472 | VTS1:VTS condition | R | 1 | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
9473 | VTS1:Bus voltages | R | 1 | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
9474 | FLX1:Fault locator condition | R | 1 | 0=Idle;1=Triggered;2=Calc ready
9475 | THD1:THD condition | R | 1 | 0=Normal;1=Start;2=Alarm;3=Blocked
9476 | CBW1:CBW condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On
9477 | NJK1:U0> RECL condition | R | 1 | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
9478 | SOF1:SOTF condition | R | 1 | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
9479 | PCS1:PCS1 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9480 |  |  |  | HR9479 (Lo-16bits)
9481 | PCS2:PCS2 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9482 |  |  |  | HR9481 (Lo-16bits)
9483 | PCS3:PCS3 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9484 |  |  |  | HR9483 (Lo-16bits)
9485 | PCS4:PCS4 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9486 |  |  |  | HR9485 (Lo-16bits)
9487 | PCS5:PCS5 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9488 |  |  |  | HR9487 (Lo-16bits)
9489 | SYN1:SYN1 Condition | R | 2 | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok (Hi-16bits)
9490 |  |  |  | HR9489 (Lo-16bits)
9491 | SYN1:SYN2 Condition | R | 2 | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok (Hi-16bits)
9492 |  |  |  | HR9491 (Lo-16bits)
9493 | SYN1:SYN3 Condition | R | 2 | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok (Hi-16bits)
9494 |  |  |  | HR9493 (Lo-16bits)
9495 | SYN1:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9496 |  |  |  | HR9495 (Lo-16bits)
9497 | SYN1:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9498 |  |  |  | HR9497 (Lo-16bits)
9499 | SYN1:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9500 |  |  |  | HR9499 (Lo-16bits)
9501 | SYN1:SYN2 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9502 |  |  |  | HR9501 (Lo-16bits)
9503 | SYN1:SYN2 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9504 |  |  |  | HR9503 (Lo-16bits)
9505 | SYN1:SYN2 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9506 |  |  |  | HR9505 (Lo-16bits)
9507 | SYN1:SYN3 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9508 |  |  |  | HR9507 (Lo-16bits)
9509 | SYN1:SYN3 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9510 |  |  |  | HR9509 (Lo-16bits)
9511 | SYN1:SYN3 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9512 |  |  |  | HR9511 (Lo-16bits)
9513 | VJP1:<DELTA><alpha> > condition | R | 1 | 0=Normal;1=Blocked;2=Trip;3=Alarm
9514 | VJP1:Voltage meas selected | R | 1 | 0=Selection Ok;1=Selection not available
9515 | OBJ1:Object1 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9516 | OBJ2:Object2 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9517 | OBJ3:Object3 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9518 | OBJ4:Object4 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9519 | OBJ5:Object5 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9520 | OBJ6:Object6 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9521 | OBJ7:Object7 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9522 | OBJ8:Object8 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9523 | OBJ9:Object9 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9524 | OBJ10:Object10 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9525 | CIN1:Ind.1 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9526 | CIN2:Ind.2 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9527 | CIN3:Ind.3 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9528 | CIN4:Ind.4 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9529 | CIN5:Ind.5 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9530 | AR1:Auto-recloser [79] Mode | RW | 1 | 0=Disabled;1=Activated
9531 | AR1:AR Status | R | 2 | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear (Hi-16bits)
9532 |  |  |  | HR9531 (Lo-16bits)
9533 | AR1:Timer active | R | 1 | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
9534 | VRG1:Vreg settings condition | R | 2 | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok (Hi-16bits)
9535 |  |  |  | HR9534 (Lo-16bits)
9536 | VRG1:Vreg condition | R | 2 | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on (Hi-16bits)
9537 |  |  |  | HR9536 (Lo-16bits)
9538 | VRG1:Vreg timer active | R | 1 | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
9539 | VRG1:Voltage now | R | 2 | FLOAT [0...140] (Hi-16bits)
9540 |  |  |  | HR9539 (Lo-16bits)
9541 | VRG1:Voltage difference to set target | R | 2 | FLOAT [-140...140] (Hi-16bits)
9542 |  |  |  | HR9541 (Lo-16bits)
9543 | VRG1:Voltage meas condition | R | 1 | 0=Not configured;1=System U12;2=System U23;3=System U31;4=VT4 meas U12;5=VT4 meas U23;6=VT4 meas U31;7=VT4 conf not ok
9544 | VRG1:Tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
9545 |  |  |  | HR9544 (Lo-16bits)
9546 | VRG1:Absolute tap location | R | 2 | FLOAT [0...50] (Hi-16bits)
9547 |  |  |  | HR9546 (Lo-16bits)
9548 | VRG1:Control mode | R | 1 | 0=Auto;1=Manual (loc&rem)
9549 | VRG1:Remote tap control input | RW | 1 | 0=Stop;1=Lower;2=Higher
9550 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9551 |  |  |  | HR9550 (Lo-16bits)
9552 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9553 |  |  |  | HR9552 (Lo-16bits)
9554 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9555 |  |  |  | HR9554 (Lo-16bits)
9556 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9557 |  |  |  | HR9556 (Lo-16bits)
9558 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9559 |  |  |  | HR9558 (Lo-16bits)
9560 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9561 |  |  |  | HR9560 (Lo-16bits)
9562 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9563 |  |  |  | HR9562 (Lo-16bits)
9564 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9565 |  |  |  | HR9564 (Lo-16bits)
9566 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9567 |  |  |  | HR9566 (Lo-16bits)
9568 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9569 |  |  |  | HR9568 (Lo-16bits)
9570 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9571 |  |  |  | HR9570 (Lo-16bits)
9572 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9573 |  |  |  | HR9572 (Lo-16bits)
9574 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9575 |  |  |  | HR9574 (Lo-16bits)
9576 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9577 |  |  |  | HR9576 (Lo-16bits)
9578 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9579 |  |  |  | HR9578 (Lo-16bits)
9580 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9581 |  |  |  | HR9580 (Lo-16bits)
9582 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9583 |  |  |  | HR9582 (Lo-16bits)
9584 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9585 |  |  |  | HR9584 (Lo-16bits)
9586 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9587 |  |  |  | HR9586 (Lo-16bits)
9588 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9589 |  |  |  | HR9588 (Lo-16bits)
9590 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9591 |  |  |  | HR9590 (Lo-16bits)
9592 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9593 |  |  |  | HR9592 (Lo-16bits)
9594 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9595 |  |  |  | HR9594 (Lo-16bits)
9596 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9597 |  |  |  | HR9596 (Lo-16bits)
9598 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9599 |  |  |  | HR9598 (Lo-16bits)
9600 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9601 |  |  |  | HR9600 (Lo-16bits)
9602 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9603 |  |  |  | HR9602 (Lo-16bits)
9604 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9605 |  |  |  | HR9604 (Lo-16bits)
9606 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9607 |  |  |  | HR9606 (Lo-16bits)
9608 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9609 |  |  |  | HR9608 (Lo-16bits)
9610 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9611 |  |  |  | HR9610 (Lo-16bits)
9612 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9613 |  |  |  | HR9612 (Lo-16bits)
9614 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9615 |  |  |  | HR9614 (Lo-16bits)
9616 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9617 |  |  |  | HR9616 (Lo-16bits)
9618 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9619 |  |  |  | HR9618 (Lo-16bits)
9620 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9621 |  |  |  | HR9620 (Lo-16bits)
9622 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9623 |  |  |  | HR9622 (Lo-16bits)
9624 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9625 |  |  |  | HR9624 (Lo-16bits)
9626 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9627 |  |  |  | HR9626 (Lo-16bits)
9628 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9629 |  |  |  | HR9628 (Lo-16bits)
9630 | EMON1:I> (50) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9631 | EMON1:I0> (50N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9632 | EMON1:Idir> (67) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9633 | EMON1:I0dir> (67N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9634 | EMON1:I0Int> (67NT) Monitor condition | R | 1 | 0=Normal;1=FLT FW;2=FLT REV
9635 | EMON1:U< (27) Monitor condition | R | 1 | 0=Normal;1=Undervoltage;2=No voltage
9636 | EMON1:U0> (59N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9637 | EMON1:FL (21FL) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9638 | ALARM:Alarms 1-32 | R | 2 | 0b=A1;1b=A2;2b=A3;3b=A4;4b=A5;5b=A6;6b=A7;7b=A8;8b=A9;9b=A10;10b=A11;11b=A12;12b=A13;13b=A14;14b=A15;15b=A16;16b=A17;17b=A18;18b=A19;19b=A20;20b=A21;21b=A22;22b=A23;23b=A24;24b=A25;25b=A26;26b=A27;27b=A28;28b=A29;29b=A30;30b=A31;31b=A32 (Hi-16bits)
9639 |  |  |  | HR9638 (Lo-16bits)
9640 | ALARM:Alarms 33-64 | R | 2 | 0b=A33;1b=A34;2b=A35;3b=A36;4b=A37;5b=A38;6b=A39;7b=A40;8b=A41;9b=A42;10b=A43;11b=A44;12b=A45;13b=A46;14b=A47;15b=A48;16b=A49;17b=A50;18b=A51;19b=A52;20b=A53;21b=A54;22b=A55;23b=A56;24b=A57;25b=A58;26b=A59;27b=A60;28b=A61;29b=A62;30b=A63;31b=A64 (Hi-16bits)
9641 |  |  |  | HR9640 (Lo-16bits)
9642 | GSYN:Synchronizer mode | RW | 1 | 0=Disabled;1=Activated
9643 | GSYN:Synchronizing by | RW | 1 | 0=Autosynchronizer;1=Manual commands
9644 | GSYN:Manual switching mode | RW | 1 | 0=Assisted synchroswitch;1=I know what I am doing
9645 | GSYN:Magnitude side A | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9646 |  |  |  | HR9645 (Lo-16bits)
9647 | GSYN:Magnitude side B | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9648 |  |  |  | HR9647 (Lo-16bits)
9649 | GSYN:Frequency side A | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9650 |  |  |  | HR9649 (Lo-16bits)
9651 | GSYN:Frequency side B | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9652 |  |  |  | HR9651 (Lo-16bits)
9653 | GSYN:Magnitude difference | R | 2 | FLOAT [-200...200] (Hi-16bits)
9654 |  |  |  | HR9653 (Lo-16bits)
9655 | GSYN:Frequency difference | R | 2 | FLOAT [-100...100] (Hi-16bits)
9656 |  |  |  | HR9655 (Lo-16bits)
9657 | GSYN:Angle difference | R | 2 | FLOAT [-360...360] (Hi-16bits)
9658 |  |  |  | HR9657 (Lo-16bits)
9659 | GSYN:Magnitude difference on closing BRK | R | 2 | FLOAT [-200...200] (Hi-16bits)
9660 |  |  |  | HR9659 (Lo-16bits)
9661 | GSYN:Frequency difference on closing BRK | R | 2 | FLOAT [-100...100] (Hi-16bits)
9662 |  |  |  | HR9661 (Lo-16bits)
9663 | GSYN:Angle difference on closing BRK | R | 2 | FLOAT [-360...360] (Hi-16bits)
9664 |  |  |  | HR9663 (Lo-16bits)
9665 | GSYN:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9666 |  |  |  | HR9665 (Lo-16bits)
9667 | GSYN:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9668 |  |  |  | HR9667 (Lo-16bits)
9669 | GSYN:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9670 |  |  |  | HR9669 (Lo-16bits)
9671 | GSYN:Synchronizing time left | R | 2 | FLOAT [0...1800] (Hi-16bits)
9672 |  |  |  | HR9671 (Lo-16bits)
9673 | GSYN:Magnitude difference fine tune | RW | 2 | FLOAT [-200...200] (Hi-16bits)
9674 |  |  |  | HR9673 (Lo-16bits)
9675 | GSYN:Frequency difference fine tune | RW | 2 | FLOAT [-100...100] (Hi-16bits)
9676 |  |  |  | HR9675 (Lo-16bits)
9677 | GSYN:Angle difference fine tune | RW | 2 | FLOAT [-360...360] (Hi-16bits)
9678 |  |  |  | HR9677 (Lo-16bits)
9679 | GSYN:Start Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9680 |  |  |  | HR9679 (Lo-16bits)
9681 | GSYN:Stop Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9682 |  |  |  | HR9681 (Lo-16bits)
9683 | GSYN:Block and Interrupt Synchronizing | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9684 |  |  |  | HR9683 (Lo-16bits)
9685 | GSYN:Breaker Closed | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9686 |  |  |  | HR9685 (Lo-16bits)
9687 | GSYN:Manual increase voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9688 |  |  |  | HR9687 (Lo-16bits)
9689 | GSYN:Manual decrease voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9690 |  |  |  | HR9689 (Lo-16bits)
9691 | GSYN:Manual increase frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9692 |  |  |  | HR9691 (Lo-16bits)
9693 | GSYN:Manual decrease frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9694 |  |  |  | HR9693 (Lo-16bits)
9695 | GSYN:Manual Close Breaker | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9696 |  |  |  | HR9695 (Lo-16bits)
9697 | GSYN:GSYN Voltage Mag.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9698 |  |  |  | HR9697 (Lo-16bits)
9699 | GSYN:GSYN Voltage Freq.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9700 |  |  |  | HR9699 (Lo-16bits)
9701 | GSYN:GSYN Voltage Ang.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9702 |  |  |  | HR9701 (Lo-16bits)
9703 | GSYN:GSYN Blocked | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9704 |  |  |  | HR9703 (Lo-16bits)
9705 | GSYN:GSYN Running | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9706 |  |  |  | HR9705 (Lo-16bits)
9707 | GSYN:GSYN Increase Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9708 |  |  |  | HR9707 (Lo-16bits)
9709 | GSYN:GSYN Decrease Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9710 |  |  |  | HR9709 (Lo-16bits)
9711 | GSYN:GSYN Increase Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9712 |  |  |  | HR9711 (Lo-16bits)
9713 | GSYN:GSYN Decrease Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9714 |  |  |  | HR9713 (Lo-16bits)
9715 | GSYN:GSYN Breaker Close Pulse | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9716 |  |  |  | HR9715 (Lo-16bits)
9717 | GSYN:GSYN Long Sync Time | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9718 |  |  |  | HR9717 (Lo-16bits)
9719 | GSYN:GSYN Nets Standstill | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9720 |  |  |  | HR9719 (Lo-16bits)
9721 | GSYN:GSYN Nets Departing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9722 |  |  |  | HR9721 (Lo-16bits)
9723 | GSYN:GSYN Nets Enclosing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9724 |  |  |  | HR9723 (Lo-16bits)
9725 | VREC:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9726 | VREC:Scale current values to primary | RW | 1 | 0=No;1=Yes
9727 | VREC:Record fault types (Overcurrrent & Voltage Over/Under) faults | RW | 1 | 0=No;1=Yes
9728 | VREC:Trigger register to memory | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9729 |  |  |  | HR9728 (Lo-16bits)
9730 | VREC:VREC Magnitude 1 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9731 |  |  |  | HR9730 (Lo-16bits)
9732 | VREC:VREC Magnitude 2 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9733 |  |  |  | HR9732 (Lo-16bits)
9734 | VREC:VREC Magnitude 3 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9735 |  |  |  | HR9734 (Lo-16bits)
9736 | VREC:VREC Magnitude 4 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9737 |  |  |  | HR9736 (Lo-16bits)
9738 | VREC:VREC Magnitude 5 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9739 |  |  |  | HR9738 (Lo-16bits)
9740 | VREC:VREC Magnitude 6 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9741 |  |  |  | HR9740 (Lo-16bits)
9742 | VREC:VREC Magnitude 7 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9743 |  |  |  | HR9742 (Lo-16bits)
9744 | VREC:VREC Magnitude 8 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9745 |  |  |  | HR9744 (Lo-16bits)
9746 | RTB:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9747 | RTB:Scale current values to primary | RW | 1 | 0=No;1=Yes
9748 | RTB:RTS to bus Magnitude 1 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9749 |  |  |  | HR9748 (Lo-16bits)
9750 | RTB:RTS to bus Magnitude 2 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9751 |  |  |  | HR9750 (Lo-16bits)
9752 | RTB:RTS to bus Magnitude 3 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9753 |  |  |  | HR9752 (Lo-16bits)
9754 | RTB:RTS to bus Magnitude 4 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9755 |  |  |  | HR9754 (Lo-16bits)
9756 | RTB:RTS to bus Magnitude 5 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9757 |  |  |  | HR9756 (Lo-16bits)
9758 | RTB:RTS to bus Magnitude 6 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9759 |  |  |  | HR9758 (Lo-16bits)
9760 | RTB:RTS to bus Magnitude 7 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9761 |  |  |  | HR9760 (Lo-16bits)
9762 | RTB:RTS to bus Magnitude 8 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9763 |  |  |  | HR9762 (Lo-16bits)
9764 | RTB:RTS to bus Magnitude 9 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9765 |  |  |  | HR9764 (Lo-16bits)
9766 | RTB:RTS to bus Magnitude 10 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9767 |  |  |  | HR9766 (Lo-16bits)
9768 | AOUT:mA In Channel 1 | R | 2 | FLOAT [0...24] (Hi-16bits)
9769 |  |  |  | HR9768 (Lo-16bits)
9770 | AOUT:mA In Channel 2 | R | 2 | FLOAT [0...24] (Hi-16bits)
9771 |  |  |  | HR9770 (Lo-16bits)
9772 | AOUT:mA Out Channel 1 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9773 |  |  |  | HR9772 (Lo-16bits)
9774 | AOUT:mA Out Channel 1 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9775 |  |  |  | HR9774 (Lo-16bits)
9776 | AOUT:mA Out Channel 2 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9777 |  |  |  | HR9776 (Lo-16bits)
9778 | AOUT:mA Out Channel 2 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9779 |  |  |  | HR9778 (Lo-16bits)
9780 | AOUT:mA Out Channel 3 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9781 |  |  |  | HR9780 (Lo-16bits)
9782 | AOUT:mA Out Channel 3 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9783 |  |  |  | HR9782 (Lo-16bits)
9784 | AOUT:mA Out Channel 4 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9785 |  |  |  | HR9784 (Lo-16bits)
9786 | AOUT:mA Out Channel 4 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9787 |  |  |  | HR9786 (Lo-16bits)
9788 | AOUT:mA Out Channel 5 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9789 |  |  |  | HR9788 (Lo-16bits)
9790 | AOUT:mA Out Channel 5 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9791 |  |  |  | HR9790 (Lo-16bits)
9792 | AOUT:mA Out Channel 6 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9793 |  |  |  | HR9792 (Lo-16bits)
9794 | AOUT:mA Out Channel 6 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9795 |  |  |  | HR9794 (Lo-16bits)
9796 | AOUT:mA Out Channel 7 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9797 |  |  |  | HR9796 (Lo-16bits)
9798 | AOUT:mA Out Channel 7 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9799 |  |  |  | HR9798 (Lo-16bits)
9800 | AOUT:mA Out Channel 8 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9801 |  |  |  | HR9800 (Lo-16bits)
9802 | AOUT:mA Out Channel 8 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9803 |  |  |  | HR9802 (Lo-16bits)
9906 | Object6 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9907 | Object7 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9908 | Object8 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9909 | Object9 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9910 | Object10 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020

## AQ-T215 & AQ-T216, v2.1.1.3-247
HR | Parameter | Access | Length | Info
1 | Modbus requests | R/W=0 | 1 | Diagnostic request counter
2 | Modbus quality | R | 1 | Diagnostic quality
3 | Modbus errors | R/W=0 | 1 | Diagnostic error counter
4 | Modbus Ctrl OK | R/W=0 | 1 | Diagnostic Control OK counter
5 | Modbus Ctrl Errors | R/W=0 | 1 | Diagnostic Control Error counter
6 | Object1 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
7 | Object2 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
8 | Object3 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9 | Object4 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
10 | Object5 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
11 | Previous Event register | R | 6 | Event code
12 | Previous Event register | R | 6 | Event timestamp (ms)
13 | Previous Event register | R | 6 | Event timestamp (sec Hi-16bits)
14 | Previous Event register | R | 6 | Event timestamp (sec Lo-16bits)
15 | Previous Event register | R | 6 | Event sequential index
16 | Previous Event register | R | 6 | RESERVED
17 | Event register | R | 6 | Event code
18 | Event register | R | 6 | Event timestamp (ms)
19 | Event register | R | 6 | Event timestamp (sec Hi-16bits)
20 | Event register | R | 6 | Event timestamp (sec Lo-16bits)
21 | Event register | R | 6 | Event sequential index
22 | Event register | R | 6 | RESERVED
23 | System time | RW | 3 | System time (ms)
24 | System time | RW | 3 | System time (sec Hi-16bits)
25 | System time | RW | 3 | System time (sec Lo-16bits)
26 | MEAS1:Pri.Pha.curr.IL1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
27 |  |  |  | HR26 (Lo-16bits)
28 | MEAS1:Pri.Pha.curr.IL2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
29 |  |  |  | HR28 (Lo-16bits)
30 | MEAS1:Pri.Pha.curr.IL3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
31 |  |  |  | HR30 (Lo-16bits)
32 | MEAS1:Pri.Res.curr.I01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
33 |  |  |  | HR32 (Lo-16bits)
34 | MEAS1:Pri.Res.curr.I02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
35 |  |  |  | HR34 (Lo-16bits)
36 | MEAS1:Pha.angle IL1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
37 |  |  |  | HR36 (Lo-16bits)
38 | MEAS1:Pha.angle IL2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
39 |  |  |  | HR38 (Lo-16bits)
40 | MEAS1:Pha.angle IL3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
41 |  |  |  | HR40 (Lo-16bits)
42 | MEAS1:Res.curr.angle I01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
43 |  |  |  | HR42 (Lo-16bits)
44 | MEAS1:Res.curr.angle I02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
45 |  |  |  | HR44 (Lo-16bits)
46 | MEAS1:Pri.calc.I0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
47 |  |  |  | HR46 (Lo-16bits)
48 | MEAS1:calc.I0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
49 |  |  |  | HR48 (Lo-16bits)
50 | MEAS1:Pha.curr.IL1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
51 |  |  |  | HR50 (Lo-16bits)
52 | MEAS1:Pha.curr.IL2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
53 |  |  |  | HR52 (Lo-16bits)
54 | MEAS1:Pha.curr.IL3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
55 |  |  |  | HR54 (Lo-16bits)
56 | MEAS1:Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
57 |  |  |  | HR56 (Lo-16bits)
58 | MEAS1:Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
59 |  |  |  | HR58 (Lo-16bits)
60 | MEAS1:Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
61 |  |  |  | HR60 (Lo-16bits)
62 | MEAS1:Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
63 |  |  |  | HR62 (Lo-16bits)
64 | MEAS1:Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
65 |  |  |  | HR64 (Lo-16bits)
66 | MEAS1:Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
67 |  |  |  | HR66 (Lo-16bits)
68 | MEAS1:Res.curr.I01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
69 |  |  |  | HR68 (Lo-16bits)
70 | MEAS1:Res.curr.I02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
71 |  |  |  | HR70 (Lo-16bits)
72 | MEAS1:Pha.L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
73 |  |  |  | HR72 (Lo-16bits)
74 | MEAS1:Pha.L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
75 |  |  |  | HR74 (Lo-16bits)
76 | MEAS1:Pha.L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
77 |  |  |  | HR76 (Lo-16bits)
78 | MEAS1:Pha.L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
79 |  |  |  | HR78 (Lo-16bits)
80 | MEAS1:Pha.L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
81 |  |  |  | HR80 (Lo-16bits)
82 | MEAS1:Pha.L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
83 |  |  |  | HR82 (Lo-16bits)
84 | MEAS1:Res.I01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
85 |  |  |  | HR84 (Lo-16bits)
86 | MEAS1:Res.I01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
87 |  |  |  | HR86 (Lo-16bits)
88 | MEAS1:Res.I02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
89 |  |  |  | HR88 (Lo-16bits)
90 | MEAS1:Res.I02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
91 |  |  |  | HR90 (Lo-16bits)
92 | MEAS1:P-P curr.IL1 | R | 2 | FLOAT [0...500] (Hi-16bits)
93 |  |  |  | HR92 (Lo-16bits)
94 | MEAS1:P-P curr.IL2 | R | 2 | FLOAT [0...500] (Hi-16bits)
95 |  |  |  | HR94 (Lo-16bits)
96 | MEAS1:P-P curr.IL3 | R | 2 | FLOAT [0...500] (Hi-16bits)
97 |  |  |  | HR96 (Lo-16bits)
98 | MEAS1:P-P curr.I01 | R | 2 | FLOAT [0...500] (Hi-16bits)
99 |  |  |  | HR98 (Lo-16bits)
100 | MEAS1:P-P curr.I02 | R | 2 | FLOAT [0...500] (Hi-16bits)
101 |  |  |  | HR100 (Lo-16bits)
102 | MEAS1:IL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
103 |  |  |  | HR102 (Lo-16bits)
104 | MEAS1:IL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
105 |  |  |  | HR104 (Lo-16bits)
106 | MEAS1:IL1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
107 |  |  |  | HR106 (Lo-16bits)
108 | MEAS1:IL1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
109 |  |  |  | HR108 (Lo-16bits)
110 | MEAS1:IL1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
111 |  |  |  | HR110 (Lo-16bits)
112 | MEAS1:IL1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
113 |  |  |  | HR112 (Lo-16bits)
114 | MEAS1:IL1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
115 |  |  |  | HR114 (Lo-16bits)
116 | MEAS1:IL1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
117 |  |  |  | HR116 (Lo-16bits)
118 | MEAS1:IL1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
119 |  |  |  | HR118 (Lo-16bits)
120 | MEAS1:IL1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
121 |  |  |  | HR120 (Lo-16bits)
122 | MEAS1:IL1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
123 |  |  |  | HR122 (Lo-16bits)
124 | MEAS1:IL1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
125 |  |  |  | HR124 (Lo-16bits)
126 | MEAS1:IL1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
127 |  |  |  | HR126 (Lo-16bits)
128 | MEAS1:IL1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
129 |  |  |  | HR128 (Lo-16bits)
130 | MEAS1:IL1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
131 |  |  |  | HR130 (Lo-16bits)
132 | MEAS1:IL1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
133 |  |  |  | HR132 (Lo-16bits)
134 | MEAS1:IL1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
135 |  |  |  | HR134 (Lo-16bits)
136 | MEAS1:IL1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
137 |  |  |  | HR136 (Lo-16bits)
138 | MEAS1:IL1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
139 |  |  |  | HR138 (Lo-16bits)
140 | MEAS1:IL1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
141 |  |  |  | HR140 (Lo-16bits)
142 | MEAS1:IL1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
143 |  |  |  | HR142 (Lo-16bits)
144 | MEAS1:IL1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
145 |  |  |  | HR144 (Lo-16bits)
146 | MEAS1:IL1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
147 |  |  |  | HR146 (Lo-16bits)
148 | MEAS1:IL1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
149 |  |  |  | HR148 (Lo-16bits)
150 | MEAS1:IL1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
151 |  |  |  | HR150 (Lo-16bits)
152 | MEAS1:IL1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
153 |  |  |  | HR152 (Lo-16bits)
154 | MEAS1:IL1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
155 |  |  |  | HR154 (Lo-16bits)
156 | MEAS1:IL1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
157 |  |  |  | HR156 (Lo-16bits)
158 | MEAS1:IL1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
159 |  |  |  | HR158 (Lo-16bits)
160 | MEAS1:IL1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
161 |  |  |  | HR160 (Lo-16bits)
162 | MEAS1:IL1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
163 |  |  |  | HR162 (Lo-16bits)
164 | MEAS1:IL1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
165 |  |  |  | HR164 (Lo-16bits)
166 | MEAS1:IL1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
167 |  |  |  | HR166 (Lo-16bits)
168 | MEAS1:IL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
169 |  |  |  | HR168 (Lo-16bits)
170 | MEAS1:IL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
171 |  |  |  | HR170 (Lo-16bits)
172 | MEAS1:IL2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
173 |  |  |  | HR172 (Lo-16bits)
174 | MEAS1:IL2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
175 |  |  |  | HR174 (Lo-16bits)
176 | MEAS1:IL2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
177 |  |  |  | HR176 (Lo-16bits)
178 | MEAS1:IL2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
179 |  |  |  | HR178 (Lo-16bits)
180 | MEAS1:IL2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
181 |  |  |  | HR180 (Lo-16bits)
182 | MEAS1:IL2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
183 |  |  |  | HR182 (Lo-16bits)
184 | MEAS1:IL2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
185 |  |  |  | HR184 (Lo-16bits)
186 | MEAS1:IL2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
187 |  |  |  | HR186 (Lo-16bits)
188 | MEAS1:IL2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
189 |  |  |  | HR188 (Lo-16bits)
190 | MEAS1:IL2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
191 |  |  |  | HR190 (Lo-16bits)
192 | MEAS1:IL2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
193 |  |  |  | HR192 (Lo-16bits)
194 | MEAS1:IL2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
195 |  |  |  | HR194 (Lo-16bits)
196 | MEAS1:IL2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
197 |  |  |  | HR196 (Lo-16bits)
198 | MEAS1:IL2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
199 |  |  |  | HR198 (Lo-16bits)
200 | MEAS1:IL2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
201 |  |  |  | HR200 (Lo-16bits)
202 | MEAS1:IL2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
203 |  |  |  | HR202 (Lo-16bits)
204 | MEAS1:IL2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
205 |  |  |  | HR204 (Lo-16bits)
206 | MEAS1:IL2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
207 |  |  |  | HR206 (Lo-16bits)
208 | MEAS1:IL2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
209 |  |  |  | HR208 (Lo-16bits)
210 | MEAS1:IL2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
211 |  |  |  | HR210 (Lo-16bits)
212 | MEAS1:IL2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
213 |  |  |  | HR212 (Lo-16bits)
214 | MEAS1:IL2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
215 |  |  |  | HR214 (Lo-16bits)
216 | MEAS1:IL2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
217 |  |  |  | HR216 (Lo-16bits)
218 | MEAS1:IL2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
219 |  |  |  | HR218 (Lo-16bits)
220 | MEAS1:IL2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
221 |  |  |  | HR220 (Lo-16bits)
222 | MEAS1:IL2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
223 |  |  |  | HR222 (Lo-16bits)
224 | MEAS1:IL2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
225 |  |  |  | HR224 (Lo-16bits)
226 | MEAS1:IL2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
227 |  |  |  | HR226 (Lo-16bits)
228 | MEAS1:IL2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
229 |  |  |  | HR228 (Lo-16bits)
230 | MEAS1:IL2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
231 |  |  |  | HR230 (Lo-16bits)
232 | MEAS1:IL2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
233 |  |  |  | HR232 (Lo-16bits)
234 | MEAS1:IL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
235 |  |  |  | HR234 (Lo-16bits)
236 | MEAS1:IL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
237 |  |  |  | HR236 (Lo-16bits)
238 | MEAS1:IL3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
239 |  |  |  | HR238 (Lo-16bits)
240 | MEAS1:IL3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
241 |  |  |  | HR240 (Lo-16bits)
242 | MEAS1:IL3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
243 |  |  |  | HR242 (Lo-16bits)
244 | MEAS1:IL3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
245 |  |  |  | HR244 (Lo-16bits)
246 | MEAS1:IL3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
247 |  |  |  | HR246 (Lo-16bits)
248 | MEAS1:IL3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
249 |  |  |  | HR248 (Lo-16bits)
250 | MEAS1:IL3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
251 |  |  |  | HR250 (Lo-16bits)
252 | MEAS1:IL3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
253 |  |  |  | HR252 (Lo-16bits)
254 | MEAS1:IL3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
255 |  |  |  | HR254 (Lo-16bits)
256 | MEAS1:IL3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
257 |  |  |  | HR256 (Lo-16bits)
258 | MEAS1:IL3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
259 |  |  |  | HR258 (Lo-16bits)
260 | MEAS1:IL3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
261 |  |  |  | HR260 (Lo-16bits)
262 | MEAS1:IL3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
263 |  |  |  | HR262 (Lo-16bits)
264 | MEAS1:IL3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
265 |  |  |  | HR264 (Lo-16bits)
266 | MEAS1:IL3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
267 |  |  |  | HR266 (Lo-16bits)
268 | MEAS1:IL3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
269 |  |  |  | HR268 (Lo-16bits)
270 | MEAS1:IL3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
271 |  |  |  | HR270 (Lo-16bits)
272 | MEAS1:IL3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
273 |  |  |  | HR272 (Lo-16bits)
274 | MEAS1:IL3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
275 |  |  |  | HR274 (Lo-16bits)
276 | MEAS1:IL3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
277 |  |  |  | HR276 (Lo-16bits)
278 | MEAS1:IL3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
279 |  |  |  | HR278 (Lo-16bits)
280 | MEAS1:IL3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
281 |  |  |  | HR280 (Lo-16bits)
282 | MEAS1:IL3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
283 |  |  |  | HR282 (Lo-16bits)
284 | MEAS1:IL3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
285 |  |  |  | HR284 (Lo-16bits)
286 | MEAS1:IL3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
287 |  |  |  | HR286 (Lo-16bits)
288 | MEAS1:IL3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
289 |  |  |  | HR288 (Lo-16bits)
290 | MEAS1:IL3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
291 |  |  |  | HR290 (Lo-16bits)
292 | MEAS1:IL3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
293 |  |  |  | HR292 (Lo-16bits)
294 | MEAS1:IL3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
295 |  |  |  | HR294 (Lo-16bits)
296 | MEAS1:IL3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
297 |  |  |  | HR296 (Lo-16bits)
298 | MEAS1:IL3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
299 |  |  |  | HR298 (Lo-16bits)
300 | MEAS1:I01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
301 |  |  |  | HR300 (Lo-16bits)
302 | MEAS1:I01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
303 |  |  |  | HR302 (Lo-16bits)
304 | MEAS1:I01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
305 |  |  |  | HR304 (Lo-16bits)
306 | MEAS1:I01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
307 |  |  |  | HR306 (Lo-16bits)
308 | MEAS1:I01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
309 |  |  |  | HR308 (Lo-16bits)
310 | MEAS1:I01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
311 |  |  |  | HR310 (Lo-16bits)
312 | MEAS1:I01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
313 |  |  |  | HR312 (Lo-16bits)
314 | MEAS1:I01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
315 |  |  |  | HR314 (Lo-16bits)
316 | MEAS1:I01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
317 |  |  |  | HR316 (Lo-16bits)
318 | MEAS1:I01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
319 |  |  |  | HR318 (Lo-16bits)
320 | MEAS1:I01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
321 |  |  |  | HR320 (Lo-16bits)
322 | MEAS1:I01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
323 |  |  |  | HR322 (Lo-16bits)
324 | MEAS1:I01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
325 |  |  |  | HR324 (Lo-16bits)
326 | MEAS1:I01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
327 |  |  |  | HR326 (Lo-16bits)
328 | MEAS1:I01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
329 |  |  |  | HR328 (Lo-16bits)
330 | MEAS1:I01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
331 |  |  |  | HR330 (Lo-16bits)
332 | MEAS1:I01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
333 |  |  |  | HR332 (Lo-16bits)
334 | MEAS1:I01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
335 |  |  |  | HR334 (Lo-16bits)
336 | MEAS1:I01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
337 |  |  |  | HR336 (Lo-16bits)
338 | MEAS1:I01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
339 |  |  |  | HR338 (Lo-16bits)
340 | MEAS1:I01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
341 |  |  |  | HR340 (Lo-16bits)
342 | MEAS1:I01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
343 |  |  |  | HR342 (Lo-16bits)
344 | MEAS1:I01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
345 |  |  |  | HR344 (Lo-16bits)
346 | MEAS1:I01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
347 |  |  |  | HR346 (Lo-16bits)
348 | MEAS1:I01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
349 |  |  |  | HR348 (Lo-16bits)
350 | MEAS1:I01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
351 |  |  |  | HR350 (Lo-16bits)
352 | MEAS1:I01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
353 |  |  |  | HR352 (Lo-16bits)
354 | MEAS1:I01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
355 |  |  |  | HR354 (Lo-16bits)
356 | MEAS1:I01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
357 |  |  |  | HR356 (Lo-16bits)
358 | MEAS1:I01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
359 |  |  |  | HR358 (Lo-16bits)
360 | MEAS1:I01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
361 |  |  |  | HR360 (Lo-16bits)
362 | MEAS1:I01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
363 |  |  |  | HR362 (Lo-16bits)
364 | MEAS1:I01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
365 |  |  |  | HR364 (Lo-16bits)
366 | MEAS1:I02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
367 |  |  |  | HR366 (Lo-16bits)
368 | MEAS1:I02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
369 |  |  |  | HR368 (Lo-16bits)
370 | MEAS1:I02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
371 |  |  |  | HR370 (Lo-16bits)
372 | MEAS1:I02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
373 |  |  |  | HR372 (Lo-16bits)
374 | MEAS1:I02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
375 |  |  |  | HR374 (Lo-16bits)
376 | MEAS1:I02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
377 |  |  |  | HR376 (Lo-16bits)
378 | MEAS1:I02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
379 |  |  |  | HR378 (Lo-16bits)
380 | MEAS1:I02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
381 |  |  |  | HR380 (Lo-16bits)
382 | MEAS1:I02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
383 |  |  |  | HR382 (Lo-16bits)
384 | MEAS1:I02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
385 |  |  |  | HR384 (Lo-16bits)
386 | MEAS1:I02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
387 |  |  |  | HR386 (Lo-16bits)
388 | MEAS1:I02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
389 |  |  |  | HR388 (Lo-16bits)
390 | MEAS1:I02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
391 |  |  |  | HR390 (Lo-16bits)
392 | MEAS1:I02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
393 |  |  |  | HR392 (Lo-16bits)
394 | MEAS1:I02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
395 |  |  |  | HR394 (Lo-16bits)
396 | MEAS1:I02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
397 |  |  |  | HR396 (Lo-16bits)
398 | MEAS1:I02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
399 |  |  |  | HR398 (Lo-16bits)
400 | MEAS1:I02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
401 |  |  |  | HR400 (Lo-16bits)
402 | MEAS1:I02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
403 |  |  |  | HR402 (Lo-16bits)
404 | MEAS1:I02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
405 |  |  |  | HR404 (Lo-16bits)
406 | MEAS1:I02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
407 |  |  |  | HR406 (Lo-16bits)
408 | MEAS1:I02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
409 |  |  |  | HR408 (Lo-16bits)
410 | MEAS1:I02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
411 |  |  |  | HR410 (Lo-16bits)
412 | MEAS1:I02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
413 |  |  |  | HR412 (Lo-16bits)
414 | MEAS1:I02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
415 |  |  |  | HR414 (Lo-16bits)
416 | MEAS1:I02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
417 |  |  |  | HR416 (Lo-16bits)
418 | MEAS1:I02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
419 |  |  |  | HR418 (Lo-16bits)
420 | MEAS1:I02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
421 |  |  |  | HR420 (Lo-16bits)
422 | MEAS1:I02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
423 |  |  |  | HR422 (Lo-16bits)
424 | MEAS1:I02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
425 |  |  |  | HR424 (Lo-16bits)
426 | MEAS1:I02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
427 |  |  |  | HR426 (Lo-16bits)
428 | MEAS1:I02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
429 |  |  |  | HR428 (Lo-16bits)
430 | MEAS1:I02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
431 |  |  |  | HR430 (Lo-16bits)
432 | MEAS1:Meas1 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
433 |  |  |  | HR432 (Lo-16bits)
434 | MEAS2:Pri.Pha.curr.I''L1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
435 |  |  |  | HR434 (Lo-16bits)
436 | MEAS2:Pri.Pha.curr.I''L2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
437 |  |  |  | HR436 (Lo-16bits)
438 | MEAS2:Pri.Pha.curr.I''L3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
439 |  |  |  | HR438 (Lo-16bits)
440 | MEAS2:Pha.angle I''L1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
441 |  |  |  | HR440 (Lo-16bits)
442 | MEAS2:Pha.angle I''L2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
443 |  |  |  | HR442 (Lo-16bits)
444 | MEAS2:Pha.angle I''L3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
445 |  |  |  | HR444 (Lo-16bits)
446 | MEAS2:Pri.Res.curr.I''01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
447 |  |  |  | HR446 (Lo-16bits)
448 | MEAS2:Res.curr.angle I''01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
449 |  |  |  | HR448 (Lo-16bits)
450 | MEAS2:Pri.Res.curr.I''02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
451 |  |  |  | HR450 (Lo-16bits)
452 | MEAS2:Res.curr.angle I''02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
453 |  |  |  | HR452 (Lo-16bits)
454 | MEAS2:Pri.calc.I''0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
455 |  |  |  | HR454 (Lo-16bits)
456 | MEAS2:calc.I''0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
457 |  |  |  | HR456 (Lo-16bits)
458 | MEAS2:Pha.curr.I''L1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
459 |  |  |  | HR458 (Lo-16bits)
460 | MEAS2:Pha.curr.I''L2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
461 |  |  |  | HR460 (Lo-16bits)
462 | MEAS2:Pha.curr.I''L3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
463 |  |  |  | HR462 (Lo-16bits)
464 | MEAS2:I'' Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
465 |  |  |  | HR464 (Lo-16bits)
466 | MEAS2:I'' Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
467 |  |  |  | HR466 (Lo-16bits)
468 | MEAS2:I'' Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
469 |  |  |  | HR468 (Lo-16bits)
470 | MEAS2:I'' Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
471 |  |  |  | HR470 (Lo-16bits)
472 | MEAS2:I'' Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
473 |  |  |  | HR472 (Lo-16bits)
474 | MEAS2:I'' Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
475 |  |  |  | HR474 (Lo-16bits)
476 | MEAS2:Res.curr.I''01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
477 |  |  |  | HR476 (Lo-16bits)
478 | MEAS2:Res.curr.I''02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
479 |  |  |  | HR478 (Lo-16bits)
480 | MEAS2:Pha.I''L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
481 |  |  |  | HR480 (Lo-16bits)
482 | MEAS2:Pha.I''L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
483 |  |  |  | HR482 (Lo-16bits)
484 | MEAS2:Pha.I''L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
485 |  |  |  | HR484 (Lo-16bits)
486 | MEAS2:Pha.I''L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
487 |  |  |  | HR486 (Lo-16bits)
488 | MEAS2:Pha.I''L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
489 |  |  |  | HR488 (Lo-16bits)
490 | MEAS2:Pha.I''L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
491 |  |  |  | HR490 (Lo-16bits)
492 | MEAS2:Res.I''01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
493 |  |  |  | HR492 (Lo-16bits)
494 | MEAS2:Res.I''01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
495 |  |  |  | HR494 (Lo-16bits)
496 | MEAS2:Res.I''02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
497 |  |  |  | HR496 (Lo-16bits)
498 | MEAS2:Res.I''02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
499 |  |  |  | HR498 (Lo-16bits)
500 | MEAS2:P-P curr.I''L1 | R | 2 | FLOAT [0...500] (Hi-16bits)
501 |  |  |  | HR500 (Lo-16bits)
502 | MEAS2:P-P curr.I''L2 | R | 2 | FLOAT [0...500] (Hi-16bits)
503 |  |  |  | HR502 (Lo-16bits)
504 | MEAS2:P-P curr.I''L3 | R | 2 | FLOAT [0...500] (Hi-16bits)
505 |  |  |  | HR504 (Lo-16bits)
506 | MEAS2:P-P curr.I''01 | R | 2 | FLOAT [0...500] (Hi-16bits)
507 |  |  |  | HR506 (Lo-16bits)
508 | MEAS2:P-P curr.I''02 | R | 2 | FLOAT [0...500] (Hi-16bits)
509 |  |  |  | HR508 (Lo-16bits)
510 | MEAS2:I''L1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
511 |  |  |  | HR510 (Lo-16bits)
512 | MEAS2:I''L1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
513 |  |  |  | HR512 (Lo-16bits)
514 | MEAS2:I''L1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
515 |  |  |  | HR514 (Lo-16bits)
516 | MEAS2:I''L1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
517 |  |  |  | HR516 (Lo-16bits)
518 | MEAS2:I''L1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
519 |  |  |  | HR518 (Lo-16bits)
520 | MEAS2:I''L1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
521 |  |  |  | HR520 (Lo-16bits)
522 | MEAS2:I''L1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
523 |  |  |  | HR522 (Lo-16bits)
524 | MEAS2:I''L1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
525 |  |  |  | HR524 (Lo-16bits)
526 | MEAS2:I''L1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
527 |  |  |  | HR526 (Lo-16bits)
528 | MEAS2:I''L1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
529 |  |  |  | HR528 (Lo-16bits)
530 | MEAS2:I''L1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
531 |  |  |  | HR530 (Lo-16bits)
532 | MEAS2:I''L1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
533 |  |  |  | HR532 (Lo-16bits)
534 | MEAS2:I''L1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
535 |  |  |  | HR534 (Lo-16bits)
536 | MEAS2:I''L1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
537 |  |  |  | HR536 (Lo-16bits)
538 | MEAS2:I''L1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
539 |  |  |  | HR538 (Lo-16bits)
540 | MEAS2:I''L1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
541 |  |  |  | HR540 (Lo-16bits)
542 | MEAS2:I''L1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
543 |  |  |  | HR542 (Lo-16bits)
544 | MEAS2:I''L1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
545 |  |  |  | HR544 (Lo-16bits)
546 | MEAS2:I''L1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
547 |  |  |  | HR546 (Lo-16bits)
548 | MEAS2:I''L1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
549 |  |  |  | HR548 (Lo-16bits)
550 | MEAS2:I''L1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
551 |  |  |  | HR550 (Lo-16bits)
552 | MEAS2:I''L1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
553 |  |  |  | HR552 (Lo-16bits)
554 | MEAS2:I''L1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
555 |  |  |  | HR554 (Lo-16bits)
556 | MEAS2:I''L1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
557 |  |  |  | HR556 (Lo-16bits)
558 | MEAS2:I''L1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
559 |  |  |  | HR558 (Lo-16bits)
560 | MEAS2:I''L1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
561 |  |  |  | HR560 (Lo-16bits)
562 | MEAS2:I''L1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
563 |  |  |  | HR562 (Lo-16bits)
564 | MEAS2:I''L1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
565 |  |  |  | HR564 (Lo-16bits)
566 | MEAS2:I''L1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
567 |  |  |  | HR566 (Lo-16bits)
568 | MEAS2:I''L1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
569 |  |  |  | HR568 (Lo-16bits)
570 | MEAS2:I''L1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
571 |  |  |  | HR570 (Lo-16bits)
572 | MEAS2:I''L1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
573 |  |  |  | HR572 (Lo-16bits)
574 | MEAS2:I''L1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
575 |  |  |  | HR574 (Lo-16bits)
576 | MEAS2:I''L2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
577 |  |  |  | HR576 (Lo-16bits)
578 | MEAS2:I''L2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
579 |  |  |  | HR578 (Lo-16bits)
580 | MEAS2:I''L2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
581 |  |  |  | HR580 (Lo-16bits)
582 | MEAS2:I''L2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
583 |  |  |  | HR582 (Lo-16bits)
584 | MEAS2:I''L2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
585 |  |  |  | HR584 (Lo-16bits)
586 | MEAS2:I''L2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
587 |  |  |  | HR586 (Lo-16bits)
588 | MEAS2:I''L2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
589 |  |  |  | HR588 (Lo-16bits)
590 | MEAS2:I''L2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
591 |  |  |  | HR590 (Lo-16bits)
592 | MEAS2:I''L2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
593 |  |  |  | HR592 (Lo-16bits)
594 | MEAS2:I''L2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
595 |  |  |  | HR594 (Lo-16bits)
596 | MEAS2:I''L2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
597 |  |  |  | HR596 (Lo-16bits)
598 | MEAS2:I''L2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
599 |  |  |  | HR598 (Lo-16bits)
600 | MEAS2:I''L2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
601 |  |  |  | HR600 (Lo-16bits)
602 | MEAS2:I''L2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
603 |  |  |  | HR602 (Lo-16bits)
604 | MEAS2:I''L2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
605 |  |  |  | HR604 (Lo-16bits)
606 | MEAS2:I''L2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
607 |  |  |  | HR606 (Lo-16bits)
608 | MEAS2:I''L2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
609 |  |  |  | HR608 (Lo-16bits)
610 | MEAS2:I''L2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
611 |  |  |  | HR610 (Lo-16bits)
612 | MEAS2:I''L2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
613 |  |  |  | HR612 (Lo-16bits)
614 | MEAS2:I''L2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
615 |  |  |  | HR614 (Lo-16bits)
616 | MEAS2:I''L2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
617 |  |  |  | HR616 (Lo-16bits)
618 | MEAS2:I''L2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
619 |  |  |  | HR618 (Lo-16bits)
620 | MEAS2:I''L2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
621 |  |  |  | HR620 (Lo-16bits)
622 | MEAS2:I''L2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
623 |  |  |  | HR622 (Lo-16bits)
624 | MEAS2:I''L2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
625 |  |  |  | HR624 (Lo-16bits)
626 | MEAS2:I''L2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
627 |  |  |  | HR626 (Lo-16bits)
628 | MEAS2:I''L2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
629 |  |  |  | HR628 (Lo-16bits)
630 | MEAS2:I''L2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
631 |  |  |  | HR630 (Lo-16bits)
632 | MEAS2:I''L2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
633 |  |  |  | HR632 (Lo-16bits)
634 | MEAS2:I''L2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
635 |  |  |  | HR634 (Lo-16bits)
636 | MEAS2:I''L2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
637 |  |  |  | HR636 (Lo-16bits)
638 | MEAS2:I''L2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
639 |  |  |  | HR638 (Lo-16bits)
640 | MEAS2:I''L2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
641 |  |  |  | HR640 (Lo-16bits)
642 | MEAS2:I''L3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
643 |  |  |  | HR642 (Lo-16bits)
644 | MEAS2:I''L3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
645 |  |  |  | HR644 (Lo-16bits)
646 | MEAS2:I''L3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
647 |  |  |  | HR646 (Lo-16bits)
648 | MEAS2:I''L3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
649 |  |  |  | HR648 (Lo-16bits)
650 | MEAS2:I''L3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
651 |  |  |  | HR650 (Lo-16bits)
652 | MEAS2:I''L3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
653 |  |  |  | HR652 (Lo-16bits)
654 | MEAS2:I''L3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
655 |  |  |  | HR654 (Lo-16bits)
656 | MEAS2:I''L3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
657 |  |  |  | HR656 (Lo-16bits)
658 | MEAS2:I''L3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
659 |  |  |  | HR658 (Lo-16bits)
660 | MEAS2:I''L3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
661 |  |  |  | HR660 (Lo-16bits)
662 | MEAS2:I''L3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
663 |  |  |  | HR662 (Lo-16bits)
664 | MEAS2:I''L3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
665 |  |  |  | HR664 (Lo-16bits)
666 | MEAS2:I''L3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
667 |  |  |  | HR666 (Lo-16bits)
668 | MEAS2:I''L3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
669 |  |  |  | HR668 (Lo-16bits)
670 | MEAS2:I''L3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
671 |  |  |  | HR670 (Lo-16bits)
672 | MEAS2:I''L3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
673 |  |  |  | HR672 (Lo-16bits)
674 | MEAS2:I''L3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
675 |  |  |  | HR674 (Lo-16bits)
676 | MEAS2:I''L3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
677 |  |  |  | HR676 (Lo-16bits)
678 | MEAS2:I''L3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
679 |  |  |  | HR678 (Lo-16bits)
680 | MEAS2:I''L3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
681 |  |  |  | HR680 (Lo-16bits)
682 | MEAS2:I''L3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
683 |  |  |  | HR682 (Lo-16bits)
684 | MEAS2:I''L3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
685 |  |  |  | HR684 (Lo-16bits)
686 | MEAS2:I''L3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
687 |  |  |  | HR686 (Lo-16bits)
688 | MEAS2:I''L3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
689 |  |  |  | HR688 (Lo-16bits)
690 | MEAS2:I''L3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
691 |  |  |  | HR690 (Lo-16bits)
692 | MEAS2:I''L3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
693 |  |  |  | HR692 (Lo-16bits)
694 | MEAS2:I''L3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
695 |  |  |  | HR694 (Lo-16bits)
696 | MEAS2:I''L3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
697 |  |  |  | HR696 (Lo-16bits)
698 | MEAS2:I''L3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
699 |  |  |  | HR698 (Lo-16bits)
700 | MEAS2:I''L3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
701 |  |  |  | HR700 (Lo-16bits)
702 | MEAS2:I''L3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
703 |  |  |  | HR702 (Lo-16bits)
704 | MEAS2:I''L3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
705 |  |  |  | HR704 (Lo-16bits)
706 | MEAS2:I''L3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
707 |  |  |  | HR706 (Lo-16bits)
708 | MEAS2:I''01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
709 |  |  |  | HR708 (Lo-16bits)
710 | MEAS2:I''01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
711 |  |  |  | HR710 (Lo-16bits)
712 | MEAS2:I''01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
713 |  |  |  | HR712 (Lo-16bits)
714 | MEAS2:I''01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
715 |  |  |  | HR714 (Lo-16bits)
716 | MEAS2:I''01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
717 |  |  |  | HR716 (Lo-16bits)
718 | MEAS2:I''01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
719 |  |  |  | HR718 (Lo-16bits)
720 | MEAS2:I''01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
721 |  |  |  | HR720 (Lo-16bits)
722 | MEAS2:I''01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
723 |  |  |  | HR722 (Lo-16bits)
724 | MEAS2:I''01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
725 |  |  |  | HR724 (Lo-16bits)
726 | MEAS2:I''01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
727 |  |  |  | HR726 (Lo-16bits)
728 | MEAS2:I''01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
729 |  |  |  | HR728 (Lo-16bits)
730 | MEAS2:I''01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
731 |  |  |  | HR730 (Lo-16bits)
732 | MEAS2:I''01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
733 |  |  |  | HR732 (Lo-16bits)
734 | MEAS2:I''01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
735 |  |  |  | HR734 (Lo-16bits)
736 | MEAS2:I''01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
737 |  |  |  | HR736 (Lo-16bits)
738 | MEAS2:I''01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
739 |  |  |  | HR738 (Lo-16bits)
740 | MEAS2:I''01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
741 |  |  |  | HR740 (Lo-16bits)
742 | MEAS2:I''01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
743 |  |  |  | HR742 (Lo-16bits)
744 | MEAS2:I''01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
745 |  |  |  | HR744 (Lo-16bits)
746 | MEAS2:I''01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
747 |  |  |  | HR746 (Lo-16bits)
748 | MEAS2:I''01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
749 |  |  |  | HR748 (Lo-16bits)
750 | MEAS2:I''01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
751 |  |  |  | HR750 (Lo-16bits)
752 | MEAS2:I''01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
753 |  |  |  | HR752 (Lo-16bits)
754 | MEAS2:I''01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
755 |  |  |  | HR754 (Lo-16bits)
756 | MEAS2:I''01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
757 |  |  |  | HR756 (Lo-16bits)
758 | MEAS2:I''01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
759 |  |  |  | HR758 (Lo-16bits)
760 | MEAS2:I''01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
761 |  |  |  | HR760 (Lo-16bits)
762 | MEAS2:I''01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
763 |  |  |  | HR762 (Lo-16bits)
764 | MEAS2:I''01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
765 |  |  |  | HR764 (Lo-16bits)
766 | MEAS2:I''01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
767 |  |  |  | HR766 (Lo-16bits)
768 | MEAS2:I''01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
769 |  |  |  | HR768 (Lo-16bits)
770 | MEAS2:I''01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
771 |  |  |  | HR770 (Lo-16bits)
772 | MEAS2:I''01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
773 |  |  |  | HR772 (Lo-16bits)
774 | MEAS2:I''02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
775 |  |  |  | HR774 (Lo-16bits)
776 | MEAS2:I''02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
777 |  |  |  | HR776 (Lo-16bits)
778 | MEAS2:I''02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
779 |  |  |  | HR778 (Lo-16bits)
780 | MEAS2:I''02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
781 |  |  |  | HR780 (Lo-16bits)
782 | MEAS2:I''02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
783 |  |  |  | HR782 (Lo-16bits)
784 | MEAS2:I''02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
785 |  |  |  | HR784 (Lo-16bits)
786 | MEAS2:I''02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
787 |  |  |  | HR786 (Lo-16bits)
788 | MEAS2:I''02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
789 |  |  |  | HR788 (Lo-16bits)
790 | MEAS2:I''02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
791 |  |  |  | HR790 (Lo-16bits)
792 | MEAS2:I''02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
793 |  |  |  | HR792 (Lo-16bits)
794 | MEAS2:I''02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
795 |  |  |  | HR794 (Lo-16bits)
796 | MEAS2:I''02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
797 |  |  |  | HR796 (Lo-16bits)
798 | MEAS2:I''02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
799 |  |  |  | HR798 (Lo-16bits)
800 | MEAS2:I''02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
801 |  |  |  | HR800 (Lo-16bits)
802 | MEAS2:I''02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
803 |  |  |  | HR802 (Lo-16bits)
804 | MEAS2:I''02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
805 |  |  |  | HR804 (Lo-16bits)
806 | MEAS2:I''02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
807 |  |  |  | HR806 (Lo-16bits)
808 | MEAS2:I''02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
809 |  |  |  | HR808 (Lo-16bits)
810 | MEAS2:I''02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
811 |  |  |  | HR810 (Lo-16bits)
812 | MEAS2:I''02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
813 |  |  |  | HR812 (Lo-16bits)
814 | MEAS2:I''02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
815 |  |  |  | HR814 (Lo-16bits)
816 | MEAS2:I''02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
817 |  |  |  | HR816 (Lo-16bits)
818 | MEAS2:I''02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
819 |  |  |  | HR818 (Lo-16bits)
820 | MEAS2:I''02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
821 |  |  |  | HR820 (Lo-16bits)
822 | MEAS2:I''02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
823 |  |  |  | HR822 (Lo-16bits)
824 | MEAS2:I''02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
825 |  |  |  | HR824 (Lo-16bits)
826 | MEAS2:I''02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
827 |  |  |  | HR826 (Lo-16bits)
828 | MEAS2:I''02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
829 |  |  |  | HR828 (Lo-16bits)
830 | MEAS2:I''02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
831 |  |  |  | HR830 (Lo-16bits)
832 | MEAS2:I''02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
833 |  |  |  | HR832 (Lo-16bits)
834 | MEAS2:I''02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
835 |  |  |  | HR834 (Lo-16bits)
836 | MEAS2:I''02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
837 |  |  |  | HR836 (Lo-16bits)
838 | MEAS2:I''02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
839 |  |  |  | HR838 (Lo-16bits)
840 | MEAS2:MEAS2 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
841 |  |  |  | HR840 (Lo-16bits)
842 | MEAS3:U1Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
843 |  |  |  | HR842 (Lo-16bits)
844 | MEAS3:U1Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
845 |  |  |  | HR844 (Lo-16bits)
846 | MEAS3:U2Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
847 |  |  |  | HR846 (Lo-16bits)
848 | MEAS3:U2Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
849 |  |  |  | HR848 (Lo-16bits)
850 | MEAS3:U3Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
851 |  |  |  | HR850 (Lo-16bits)
852 | MEAS3:U3Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
853 |  |  |  | HR852 (Lo-16bits)
854 | MEAS3:U4Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
855 |  |  |  | HR854 (Lo-16bits)
856 | MEAS3:U4Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
857 |  |  |  | HR856 (Lo-16bits)
858 | MEAS3:U1Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
859 |  |  |  | HR858 (Lo-16bits)
860 | MEAS3:U1Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
861 |  |  |  | HR860 (Lo-16bits)
862 | MEAS3:U2Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
863 |  |  |  | HR862 (Lo-16bits)
864 | MEAS3:U2Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
865 |  |  |  | HR864 (Lo-16bits)
866 | MEAS3:U3Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
867 |  |  |  | HR866 (Lo-16bits)
868 | MEAS3:U3Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
869 |  |  |  | HR868 (Lo-16bits)
870 | MEAS3:U4Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
871 |  |  |  | HR870 (Lo-16bits)
872 | MEAS3:U4Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
873 |  |  |  | HR872 (Lo-16bits)
874 | MEAS3:Pos.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
875 |  |  |  | HR874 (Lo-16bits)
876 | MEAS3:Pos.seq.Volt.sec | R | 2 | FLOAT [0...480] (Hi-16bits)
877 |  |  |  | HR876 (Lo-16bits)
878 | MEAS3:Neg.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
879 |  |  |  | HR878 (Lo-16bits)
880 | MEAS3:Neg.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
881 |  |  |  | HR880 (Lo-16bits)
882 | MEAS3:Zero.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
883 |  |  |  | HR882 (Lo-16bits)
884 | MEAS3:Zero.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
885 |  |  |  | HR884 (Lo-16bits)
886 | MEAS3:U0 Calc. pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
887 |  |  |  | HR886 (Lo-16bits)
888 | MEAS3:U0 Calc.Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
889 |  |  |  | HR888 (Lo-16bits)
890 | MEAS3:U1 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
891 |  |  |  | HR890 (Lo-16bits)
892 | MEAS3:U2 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
893 |  |  |  | HR892 (Lo-16bits)
894 | MEAS3:U3 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
895 |  |  |  | HR894 (Lo-16bits)
896 | MEAS3:U4 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
897 |  |  |  | HR896 (Lo-16bits)
898 | MEAS3:Pos.Seq volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
899 |  |  |  | HR898 (Lo-16bits)
900 | MEAS3:Neg.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
901 |  |  |  | HR900 (Lo-16bits)
902 | MEAS3:Zero.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
903 |  |  |  | HR902 (Lo-16bits)
904 | MEAS3:System volt UL12 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
905 |  |  |  | HR904 (Lo-16bits)
906 | MEAS3:System volt UL12 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
907 |  |  |  | HR906 (Lo-16bits)
908 | MEAS3:System volt UL12 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
909 |  |  |  | HR908 (Lo-16bits)
910 | MEAS3:System volt UL23 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
911 |  |  |  | HR910 (Lo-16bits)
912 | MEAS3:System volt UL23 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
913 |  |  |  | HR912 (Lo-16bits)
914 | MEAS3:System volt UL23 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
915 |  |  |  | HR914 (Lo-16bits)
916 | MEAS3:System volt UL31 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
917 |  |  |  | HR916 (Lo-16bits)
918 | MEAS3:System volt UL31 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
919 |  |  |  | HR918 (Lo-16bits)
920 | MEAS3:System volt UL31 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
921 |  |  |  | HR920 (Lo-16bits)
922 | MEAS3:System volt UL1 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
923 |  |  |  | HR922 (Lo-16bits)
924 | MEAS3:System volt UL1 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
925 |  |  |  | HR924 (Lo-16bits)
926 | MEAS3:System volt UL1 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
927 |  |  |  | HR926 (Lo-16bits)
928 | MEAS3:System volt UL2 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
929 |  |  |  | HR928 (Lo-16bits)
930 | MEAS3:System volt UL2 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
931 |  |  |  | HR930 (Lo-16bits)
932 | MEAS3:System volt UL2 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
933 |  |  |  | HR932 (Lo-16bits)
934 | MEAS3:System volt UL3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
935 |  |  |  | HR934 (Lo-16bits)
936 | MEAS3:System volt UL3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
937 |  |  |  | HR936 (Lo-16bits)
938 | MEAS3:System volt UL3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
939 |  |  |  | HR938 (Lo-16bits)
940 | MEAS3:System volt U0 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
941 |  |  |  | HR940 (Lo-16bits)
942 | MEAS3:System volt U0 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
943 |  |  |  | HR942 (Lo-16bits)
944 | MEAS3:System volt U0 mag(%) | R | 2 | FLOAT [0...120] (Hi-16bits)
945 |  |  |  | HR944 (Lo-16bits)
946 | MEAS3:System volt U0 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
947 |  |  |  | HR946 (Lo-16bits)
948 | MEAS3:System volt U3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
949 |  |  |  | HR948 (Lo-16bits)
950 | MEAS3:System volt U3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
951 |  |  |  | HR950 (Lo-16bits)
952 | MEAS3:System volt U3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
953 |  |  |  | HR952 (Lo-16bits)
954 | MEAS3:System volt U4 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
955 |  |  |  | HR954 (Lo-16bits)
956 | MEAS3:System volt U4 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
957 |  |  |  | HR956 (Lo-16bits)
958 | MEAS3:System volt U4 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
959 |  |  |  | HR958 (Lo-16bits)
960 | MEAS3:System volt UL1 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
961 |  |  |  | HR960 (Lo-16bits)
962 | MEAS3:System volt UL2 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
963 |  |  |  | HR962 (Lo-16bits)
964 | MEAS3:System volt UL3 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
965 |  |  |  | HR964 (Lo-16bits)
966 | MEAS3:UL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
967 |  |  |  | HR966 (Lo-16bits)
968 | MEAS3:UL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
969 |  |  |  | HR968 (Lo-16bits)
970 | MEAS3:UL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
971 |  |  |  | HR970 (Lo-16bits)
972 | MEAS3:UL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
973 |  |  |  | HR972 (Lo-16bits)
974 | MEAS3:UL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
975 |  |  |  | HR974 (Lo-16bits)
976 | MEAS3:UL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
977 |  |  |  | HR976 (Lo-16bits)
978 | MEAS3:U1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
979 |  |  |  | HR978 (Lo-16bits)
980 | MEAS3:U1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
981 |  |  |  | HR980 (Lo-16bits)
982 | MEAS3:U1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
983 |  |  |  | HR982 (Lo-16bits)
984 | MEAS3:U1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
985 |  |  |  | HR984 (Lo-16bits)
986 | MEAS3:U1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
987 |  |  |  | HR986 (Lo-16bits)
988 | MEAS3:U1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
989 |  |  |  | HR988 (Lo-16bits)
990 | MEAS3:U1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
991 |  |  |  | HR990 (Lo-16bits)
992 | MEAS3:U1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
993 |  |  |  | HR992 (Lo-16bits)
994 | MEAS3:U1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
995 |  |  |  | HR994 (Lo-16bits)
996 | MEAS3:U1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
997 |  |  |  | HR996 (Lo-16bits)
998 | MEAS3:U1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
999 |  |  |  | HR998 (Lo-16bits)
1000 | MEAS3:U1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1001 |  |  |  | HR1000 (Lo-16bits)
1002 | MEAS3:U1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1003 |  |  |  | HR1002 (Lo-16bits)
1004 | MEAS3:U1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1005 |  |  |  | HR1004 (Lo-16bits)
1006 | MEAS3:U1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1007 |  |  |  | HR1006 (Lo-16bits)
1008 | MEAS3:U1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1009 |  |  |  | HR1008 (Lo-16bits)
1010 | MEAS3:U1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1011 |  |  |  | HR1010 (Lo-16bits)
1012 | MEAS3:U1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1013 |  |  |  | HR1012 (Lo-16bits)
1014 | MEAS3:U1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1015 |  |  |  | HR1014 (Lo-16bits)
1016 | MEAS3:U1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1017 |  |  |  | HR1016 (Lo-16bits)
1018 | MEAS3:U1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1019 |  |  |  | HR1018 (Lo-16bits)
1020 | MEAS3:U1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1021 |  |  |  | HR1020 (Lo-16bits)
1022 | MEAS3:U1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1023 |  |  |  | HR1022 (Lo-16bits)
1024 | MEAS3:U1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1025 |  |  |  | HR1024 (Lo-16bits)
1026 | MEAS3:U1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1027 |  |  |  | HR1026 (Lo-16bits)
1028 | MEAS3:U1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1029 |  |  |  | HR1028 (Lo-16bits)
1030 | MEAS3:U1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1031 |  |  |  | HR1030 (Lo-16bits)
1032 | MEAS3:U1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1033 |  |  |  | HR1032 (Lo-16bits)
1034 | MEAS3:U1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1035 |  |  |  | HR1034 (Lo-16bits)
1036 | MEAS3:U1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1037 |  |  |  | HR1036 (Lo-16bits)
1038 | MEAS3:U1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1039 |  |  |  | HR1038 (Lo-16bits)
1040 | MEAS3:U2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1041 |  |  |  | HR1040 (Lo-16bits)
1042 | MEAS3:U2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1043 |  |  |  | HR1042 (Lo-16bits)
1044 | MEAS3:U2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1045 |  |  |  | HR1044 (Lo-16bits)
1046 | MEAS3:U2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1047 |  |  |  | HR1046 (Lo-16bits)
1048 | MEAS3:U2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1049 |  |  |  | HR1048 (Lo-16bits)
1050 | MEAS3:U2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1051 |  |  |  | HR1050 (Lo-16bits)
1052 | MEAS3:U2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1053 |  |  |  | HR1052 (Lo-16bits)
1054 | MEAS3:U2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1055 |  |  |  | HR1054 (Lo-16bits)
1056 | MEAS3:U2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1057 |  |  |  | HR1056 (Lo-16bits)
1058 | MEAS3:U2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1059 |  |  |  | HR1058 (Lo-16bits)
1060 | MEAS3:U2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1061 |  |  |  | HR1060 (Lo-16bits)
1062 | MEAS3:U2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1063 |  |  |  | HR1062 (Lo-16bits)
1064 | MEAS3:U2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1065 |  |  |  | HR1064 (Lo-16bits)
1066 | MEAS3:U2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1067 |  |  |  | HR1066 (Lo-16bits)
1068 | MEAS3:U2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1069 |  |  |  | HR1068 (Lo-16bits)
1070 | MEAS3:U2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1071 |  |  |  | HR1070 (Lo-16bits)
1072 | MEAS3:U2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1073 |  |  |  | HR1072 (Lo-16bits)
1074 | MEAS3:U2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1075 |  |  |  | HR1074 (Lo-16bits)
1076 | MEAS3:U2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1077 |  |  |  | HR1076 (Lo-16bits)
1078 | MEAS3:U2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1079 |  |  |  | HR1078 (Lo-16bits)
1080 | MEAS3:U2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1081 |  |  |  | HR1080 (Lo-16bits)
1082 | MEAS3:U2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1083 |  |  |  | HR1082 (Lo-16bits)
1084 | MEAS3:U2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1085 |  |  |  | HR1084 (Lo-16bits)
1086 | MEAS3:U2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1087 |  |  |  | HR1086 (Lo-16bits)
1088 | MEAS3:U2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1089 |  |  |  | HR1088 (Lo-16bits)
1090 | MEAS3:U2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1091 |  |  |  | HR1090 (Lo-16bits)
1092 | MEAS3:U2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1093 |  |  |  | HR1092 (Lo-16bits)
1094 | MEAS3:U2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1095 |  |  |  | HR1094 (Lo-16bits)
1096 | MEAS3:U2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1097 |  |  |  | HR1096 (Lo-16bits)
1098 | MEAS3:U2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1099 |  |  |  | HR1098 (Lo-16bits)
1100 | MEAS3:U2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1101 |  |  |  | HR1100 (Lo-16bits)
1102 | MEAS3:U3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1103 |  |  |  | HR1102 (Lo-16bits)
1104 | MEAS3:U3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1105 |  |  |  | HR1104 (Lo-16bits)
1106 | MEAS3:U3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1107 |  |  |  | HR1106 (Lo-16bits)
1108 | MEAS3:U3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1109 |  |  |  | HR1108 (Lo-16bits)
1110 | MEAS3:U3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1111 |  |  |  | HR1110 (Lo-16bits)
1112 | MEAS3:U3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1113 |  |  |  | HR1112 (Lo-16bits)
1114 | MEAS3:U3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1115 |  |  |  | HR1114 (Lo-16bits)
1116 | MEAS3:U3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1117 |  |  |  | HR1116 (Lo-16bits)
1118 | MEAS3:U3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1119 |  |  |  | HR1118 (Lo-16bits)
1120 | MEAS3:U3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1121 |  |  |  | HR1120 (Lo-16bits)
1122 | MEAS3:U3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1123 |  |  |  | HR1122 (Lo-16bits)
1124 | MEAS3:U3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1125 |  |  |  | HR1124 (Lo-16bits)
1126 | MEAS3:U3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1127 |  |  |  | HR1126 (Lo-16bits)
1128 | MEAS3:U3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1129 |  |  |  | HR1128 (Lo-16bits)
1130 | MEAS3:U3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1131 |  |  |  | HR1130 (Lo-16bits)
1132 | MEAS3:U3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1133 |  |  |  | HR1132 (Lo-16bits)
1134 | MEAS3:U3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1135 |  |  |  | HR1134 (Lo-16bits)
1136 | MEAS3:U3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1137 |  |  |  | HR1136 (Lo-16bits)
1138 | MEAS3:U3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1139 |  |  |  | HR1138 (Lo-16bits)
1140 | MEAS3:U3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1141 |  |  |  | HR1140 (Lo-16bits)
1142 | MEAS3:U3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1143 |  |  |  | HR1142 (Lo-16bits)
1144 | MEAS3:U3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1145 |  |  |  | HR1144 (Lo-16bits)
1146 | MEAS3:U3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1147 |  |  |  | HR1146 (Lo-16bits)
1148 | MEAS3:U3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1149 |  |  |  | HR1148 (Lo-16bits)
1150 | MEAS3:U3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1151 |  |  |  | HR1150 (Lo-16bits)
1152 | MEAS3:U3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1153 |  |  |  | HR1152 (Lo-16bits)
1154 | MEAS3:U3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1155 |  |  |  | HR1154 (Lo-16bits)
1156 | MEAS3:U3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1157 |  |  |  | HR1156 (Lo-16bits)
1158 | MEAS3:U3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1159 |  |  |  | HR1158 (Lo-16bits)
1160 | MEAS3:U3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1161 |  |  |  | HR1160 (Lo-16bits)
1162 | MEAS3:U3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1163 |  |  |  | HR1162 (Lo-16bits)
1164 | MEAS3:U4 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1165 |  |  |  | HR1164 (Lo-16bits)
1166 | MEAS3:U4 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1167 |  |  |  | HR1166 (Lo-16bits)
1168 | MEAS3:U4 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1169 |  |  |  | HR1168 (Lo-16bits)
1170 | MEAS3:U4 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1171 |  |  |  | HR1170 (Lo-16bits)
1172 | MEAS3:U4 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1173 |  |  |  | HR1172 (Lo-16bits)
1174 | MEAS3:U4 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1175 |  |  |  | HR1174 (Lo-16bits)
1176 | MEAS3:U4 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1177 |  |  |  | HR1176 (Lo-16bits)
1178 | MEAS3:U4 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1179 |  |  |  | HR1178 (Lo-16bits)
1180 | MEAS3:U4 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1181 |  |  |  | HR1180 (Lo-16bits)
1182 | MEAS3:U4 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1183 |  |  |  | HR1182 (Lo-16bits)
1184 | MEAS3:U4 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1185 |  |  |  | HR1184 (Lo-16bits)
1186 | MEAS3:U4 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1187 |  |  |  | HR1186 (Lo-16bits)
1188 | MEAS3:U4 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1189 |  |  |  | HR1188 (Lo-16bits)
1190 | MEAS3:U4 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1191 |  |  |  | HR1190 (Lo-16bits)
1192 | MEAS3:U4 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1193 |  |  |  | HR1192 (Lo-16bits)
1194 | MEAS3:U4 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1195 |  |  |  | HR1194 (Lo-16bits)
1196 | MEAS3:U4 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1197 |  |  |  | HR1196 (Lo-16bits)
1198 | MEAS3:U4 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1199 |  |  |  | HR1198 (Lo-16bits)
1200 | MEAS3:U4 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1201 |  |  |  | HR1200 (Lo-16bits)
1202 | MEAS3:U4 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1203 |  |  |  | HR1202 (Lo-16bits)
1204 | MEAS3:U4 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1205 |  |  |  | HR1204 (Lo-16bits)
1206 | MEAS3:U4 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1207 |  |  |  | HR1206 (Lo-16bits)
1208 | MEAS3:U4 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1209 |  |  |  | HR1208 (Lo-16bits)
1210 | MEAS3:U4 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1211 |  |  |  | HR1210 (Lo-16bits)
1212 | MEAS3:U4 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1213 |  |  |  | HR1212 (Lo-16bits)
1214 | MEAS3:U4 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1215 |  |  |  | HR1214 (Lo-16bits)
1216 | MEAS3:U4 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1217 |  |  |  | HR1216 (Lo-16bits)
1218 | MEAS3:U4 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1219 |  |  |  | HR1218 (Lo-16bits)
1220 | MEAS3:U4 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1221 |  |  |  | HR1220 (Lo-16bits)
1222 | MEAS3:U4 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1223 |  |  |  | HR1222 (Lo-16bits)
1224 | MEAS3:U4 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1225 |  |  |  | HR1224 (Lo-16bits)
1226 | IMERX:IL1 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1227 |  |  |  | HR1226 (Lo-16bits)
1228 | IMERX:IL1 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1229 |  |  |  | HR1228 (Lo-16bits)
1230 | IMERX:IL2 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1231 |  |  |  | HR1230 (Lo-16bits)
1232 | IMERX:IL2 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1233 |  |  |  | HR1232 (Lo-16bits)
1234 | IMERX:IL3 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1235 |  |  |  | HR1234 (Lo-16bits)
1236 | IMERX:IL3 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1237 |  |  |  | HR1236 (Lo-16bits)
1238 | IMERX:Pos.seq. Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1239 |  |  |  | HR1238 (Lo-16bits)
1240 | IMERX:Pos.Seq. Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1241 |  |  |  | HR1240 (Lo-16bits)
1242 | IMERX:I01 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1243 |  |  |  | HR1242 (Lo-16bits)
1244 | IMERX:I01 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1245 |  |  |  | HR1244 (Lo-16bits)
1246 | IMERX:I02 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1247 |  |  |  | HR1246 (Lo-16bits)
1248 | IMERX:I02 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1249 |  |  |  | HR1248 (Lo-16bits)
1250 | IMERX:I01 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1251 |  |  |  | HR1250 (Lo-16bits)
1252 | IMERX:I01 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1253 |  |  |  | HR1252 (Lo-16bits)
1254 | IMERX:I02 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1255 |  |  |  | HR1254 (Lo-16bits)
1256 | IMERX:I02 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1257 |  |  |  | HR1256 (Lo-16bits)
1258 | POW1:Export Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1259 |  |  |  | HR1258 (Lo-16bits)
1260 | POW1:Export Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1261 |  |  |  | HR1260 (Lo-16bits)
1262 | POW1:Import Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1263 |  |  |  | HR1262 (Lo-16bits)
1264 | POW1:Import Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1265 |  |  |  | HR1264 (Lo-16bits)
1266 | POW1:Active Energy (P) Export/Import balance MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1267 |  |  |  | HR1266 (Lo-16bits)
1268 | POW1:Active Energy (P) Export/Import balance kWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1269 |  |  |  | HR1268 (Lo-16bits)
1270 | POW1:Exported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1271 |  |  |  | HR1270 (Lo-16bits)
1272 | POW1:Exported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1273 |  |  |  | HR1272 (Lo-16bits)
1274 | POW1:Imported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1275 |  |  |  | HR1274 (Lo-16bits)
1276 | POW1:Imported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1277 |  |  |  | HR1276 (Lo-16bits)
1278 | POW1:Reactive Energy (Q) balance while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1279 |  |  |  | HR1278 (Lo-16bits)
1280 | POW1:Reactive Energy (Q) balance while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1281 |  |  |  | HR1280 (Lo-16bits)
1282 | POW1:Exported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1283 |  |  |  | HR1282 (Lo-16bits)
1284 | POW1:Exported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1285 |  |  |  | HR1284 (Lo-16bits)
1286 | POW1:Imported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1287 |  |  |  | HR1286 (Lo-16bits)
1288 | POW1:Imported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1289 |  |  |  | HR1288 (Lo-16bits)
1290 | POW1:Reactive Energy (Q) balance while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1291 |  |  |  | HR1290 (Lo-16bits)
1292 | POW1:Reactive Energy (Q) balance while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1293 |  |  |  | HR1292 (Lo-16bits)
1294 | POW1:Apparent Energy (S) while Export (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1295 |  |  |  | HR1294 (Lo-16bits)
1296 | POW1:Apparent Energy (S) while Export (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1297 |  |  |  | HR1296 (Lo-16bits)
1298 | POW1:Apparent Energy (S) while Import (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1299 |  |  |  | HR1298 (Lo-16bits)
1300 | POW1:Apparent Energy (S) while Import (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1301 |  |  |  | HR1300 (Lo-16bits)
1302 | POW1:Apparent Energy (S) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1303 |  |  |  | HR1302 (Lo-16bits)
1304 | POW1:Real Energy (P) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1305 |  |  |  | HR1304 (Lo-16bits)
1306 | POW1:Reactive Energy (Q) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1307 |  |  |  | HR1306 (Lo-16bits)
1308 | POW1:Real Energy (P) Supply (Default supply direction towards busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1309 |  |  |  | HR1308 (Lo-16bits)
1310 | POW1:Reactive Energy (Q) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1311 |  |  |  | HR1310 (Lo-16bits)
1312 | POW1:Real Energy (P) Demand (Default demand direction from busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1313 |  |  |  | HR1312 (Lo-16bits)
1314 | POW1:Reactive Energy (Q) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1315 |  |  |  | HR1314 (Lo-16bits)
1316 | POW1:Reset 3ph Energies | RW | 1 | 0=-;1=Reset
1317 | POW1:POW1 3PH Apparent power (S) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1318 |  |  |  | HR1317 (Lo-16bits)
1319 | POW1:POW1 3PH Apparent power (S MVA) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1320 |  |  |  | HR1319 (Lo-16bits)
1321 | POW1:POW1 3PH Active power (P) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1322 |  |  |  | HR1321 (Lo-16bits)
1323 | POW1:POW1 3PH Active power (P MW) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1324 |  |  |  | HR1323 (Lo-16bits)
1325 | POW1:POW1 3PH Reactive power (Q) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1326 |  |  |  | HR1325 (Lo-16bits)
1327 | POW1:POW1 3PH Reactive power (QMVar) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1328 |  |  |  | HR1327 (Lo-16bits)
1329 | POW1:POW1 3PH Tan(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1330 |  |  |  | HR1329 (Lo-16bits)
1331 | POW1:POW1 3PH Cos(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1332 |  |  |  | HR1331 (Lo-16bits)
1333 | POW1:3PH PF | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1334 |  |  |  | HR1333 (Lo-16bits)
1335 | ASC1:Curve1 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1336 |  |  |  | HR1335 (Lo-16bits)
1337 | ASC1:Curve1 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1338 |  |  |  | HR1337 (Lo-16bits)
1339 | ASC1:Curve2 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1340 |  |  |  | HR1339 (Lo-16bits)
1341 | ASC1:Curve2 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1342 |  |  |  | HR1341 (Lo-16bits)
1343 | ASC1:Curve3 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1344 |  |  |  | HR1343 (Lo-16bits)
1345 | ASC1:Curve3 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1346 |  |  |  | HR1345 (Lo-16bits)
1347 | ASC1:Curve4 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1348 |  |  |  | HR1347 (Lo-16bits)
1349 | ASC1:Curve4 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1350 |  |  |  | HR1349 (Lo-16bits)
1351 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1352 |  |  |  | HR1351 (Lo-16bits)
1353 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1354 |  |  |  | HR1353 (Lo-16bits)
1355 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1356 |  |  |  | HR1355 (Lo-16bits)
1357 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1358 |  |  |  | HR1357 (Lo-16bits)
1359 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1360 |  |  |  | HR1359 (Lo-16bits)
1361 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1362 |  |  |  | HR1361 (Lo-16bits)
1363 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1364 |  |  |  | HR1363 (Lo-16bits)
1365 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1366 |  |  |  | HR1365 (Lo-16bits)
1367 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1368 |  |  |  | HR1367 (Lo-16bits)
1369 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1370 |  |  |  | HR1369 (Lo-16bits)
1371 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1372 |  |  |  | HR1371 (Lo-16bits)
1373 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1374 |  |  |  | HR1373 (Lo-16bits)
1375 | M1CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1376 |  |  |  | HR1375 (Lo-16bits)
1377 | M1CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1378 |  |  |  | HR1377 (Lo-16bits)
1379 | M1CT2:I01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1380 |  |  |  | HR1379 (Lo-16bits)
1381 | M1CT2:I01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1382 |  |  |  | HR1381 (Lo-16bits)
1383 | M1CT3:I02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1384 |  |  |  | HR1383 (Lo-16bits)
1385 | M1CT3:I02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1386 |  |  |  | HR1385 (Lo-16bits)
1387 | M2CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1388 |  |  |  | HR1387 (Lo-16bits)
1389 | M2CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1390 |  |  |  | HR1389 (Lo-16bits)
1391 | M2CT2:I''01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1392 |  |  |  | HR1391 (Lo-16bits)
1393 | M2CT2:I''01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1394 |  |  |  | HR1393 (Lo-16bits)
1395 | M2CT3:I''02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1396 |  |  |  | HR1395 (Lo-16bits)
1397 | M2CT3:I''02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1398 |  |  |  | HR1397 (Lo-16bits)
1399 | M1VT1:VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1400 |  |  |  | HR1399 (Lo-16bits)
1401 | M1VT1:VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1402 |  |  |  | HR1401 (Lo-16bits)
1403 | M1VT1:U3 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1404 |  |  |  | HR1403 (Lo-16bits)
1405 | M1VT1:U3 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1406 |  |  |  | HR1405 (Lo-16bits)
1407 | M1VT1:U4 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1408 |  |  |  | HR1407 (Lo-16bits)
1409 | M1VT1:U4 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1410 |  |  |  | HR1409 (Lo-16bits)
1411 | FREQS:f atm. Protections (when not measurable returns to nominal) | R | 2 | FLOAT [0...75] (Hi-16bits)
1412 |  |  |  | HR1411 (Lo-16bits)
1413 | FREQS:f atm. Display (when not measurable is 0Hz) | R | 2 | FLOAT [0...75] (Hi-16bits)
1414 |  |  |  | HR1413 (Lo-16bits)
1415 | FREQS:SS1.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1416 |  |  |  | HR1415 (Lo-16bits)
1417 | FREQS:SS2.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1418 |  |  |  | HR1417 (Lo-16bits)
1419 | DIGI:DIs (cpu) | R | 2 | 0b=DI1;1b=DI2;2b=DI3; (Hi-16bits)
1420 |  |  |  | HR1419 (Lo-16bits)
1421 | DIGI:DIs (input option 1) | R | 2 | 0b=DI4;1b=DI5;2b=DI6;3b=DI7;4b=DI8;5b=DI9;6b=DI10;7b=DI11 (Hi-16bits)
1422 |  |  |  | HR1421 (Lo-16bits)
1423 | DIGI:DIs (input option 2) | R | 2 | 0b=DI12;1b=DI13;2b=DI14;3b=DI15;4b=DI16;5b=DI17;6b=DI18;7b=DI19 (Hi-16bits)
1424 |  |  |  | HR1423 (Lo-16bits)
1425 | DIGI:DIs (input option 3) | R | 2 | 0b=DI20;1b=DI21;2b=DI22;3b=DI23;4b=DI24;5b=DI25;6b=DI26;7b=DI27 (Hi-16bits)
1426 |  |  |  | HR1425 (Lo-16bits)
1427 | DIGI:DIs (input option 4) | R | 2 | 0b=D28;1b=DI29;2b=DI30;3b=DI31;4b=DI32;5b=DI33;6b=DI34;7b=DI35 (Hi-16bits)
1428 |  |  |  | HR1427 (Lo-16bits)
1429 | DIGI:DIs (input option 5) | R | 2 | 0b=DI36;1b=DI37;2b=DI38;3b=DI39;4b=DI40;5b=DI41;6b=DI42;7b=DI43 (Hi-16bits)
1430 |  |  |  | HR1429 (Lo-16bits)
1431 | DIGI:DIs (input option 6) | R | 2 | 0b=DI44;1b=DI45;2b=DI46;3b=DI47;4b=DI48;5b=DI49;6b=DI50;7b=DI51 (Hi-16bits)
1432 |  |  |  | HR1431 (Lo-16bits)
1433 | DIGI:Dis 1-32 | R | 2 | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32 (Hi-16bits)
1434 |  |  |  | HR1433 (Lo-16bits)
1435 | DIGI:Dis 33-64 | R | 2 | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51 (Hi-16bits)
1436 |  |  |  | HR1435 (Lo-16bits)
1437 | DIGI:DI1 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1438 |  |  |  | HR1437 (Lo-16bits)
1439 | DIGI:DI1 Counter Clear | RW | 1 | 0=-;1=Clear
1440 | DIGI:DI2 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1441 |  |  |  | HR1440 (Lo-16bits)
1442 | DIGI:DI2 Counter Clear | RW | 1 | 0=-;1=Clear
1443 | DIGI:DI3 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1444 |  |  |  | HR1443 (Lo-16bits)
1445 | DIGI:DI3 Counter Clear | RW | 1 | 0=-;1=Clear
1446 | DIGI:DI4 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1447 |  |  |  | HR1446 (Lo-16bits)
1448 | DIGI:DI4 Counter Clear | RW | 1 | 0=-;1=Clear
1449 | DIGI:DI5 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1450 |  |  |  | HR1449 (Lo-16bits)
1451 | DIGI:DI5 Counter Clear | RW | 1 | 0=-;1=Clear
1452 | DIGI:DI6 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1453 |  |  |  | HR1452 (Lo-16bits)
1454 | DIGI:DI6 Counter Clear | RW | 1 | 0=-;1=Clear
1455 | DIGI:DI7 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1456 |  |  |  | HR1455 (Lo-16bits)
1457 | DIGI:DI7 Counter Clear | RW | 1 | 0=-;1=Clear
1458 | DIGI:DI8 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1459 |  |  |  | HR1458 (Lo-16bits)
1460 | DIGI:DI8 Counter Clear | RW | 1 | 0=-;1=Clear
1461 | DIGI:DI9 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1462 |  |  |  | HR1461 (Lo-16bits)
1463 | DIGI:DI9 Counter Clear | RW | 1 | 0=-;1=Clear
1464 | DIGI:DI10 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1465 |  |  |  | HR1464 (Lo-16bits)
1466 | DIGI:DI10 Counter Clear | RW | 1 | 0=-;1=Clear
1467 | DIGI:DI11 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1468 |  |  |  | HR1467 (Lo-16bits)
1469 | DIGI:DI11 Counter Clear | RW | 1 | 0=-;1=Clear
1470 | DIGI:DI12 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1471 |  |  |  | HR1470 (Lo-16bits)
1472 | DIGI:DI12 Counter Clear | RW | 1 | 0=-;1=Clear
1473 | DIGI:DI13 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1474 |  |  |  | HR1473 (Lo-16bits)
1475 | DIGI:DI13 Counter Clear | RW | 1 | 0=-;1=Clear
1476 | DIGI:DI14 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1477 |  |  |  | HR1476 (Lo-16bits)
1478 | DIGI:DI14 Counter Clear | RW | 1 | 0=-;1=Clear
1479 | DIGI:DI15 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1480 |  |  |  | HR1479 (Lo-16bits)
1481 | DIGI:DI15 Counter Clear | RW | 1 | 0=-;1=Clear
1482 | DIGI:DI16 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1483 |  |  |  | HR1482 (Lo-16bits)
1484 | DIGI:DI16 Counter Clear | RW | 1 | 0=-;1=Clear
1485 | DIGI:DI17 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1486 |  |  |  | HR1485 (Lo-16bits)
1487 | DIGI:DI17 Counter Clear | RW | 1 | 0=-;1=Clear
1488 | DIGI:DI18 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1489 |  |  |  | HR1488 (Lo-16bits)
1490 | DIGI:DI18 Counter Clear | RW | 1 | 0=-;1=Clear
1491 | DIGI:DI19 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1492 |  |  |  | HR1491 (Lo-16bits)
1493 | DIGI:DI19 Counter Clear | RW | 1 | 0=-;1=Clear
1494 | DIGI:DI20 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1495 |  |  |  | HR1494 (Lo-16bits)
1496 | DIGI:DI20 Counter Clear | RW | 1 | 0=-;1=Clear
1497 | DIGI:DI21 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1498 |  |  |  | HR1497 (Lo-16bits)
1499 | DIGI:DI21 Counter Clear | RW | 1 | 0=-;1=Clear
1500 | DIGI:DI22 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1501 |  |  |  | HR1500 (Lo-16bits)
1502 | DIGI:DI22 Counter Clear | RW | 1 | 0=-;1=Clear
1503 | DIGI:DI23 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1504 |  |  |  | HR1503 (Lo-16bits)
1505 | DIGI:DI23 Counter Clear | RW | 1 | 0=-;1=Clear
1506 | DIGI:DI24 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1507 |  |  |  | HR1506 (Lo-16bits)
1508 | DIGI:DI24 Counter Clear | RW | 1 | 0=-;1=Clear
1509 | DIGI:DI25 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1510 |  |  |  | HR1509 (Lo-16bits)
1511 | DIGI:DI25 Counter Clear | RW | 1 | 0=-;1=Clear
1512 | DIGI:DI26 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1513 |  |  |  | HR1512 (Lo-16bits)
1514 | DIGI:DI26 Counter Clear | RW | 1 | 0=-;1=Clear
1515 | DIGI:DI27 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1516 |  |  |  | HR1515 (Lo-16bits)
1517 | DIGI:DI27 Counter Clear | RW | 1 | 0=-;1=Clear
1518 | DIGI:DI28 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1519 |  |  |  | HR1518 (Lo-16bits)
1520 | DIGI:DI28 Counter Clear | RW | 1 | 0=-;1=Clear
1521 | DIGI:DI29 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1522 |  |  |  | HR1521 (Lo-16bits)
1523 | DIGI:DI29 Counter Clear | RW | 1 | 0=-;1=Clear
1524 | DIGI:DI30 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1525 |  |  |  | HR1524 (Lo-16bits)
1526 | DIGI:DI30 Counter Clear | RW | 1 | 0=-;1=Clear
1527 | DIGI:DI31 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1528 |  |  |  | HR1527 (Lo-16bits)
1529 | DIGI:DI31 Counter Clear | RW | 1 | 0=-;1=Clear
1530 | DIGI:DI32 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1531 |  |  |  | HR1530 (Lo-16bits)
1532 | DIGI:DI32 Counter Clear | RW | 1 | 0=-;1=Clear
1533 | DIGI:DI33 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1534 |  |  |  | HR1533 (Lo-16bits)
1535 | DIGI:DI33 Counter Clear | RW | 1 | 0=-;1=Clear
1536 | DIGI:DI34 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1537 |  |  |  | HR1536 (Lo-16bits)
1538 | DIGI:DI34 Counter Clear | RW | 1 | 0=-;1=Clear
1539 | DIGI:DI35 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1540 |  |  |  | HR1539 (Lo-16bits)
1541 | DIGI:DI35 Counter Clear | RW | 1 | 0=-;1=Clear
1542 | DIGI:DI36 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1543 |  |  |  | HR1542 (Lo-16bits)
1544 | DIGI:DI36 Counter Clear | RW | 1 | 0=-;1=Clear
1545 | DIGI:DI37 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1546 |  |  |  | HR1545 (Lo-16bits)
1547 | DIGI:DI37 Counter Clear | RW | 1 | 0=-;1=Clear
1548 | DIGI:DI38 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1549 |  |  |  | HR1548 (Lo-16bits)
1550 | DIGI:DI38 Counter Clear | RW | 1 | 0=-;1=Clear
1551 | DIGI:DI39 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1552 |  |  |  | HR1551 (Lo-16bits)
1553 | DIGI:DI39 Counter Clear | RW | 1 | 0=-;1=Clear
1554 | DIGI:DI40 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1555 |  |  |  | HR1554 (Lo-16bits)
1556 | DIGI:DI40 Counter Clear | RW | 1 | 0=-;1=Clear
1557 | DIGI:DI41 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1558 |  |  |  | HR1557 (Lo-16bits)
1559 | DIGI:DI41 Counter Clear | RW | 1 | 0=-;1=Clear
1560 | DIGI:DI42 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1561 |  |  |  | HR1560 (Lo-16bits)
1562 | DIGI:DI42 Counter Clear | RW | 1 | 0=-;1=Clear
1563 | DIGI:DI43 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1564 |  |  |  | HR1563 (Lo-16bits)
1565 | DIGI:DI43 Counter Clear | RW | 1 | 0=-;1=Clear
1566 | DIGI:DI44 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1567 |  |  |  | HR1566 (Lo-16bits)
1568 | DIGI:DI44 Counter Clear | RW | 1 | 0=-;1=Clear
1569 | DIGI:DI45 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1570 |  |  |  | HR1569 (Lo-16bits)
1571 | DIGI:DI45 Counter Clear | RW | 1 | 0=-;1=Clear
1572 | DIGI:DI46 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1573 |  |  |  | HR1572 (Lo-16bits)
1574 | DIGI:DI46 Counter Clear | RW | 1 | 0=-;1=Clear
1575 | DIGI:DI47 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1576 |  |  |  | HR1575 (Lo-16bits)
1577 | DIGI:DI47 Counter Clear | RW | 1 | 0=-;1=Clear
1578 | DIGI:DI48 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1579 |  |  |  | HR1578 (Lo-16bits)
1580 | DIGI:DI48 Counter Clear | RW | 1 | 0=-;1=Clear
1581 | DIGI:DI49 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1582 |  |  |  | HR1581 (Lo-16bits)
1583 | DIGI:DI49 Counter Clear | RW | 1 | 0=-;1=Clear
1584 | DIGI:DI50 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1585 |  |  |  | HR1584 (Lo-16bits)
1586 | DIGI:DI50 Counter Clear | RW | 1 | 0=-;1=Clear
1587 | DIGI:DI51 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1588 |  |  |  | HR1587 (Lo-16bits)
1589 | DIGI:DI51 Counter Clear | RW | 1 | 0=-;1=Clear
1590 | RELE:Outputs status | R | 2 | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15 (Hi-16bits)
1591 |  |  |  | HR1590 (Lo-16bits)
1592 | SGS:Active setting group | R | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
1593 | SGS:Force SG | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1594 | SGS:Force SG change | RW | 1 | 0=Disabled;1=Enabled
1595 | SGS:Used setting groups | RW | 1 | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
1596 | SGS:Remote SG change | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1597 | CTRL:Local/Remote status | R | 1 | 0=Remote;1=Local
1598 | DEV:Serial number | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1599 |  |  |  | HR1598 (Lo-16bits)
1600 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1601 |  |  |  | HR1600 (Lo-16bits)
1602 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1603 |  |  |  | HR1602 (Lo-16bits)
1604 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1605 |  |  |  | HR1604 (Lo-16bits)
1606 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1607 |  |  |  | HR1606 (Lo-16bits)
1608 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1609 |  |  |  | HR1608 (Lo-16bits)
1610 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1611 |  |  |  | HR1610 (Lo-16bits)
1612 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1613 |  |  |  | HR1612 (Lo-16bits)
1614 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1615 |  |  |  | HR1614 (Lo-16bits)
1616 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1617 |  |  |  | HR1616 (Lo-16bits)
1618 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1619 |  |  |  | HR1618 (Lo-16bits)
1620 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1621 |  |  |  | HR1620 (Lo-16bits)
1622 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1623 |  |  |  | HR1622 (Lo-16bits)
1624 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1625 |  |  |  | HR1624 (Lo-16bits)
1626 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1627 |  |  |  | HR1626 (Lo-16bits)
1628 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1629 |  |  |  | HR1628 (Lo-16bits)
1630 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1631 |  |  |  | HR1630 (Lo-16bits)
1632 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1633 |  |  |  | HR1632 (Lo-16bits)
1634 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1635 |  |  |  | HR1634 (Lo-16bits)
1636 | DIAG:Configuration changed | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1637 |  |  |  | HR1636 (Lo-16bits)
1638 | MBTCP:Enable mapped setting value modification through Modbus | RW | 1 | 0=Disabled;1=Enabled
1639 | MBIO:MBIO ModA Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1640 |  |  |  | HR1639 (Lo-16bits)
1641 | MBIO:MBIO ModA Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1642 |  |  |  | HR1641 (Lo-16bits)
1643 | MBIO:MBIO ModA Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1644 |  |  |  | HR1643 (Lo-16bits)
1645 | MBIO:MBIO ModA Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1646 |  |  |  | HR1645 (Lo-16bits)
1647 | MBIO:MBIO ModA Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1648 |  |  |  | HR1647 (Lo-16bits)
1649 | MBIO:MBIO ModA Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1650 |  |  |  | HR1649 (Lo-16bits)
1651 | MBIO:MBIO ModA Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1652 |  |  |  | HR1651 (Lo-16bits)
1653 | MBIO:MBIO ModA Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1654 |  |  |  | HR1653 (Lo-16bits)
1655 | MBIO:MBIO ModB Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1656 |  |  |  | HR1655 (Lo-16bits)
1657 | MBIO:MBIO ModB Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1658 |  |  |  | HR1657 (Lo-16bits)
1659 | MBIO:MBIO ModB Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1660 |  |  |  | HR1659 (Lo-16bits)
1661 | MBIO:MBIO ModB Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1662 |  |  |  | HR1661 (Lo-16bits)
1663 | MBIO:MBIO ModB Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1664 |  |  |  | HR1663 (Lo-16bits)
1665 | MBIO:MBIO ModB Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1666 |  |  |  | HR1665 (Lo-16bits)
1667 | MBIO:MBIO ModB Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1668 |  |  |  | HR1667 (Lo-16bits)
1669 | MBIO:MBIO ModB Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1670 |  |  |  | HR1669 (Lo-16bits)
1671 | MBIO:MBIO ModC Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1672 |  |  |  | HR1671 (Lo-16bits)
1673 | MBIO:MBIO ModC Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1674 |  |  |  | HR1673 (Lo-16bits)
1675 | MBIO:MBIO ModC Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1676 |  |  |  | HR1675 (Lo-16bits)
1677 | MBIO:MBIO ModC Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1678 |  |  |  | HR1677 (Lo-16bits)
1679 | MBIO:MBIO ModC Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1680 |  |  |  | HR1679 (Lo-16bits)
1681 | MBIO:MBIO ModC Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1682 |  |  |  | HR1681 (Lo-16bits)
1683 | MBIO:MBIO ModC Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1684 |  |  |  | HR1683 (Lo-16bits)
1685 | MBIO:MBIO ModC Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1686 |  |  |  | HR1685 (Lo-16bits)
1687 | LOGIC:Reset Latches | RW | 1 | 0=-;1=Reset
1688 | LOGIC1:Logic out 1-32 | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
1689 |  |  |  | HR1688 (Lo-16bits)
1690 | NOC1:I> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1691 | NOC1:I> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1692 | NOC1:I> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1693 | NOC1:I> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1694 | NOC1:I> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1695 | NOC1:I> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1696 |  |  |  | HR1695 (Lo-16bits)
1697 | NOC1:I> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1698 |  |  |  | HR1697 (Lo-16bits)
1699 | NOC1:I> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1700 |  |  |  | HR1699 (Lo-16bits)
1701 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1702 |  |  |  | HR1701 (Lo-16bits)
1703 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1704 |  |  |  | HR1703 (Lo-16bits)
1705 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1706 |  |  |  | HR1705 (Lo-16bits)
1707 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1708 |  |  |  | HR1707 (Lo-16bits)
1709 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1710 |  |  |  | HR1709 (Lo-16bits)
1711 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1712 |  |  |  | HR1711 (Lo-16bits)
1713 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1714 |  |  |  | HR1713 (Lo-16bits)
1715 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1716 |  |  |  | HR1715 (Lo-16bits)
1717 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1718 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1719 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1720 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1721 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1722 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1723 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1724 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1725 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1726 |  |  |  | HR1725 (Lo-16bits)
1727 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1728 |  |  |  | HR1727 (Lo-16bits)
1729 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1730 |  |  |  | HR1729 (Lo-16bits)
1731 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1732 |  |  |  | HR1731 (Lo-16bits)
1733 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1734 |  |  |  | HR1733 (Lo-16bits)
1735 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1736 |  |  |  | HR1735 (Lo-16bits)
1737 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1738 |  |  |  | HR1737 (Lo-16bits)
1739 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1740 |  |  |  | HR1739 (Lo-16bits)
1741 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1742 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1743 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1744 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1745 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1746 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1747 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1748 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1749 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1750 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1751 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1752 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1753 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1754 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1755 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1756 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1757 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1758 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1759 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1760 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1761 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1762 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1763 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1764 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1765 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1766 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1767 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1768 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1769 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1770 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1771 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1772 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1773 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1774 |  |  |  | HR1773 (Lo-16bits)
1775 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1776 |  |  |  | HR1775 (Lo-16bits)
1777 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1778 |  |  |  | HR1777 (Lo-16bits)
1779 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1780 |  |  |  | HR1779 (Lo-16bits)
1781 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1782 |  |  |  | HR1781 (Lo-16bits)
1783 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1784 |  |  |  | HR1783 (Lo-16bits)
1785 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1786 |  |  |  | HR1785 (Lo-16bits)
1787 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1788 |  |  |  | HR1787 (Lo-16bits)
1789 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1790 |  |  |  | HR1789 (Lo-16bits)
1791 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1792 |  |  |  | HR1791 (Lo-16bits)
1793 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1794 |  |  |  | HR1793 (Lo-16bits)
1795 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1796 |  |  |  | HR1795 (Lo-16bits)
1797 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1798 |  |  |  | HR1797 (Lo-16bits)
1799 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1800 |  |  |  | HR1799 (Lo-16bits)
1801 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1802 |  |  |  | HR1801 (Lo-16bits)
1803 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1804 |  |  |  | HR1803 (Lo-16bits)
1805 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1806 |  |  |  | HR1805 (Lo-16bits)
1807 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1808 |  |  |  | HR1807 (Lo-16bits)
1809 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1810 |  |  |  | HR1809 (Lo-16bits)
1811 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1812 |  |  |  | HR1811 (Lo-16bits)
1813 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1814 |  |  |  | HR1813 (Lo-16bits)
1815 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1816 |  |  |  | HR1815 (Lo-16bits)
1817 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1818 |  |  |  | HR1817 (Lo-16bits)
1819 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1820 |  |  |  | HR1819 (Lo-16bits)
1821 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1822 |  |  |  | HR1821 (Lo-16bits)
1823 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1824 |  |  |  | HR1823 (Lo-16bits)
1825 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1826 |  |  |  | HR1825 (Lo-16bits)
1827 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1828 |  |  |  | HR1827 (Lo-16bits)
1829 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1830 |  |  |  | HR1829 (Lo-16bits)
1831 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1832 |  |  |  | HR1831 (Lo-16bits)
1833 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1834 |  |  |  | HR1833 (Lo-16bits)
1835 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1836 |  |  |  | HR1835 (Lo-16bits)
1837 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1838 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1839 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1840 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1841 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1842 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1843 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1844 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1845 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1846 |  |  |  | HR1845 (Lo-16bits)
1847 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1848 |  |  |  | HR1847 (Lo-16bits)
1849 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1850 |  |  |  | HR1849 (Lo-16bits)
1851 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1852 |  |  |  | HR1851 (Lo-16bits)
1853 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1854 |  |  |  | HR1853 (Lo-16bits)
1855 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1856 |  |  |  | HR1855 (Lo-16bits)
1857 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1858 |  |  |  | HR1857 (Lo-16bits)
1859 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1860 |  |  |  | HR1859 (Lo-16bits)
1861 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1862 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1863 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1864 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1865 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1866 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1867 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1868 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1869 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1870 |  |  |  | HR1869 (Lo-16bits)
1871 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1872 |  |  |  | HR1871 (Lo-16bits)
1873 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1874 |  |  |  | HR1873 (Lo-16bits)
1875 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1876 |  |  |  | HR1875 (Lo-16bits)
1877 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1878 |  |  |  | HR1877 (Lo-16bits)
1879 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1880 |  |  |  | HR1879 (Lo-16bits)
1881 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1882 |  |  |  | HR1881 (Lo-16bits)
1883 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1884 |  |  |  | HR1883 (Lo-16bits)
1885 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1886 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1887 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1888 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1889 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1890 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1891 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1892 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1893 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1894 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1895 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1896 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1897 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1898 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1899 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1900 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1901 | NOC1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
1902 |  |  |  | HR1901 (Lo-16bits)
1903 | NOC1:Delay type | RW | 1 | 0=DT;1=IDMT
1904 | NOC1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
1905 |  |  |  | HR1904 (Lo-16bits)
1906 | NOC1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
1907 | NOC1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1908 | NOC1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1909 | NOC1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
1910 | NOC1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
1911 |  |  |  | HR1910 (Lo-16bits)
1912 | NOC1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
1913 |  |  |  | HR1912 (Lo-16bits)
1914 | NOC1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
1915 |  |  |  | HR1914 (Lo-16bits)
1916 | NOC1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
1917 |  |  |  | HR1916 (Lo-16bits)
1918 | NOC1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
1919 | NOC1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
1920 | NOC2:I>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1921 | NOC2:I>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1922 | NOC2:I>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1923 | NOC2:I>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1924 | NOC2:I>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1925 | NOC2:I>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1926 |  |  |  | HR1925 (Lo-16bits)
1927 | NOC2:I>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1928 |  |  |  | HR1927 (Lo-16bits)
1929 | NOC2:I>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1930 |  |  |  | HR1929 (Lo-16bits)
1931 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1932 |  |  |  | HR1931 (Lo-16bits)
1933 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1934 |  |  |  | HR1933 (Lo-16bits)
1935 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1936 |  |  |  | HR1935 (Lo-16bits)
1937 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1938 |  |  |  | HR1937 (Lo-16bits)
1939 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1940 |  |  |  | HR1939 (Lo-16bits)
1941 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1942 |  |  |  | HR1941 (Lo-16bits)
1943 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1944 |  |  |  | HR1943 (Lo-16bits)
1945 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1946 |  |  |  | HR1945 (Lo-16bits)
1947 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1948 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1949 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1950 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1951 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1952 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1953 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1954 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1955 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1956 |  |  |  | HR1955 (Lo-16bits)
1957 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1958 |  |  |  | HR1957 (Lo-16bits)
1959 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1960 |  |  |  | HR1959 (Lo-16bits)
1961 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1962 |  |  |  | HR1961 (Lo-16bits)
1963 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1964 |  |  |  | HR1963 (Lo-16bits)
1965 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1966 |  |  |  | HR1965 (Lo-16bits)
1967 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1968 |  |  |  | HR1967 (Lo-16bits)
1969 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1970 |  |  |  | HR1969 (Lo-16bits)
1971 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1972 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1973 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1974 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1975 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1976 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1977 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1978 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1979 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1980 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1981 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1982 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1983 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1984 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1985 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1986 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1987 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1988 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1989 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1990 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1991 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1992 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1993 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1994 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1995 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1996 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1997 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1998 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1999 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2000 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2001 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2002 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2003 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2004 |  |  |  | HR2003 (Lo-16bits)
2005 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2006 |  |  |  | HR2005 (Lo-16bits)
2007 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2008 |  |  |  | HR2007 (Lo-16bits)
2009 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2010 |  |  |  | HR2009 (Lo-16bits)
2011 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2012 |  |  |  | HR2011 (Lo-16bits)
2013 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2014 |  |  |  | HR2013 (Lo-16bits)
2015 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2016 |  |  |  | HR2015 (Lo-16bits)
2017 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2018 |  |  |  | HR2017 (Lo-16bits)
2019 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2020 |  |  |  | HR2019 (Lo-16bits)
2021 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2022 |  |  |  | HR2021 (Lo-16bits)
2023 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2024 |  |  |  | HR2023 (Lo-16bits)
2025 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2026 |  |  |  | HR2025 (Lo-16bits)
2027 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2028 |  |  |  | HR2027 (Lo-16bits)
2029 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2030 |  |  |  | HR2029 (Lo-16bits)
2031 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2032 |  |  |  | HR2031 (Lo-16bits)
2033 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2034 |  |  |  | HR2033 (Lo-16bits)
2035 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2036 |  |  |  | HR2035 (Lo-16bits)
2037 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2038 |  |  |  | HR2037 (Lo-16bits)
2039 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2040 |  |  |  | HR2039 (Lo-16bits)
2041 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2042 |  |  |  | HR2041 (Lo-16bits)
2043 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2044 |  |  |  | HR2043 (Lo-16bits)
2045 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2046 |  |  |  | HR2045 (Lo-16bits)
2047 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2048 |  |  |  | HR2047 (Lo-16bits)
2049 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2050 |  |  |  | HR2049 (Lo-16bits)
2051 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2052 |  |  |  | HR2051 (Lo-16bits)
2053 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2054 |  |  |  | HR2053 (Lo-16bits)
2055 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2056 |  |  |  | HR2055 (Lo-16bits)
2057 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2058 |  |  |  | HR2057 (Lo-16bits)
2059 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2060 |  |  |  | HR2059 (Lo-16bits)
2061 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2062 |  |  |  | HR2061 (Lo-16bits)
2063 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2064 |  |  |  | HR2063 (Lo-16bits)
2065 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2066 |  |  |  | HR2065 (Lo-16bits)
2067 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2068 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2069 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2070 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2071 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2072 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2073 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2074 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2075 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2076 |  |  |  | HR2075 (Lo-16bits)
2077 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2078 |  |  |  | HR2077 (Lo-16bits)
2079 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2080 |  |  |  | HR2079 (Lo-16bits)
2081 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2082 |  |  |  | HR2081 (Lo-16bits)
2083 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2084 |  |  |  | HR2083 (Lo-16bits)
2085 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2086 |  |  |  | HR2085 (Lo-16bits)
2087 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2088 |  |  |  | HR2087 (Lo-16bits)
2089 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2090 |  |  |  | HR2089 (Lo-16bits)
2091 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2092 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2093 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2094 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2095 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2096 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2097 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2098 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2099 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2100 |  |  |  | HR2099 (Lo-16bits)
2101 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2102 |  |  |  | HR2101 (Lo-16bits)
2103 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2104 |  |  |  | HR2103 (Lo-16bits)
2105 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2106 |  |  |  | HR2105 (Lo-16bits)
2107 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2108 |  |  |  | HR2107 (Lo-16bits)
2109 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2110 |  |  |  | HR2109 (Lo-16bits)
2111 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2112 |  |  |  | HR2111 (Lo-16bits)
2113 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2114 |  |  |  | HR2113 (Lo-16bits)
2115 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2116 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2117 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2118 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2119 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2120 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2121 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2122 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2123 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2124 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2125 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2126 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2127 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2128 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2129 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2130 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2131 | NOC2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2132 |  |  |  | HR2131 (Lo-16bits)
2133 | NOC2:Delay type | RW | 1 | 0=DT;1=IDMT
2134 | NOC2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2135 |  |  |  | HR2134 (Lo-16bits)
2136 | NOC2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2137 | NOC2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2138 | NOC2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2139 | NOC2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2140 | NOC2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2141 |  |  |  | HR2140 (Lo-16bits)
2142 | NOC2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2143 |  |  |  | HR2142 (Lo-16bits)
2144 | NOC2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2145 |  |  |  | HR2144 (Lo-16bits)
2146 | NOC2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2147 |  |  |  | HR2146 (Lo-16bits)
2148 | NOC2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2149 | NOC2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2150 | NOC3:I>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2151 | NOC3:I>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2152 | NOC3:I>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2153 | NOC3:I>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2154 | NOC3:I>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2155 | NOC3:I>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2156 |  |  |  | HR2155 (Lo-16bits)
2157 | NOC3:I>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2158 |  |  |  | HR2157 (Lo-16bits)
2159 | NOC3:I>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2160 |  |  |  | HR2159 (Lo-16bits)
2161 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2162 |  |  |  | HR2161 (Lo-16bits)
2163 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2164 |  |  |  | HR2163 (Lo-16bits)
2165 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2166 |  |  |  | HR2165 (Lo-16bits)
2167 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2168 |  |  |  | HR2167 (Lo-16bits)
2169 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2170 |  |  |  | HR2169 (Lo-16bits)
2171 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2172 |  |  |  | HR2171 (Lo-16bits)
2173 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2174 |  |  |  | HR2173 (Lo-16bits)
2175 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2176 |  |  |  | HR2175 (Lo-16bits)
2177 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2178 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2179 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2180 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2181 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2182 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2183 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2184 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2185 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2186 |  |  |  | HR2185 (Lo-16bits)
2187 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2188 |  |  |  | HR2187 (Lo-16bits)
2189 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2190 |  |  |  | HR2189 (Lo-16bits)
2191 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2192 |  |  |  | HR2191 (Lo-16bits)
2193 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2194 |  |  |  | HR2193 (Lo-16bits)
2195 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2196 |  |  |  | HR2195 (Lo-16bits)
2197 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2198 |  |  |  | HR2197 (Lo-16bits)
2199 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2200 |  |  |  | HR2199 (Lo-16bits)
2201 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2202 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2203 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2204 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2205 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2206 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2207 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2208 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2209 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2210 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2211 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2212 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2213 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2214 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2215 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2216 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2217 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2218 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2219 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2220 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2221 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2222 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2223 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2224 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2225 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2226 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2227 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2228 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2229 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2230 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2231 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2232 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2233 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2234 |  |  |  | HR2233 (Lo-16bits)
2235 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2236 |  |  |  | HR2235 (Lo-16bits)
2237 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2238 |  |  |  | HR2237 (Lo-16bits)
2239 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2240 |  |  |  | HR2239 (Lo-16bits)
2241 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2242 |  |  |  | HR2241 (Lo-16bits)
2243 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2244 |  |  |  | HR2243 (Lo-16bits)
2245 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2246 |  |  |  | HR2245 (Lo-16bits)
2247 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2248 |  |  |  | HR2247 (Lo-16bits)
2249 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2250 |  |  |  | HR2249 (Lo-16bits)
2251 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2252 |  |  |  | HR2251 (Lo-16bits)
2253 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2254 |  |  |  | HR2253 (Lo-16bits)
2255 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2256 |  |  |  | HR2255 (Lo-16bits)
2257 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2258 |  |  |  | HR2257 (Lo-16bits)
2259 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2260 |  |  |  | HR2259 (Lo-16bits)
2261 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2262 |  |  |  | HR2261 (Lo-16bits)
2263 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2264 |  |  |  | HR2263 (Lo-16bits)
2265 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2266 |  |  |  | HR2265 (Lo-16bits)
2267 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2268 |  |  |  | HR2267 (Lo-16bits)
2269 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2270 |  |  |  | HR2269 (Lo-16bits)
2271 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2272 |  |  |  | HR2271 (Lo-16bits)
2273 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2274 |  |  |  | HR2273 (Lo-16bits)
2275 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2276 |  |  |  | HR2275 (Lo-16bits)
2277 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2278 |  |  |  | HR2277 (Lo-16bits)
2279 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2280 |  |  |  | HR2279 (Lo-16bits)
2281 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2282 |  |  |  | HR2281 (Lo-16bits)
2283 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2284 |  |  |  | HR2283 (Lo-16bits)
2285 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2286 |  |  |  | HR2285 (Lo-16bits)
2287 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2288 |  |  |  | HR2287 (Lo-16bits)
2289 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2290 |  |  |  | HR2289 (Lo-16bits)
2291 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2292 |  |  |  | HR2291 (Lo-16bits)
2293 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2294 |  |  |  | HR2293 (Lo-16bits)
2295 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2296 |  |  |  | HR2295 (Lo-16bits)
2297 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2298 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2299 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2300 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2301 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2302 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2303 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2304 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2305 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2306 |  |  |  | HR2305 (Lo-16bits)
2307 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2308 |  |  |  | HR2307 (Lo-16bits)
2309 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2310 |  |  |  | HR2309 (Lo-16bits)
2311 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2312 |  |  |  | HR2311 (Lo-16bits)
2313 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2314 |  |  |  | HR2313 (Lo-16bits)
2315 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2316 |  |  |  | HR2315 (Lo-16bits)
2317 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2318 |  |  |  | HR2317 (Lo-16bits)
2319 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2320 |  |  |  | HR2319 (Lo-16bits)
2321 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2322 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2323 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2324 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2325 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2326 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2327 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2328 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2329 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2330 |  |  |  | HR2329 (Lo-16bits)
2331 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2332 |  |  |  | HR2331 (Lo-16bits)
2333 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2334 |  |  |  | HR2333 (Lo-16bits)
2335 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2336 |  |  |  | HR2335 (Lo-16bits)
2337 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2338 |  |  |  | HR2337 (Lo-16bits)
2339 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2340 |  |  |  | HR2339 (Lo-16bits)
2341 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2342 |  |  |  | HR2341 (Lo-16bits)
2343 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2344 |  |  |  | HR2343 (Lo-16bits)
2345 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2346 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2347 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2348 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2349 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2350 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2351 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2352 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2353 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2354 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2355 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2356 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2357 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2358 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2359 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2360 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2361 | NOC3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2362 |  |  |  | HR2361 (Lo-16bits)
2363 | NOC3:Delay type | RW | 1 | 0=DT;1=IDMT
2364 | NOC3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2365 |  |  |  | HR2364 (Lo-16bits)
2366 | NOC3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2367 | NOC3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2368 | NOC3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2369 | NOC3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2370 | NOC3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2371 |  |  |  | HR2370 (Lo-16bits)
2372 | NOC3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2373 |  |  |  | HR2372 (Lo-16bits)
2374 | NOC3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2375 |  |  |  | HR2374 (Lo-16bits)
2376 | NOC3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2377 |  |  |  | HR2376 (Lo-16bits)
2378 | NOC3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2379 | NOC3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2380 | NOC4:I>>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2381 | NOC4:I>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2382 | NOC4:I>>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2383 | NOC4:I>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2384 | NOC4:I>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2385 | NOC4:I>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2386 |  |  |  | HR2385 (Lo-16bits)
2387 | NOC4:I>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2388 |  |  |  | HR2387 (Lo-16bits)
2389 | NOC4:I>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2390 |  |  |  | HR2389 (Lo-16bits)
2391 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2392 |  |  |  | HR2391 (Lo-16bits)
2393 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2394 |  |  |  | HR2393 (Lo-16bits)
2395 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2396 |  |  |  | HR2395 (Lo-16bits)
2397 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2398 |  |  |  | HR2397 (Lo-16bits)
2399 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2400 |  |  |  | HR2399 (Lo-16bits)
2401 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2402 |  |  |  | HR2401 (Lo-16bits)
2403 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2404 |  |  |  | HR2403 (Lo-16bits)
2405 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2406 |  |  |  | HR2405 (Lo-16bits)
2407 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2408 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2409 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2410 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2411 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2412 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2413 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2414 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2415 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2416 |  |  |  | HR2415 (Lo-16bits)
2417 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2418 |  |  |  | HR2417 (Lo-16bits)
2419 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2420 |  |  |  | HR2419 (Lo-16bits)
2421 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2422 |  |  |  | HR2421 (Lo-16bits)
2423 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2424 |  |  |  | HR2423 (Lo-16bits)
2425 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2426 |  |  |  | HR2425 (Lo-16bits)
2427 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2428 |  |  |  | HR2427 (Lo-16bits)
2429 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2430 |  |  |  | HR2429 (Lo-16bits)
2431 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2432 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2433 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2434 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2435 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2436 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2437 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2438 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2439 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2440 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2441 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2442 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2443 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2444 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2445 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2446 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2447 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2448 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2449 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2450 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2451 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2452 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2453 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2454 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2455 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2456 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2457 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2458 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2459 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2460 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2461 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2462 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2463 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2464 |  |  |  | HR2463 (Lo-16bits)
2465 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2466 |  |  |  | HR2465 (Lo-16bits)
2467 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2468 |  |  |  | HR2467 (Lo-16bits)
2469 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2470 |  |  |  | HR2469 (Lo-16bits)
2471 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2472 |  |  |  | HR2471 (Lo-16bits)
2473 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2474 |  |  |  | HR2473 (Lo-16bits)
2475 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2476 |  |  |  | HR2475 (Lo-16bits)
2477 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2478 |  |  |  | HR2477 (Lo-16bits)
2479 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2480 |  |  |  | HR2479 (Lo-16bits)
2481 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2482 |  |  |  | HR2481 (Lo-16bits)
2483 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2484 |  |  |  | HR2483 (Lo-16bits)
2485 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2486 |  |  |  | HR2485 (Lo-16bits)
2487 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2488 |  |  |  | HR2487 (Lo-16bits)
2489 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2490 |  |  |  | HR2489 (Lo-16bits)
2491 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2492 |  |  |  | HR2491 (Lo-16bits)
2493 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2494 |  |  |  | HR2493 (Lo-16bits)
2495 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2496 |  |  |  | HR2495 (Lo-16bits)
2497 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2498 |  |  |  | HR2497 (Lo-16bits)
2499 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2500 |  |  |  | HR2499 (Lo-16bits)
2501 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2502 |  |  |  | HR2501 (Lo-16bits)
2503 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2504 |  |  |  | HR2503 (Lo-16bits)
2505 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2506 |  |  |  | HR2505 (Lo-16bits)
2507 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2508 |  |  |  | HR2507 (Lo-16bits)
2509 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2510 |  |  |  | HR2509 (Lo-16bits)
2511 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2512 |  |  |  | HR2511 (Lo-16bits)
2513 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2514 |  |  |  | HR2513 (Lo-16bits)
2515 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2516 |  |  |  | HR2515 (Lo-16bits)
2517 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2518 |  |  |  | HR2517 (Lo-16bits)
2519 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2520 |  |  |  | HR2519 (Lo-16bits)
2521 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2522 |  |  |  | HR2521 (Lo-16bits)
2523 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2524 |  |  |  | HR2523 (Lo-16bits)
2525 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2526 |  |  |  | HR2525 (Lo-16bits)
2527 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2528 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2529 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2530 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2531 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2532 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2533 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2534 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2535 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2536 |  |  |  | HR2535 (Lo-16bits)
2537 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2538 |  |  |  | HR2537 (Lo-16bits)
2539 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2540 |  |  |  | HR2539 (Lo-16bits)
2541 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2542 |  |  |  | HR2541 (Lo-16bits)
2543 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2544 |  |  |  | HR2543 (Lo-16bits)
2545 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2546 |  |  |  | HR2545 (Lo-16bits)
2547 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2548 |  |  |  | HR2547 (Lo-16bits)
2549 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2550 |  |  |  | HR2549 (Lo-16bits)
2551 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2552 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2553 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2554 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2555 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2556 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2557 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2558 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2559 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2560 |  |  |  | HR2559 (Lo-16bits)
2561 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2562 |  |  |  | HR2561 (Lo-16bits)
2563 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2564 |  |  |  | HR2563 (Lo-16bits)
2565 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2566 |  |  |  | HR2565 (Lo-16bits)
2567 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2568 |  |  |  | HR2567 (Lo-16bits)
2569 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2570 |  |  |  | HR2569 (Lo-16bits)
2571 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2572 |  |  |  | HR2571 (Lo-16bits)
2573 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2574 |  |  |  | HR2573 (Lo-16bits)
2575 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2576 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2577 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2578 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2579 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2580 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2581 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2582 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2583 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2584 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2585 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2586 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2587 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2588 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2589 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2590 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2591 | NOC4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2592 |  |  |  | HR2591 (Lo-16bits)
2593 | NOC4:Delay type | RW | 1 | 0=DT;1=IDMT
2594 | NOC4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2595 |  |  |  | HR2594 (Lo-16bits)
2596 | NOC4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2597 | NOC4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2598 | NOC4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2599 | NOC4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2600 | NOC4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2601 |  |  |  | HR2600 (Lo-16bits)
2602 | NOC4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2603 |  |  |  | HR2602 (Lo-16bits)
2604 | NOC4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2605 |  |  |  | HR2604 (Lo-16bits)
2606 | NOC4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2607 |  |  |  | HR2606 (Lo-16bits)
2608 | NOC4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2609 | NOC4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2610 | ROC1:Idrw> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2611 | ROC1:Idrw> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2612 | ROC2:Idrw>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2613 | ROC2:Idrw>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2614 | ROC3:Idrw>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2615 | ROC3:Idrw>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2616 | ROC4:Idrw>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2617 | ROC4:Idrw>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2618 | ROC5:Idrw>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2619 | ROC5:Idrw>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2620 | ROC6:Idrw>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2621 | ROC6:Idrw>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2622 | ROC7:Idrw>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2623 | ROC7:Idrw>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2624 | ROC8:Idrw>>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2625 | ROC8:Idrw>>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2626 | ROV1:Urw>/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2627 | ROV2:Urw>>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2628 | ROV3:Urw>>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2629 | ROV4:Urw>>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2630 | COL1:ICOL> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2631 | COL2:ICOL>> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2632 | CNU1:CNU> (50UB) mode | R(W) | 1 | 0=Disabled;1=Activated
2633 | UCP1:IUC> condition | R | 1 | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
2634 | DOC1:Idir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2635 | DOC1:Idir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2636 | DOC1:Idir> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2637 | DOC1:Idir> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2638 |  |  |  | HR2637 (Lo-16bits)
2639 | DOC1:Idir> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2640 |  |  |  | HR2639 (Lo-16bits)
2641 | DOC1:Idir> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2642 |  |  |  | HR2641 (Lo-16bits)
2643 | DOC1:Idir> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2644 |  |  |  | HR2643 (Lo-16bits)
2645 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2646 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2647 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2648 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2649 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2650 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2651 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2652 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2653 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2654 |  |  |  | HR2653 (Lo-16bits)
2655 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2656 |  |  |  | HR2655 (Lo-16bits)
2657 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2658 |  |  |  | HR2657 (Lo-16bits)
2659 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2660 |  |  |  | HR2659 (Lo-16bits)
2661 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2662 |  |  |  | HR2661 (Lo-16bits)
2663 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2664 |  |  |  | HR2663 (Lo-16bits)
2665 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2666 |  |  |  | HR2665 (Lo-16bits)
2667 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2668 |  |  |  | HR2667 (Lo-16bits)
2669 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2670 |  |  |  | HR2669 (Lo-16bits)
2671 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2672 |  |  |  | HR2671 (Lo-16bits)
2673 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2674 |  |  |  | HR2673 (Lo-16bits)
2675 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2676 |  |  |  | HR2675 (Lo-16bits)
2677 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2678 |  |  |  | HR2677 (Lo-16bits)
2679 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2680 |  |  |  | HR2679 (Lo-16bits)
2681 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2682 |  |  |  | HR2681 (Lo-16bits)
2683 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2684 |  |  |  | HR2683 (Lo-16bits)
2685 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2686 |  |  |  | HR2685 (Lo-16bits)
2687 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2688 |  |  |  | HR2687 (Lo-16bits)
2689 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2690 |  |  |  | HR2689 (Lo-16bits)
2691 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2692 |  |  |  | HR2691 (Lo-16bits)
2693 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2694 |  |  |  | HR2693 (Lo-16bits)
2695 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2696 |  |  |  | HR2695 (Lo-16bits)
2697 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2698 |  |  |  | HR2697 (Lo-16bits)
2699 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2700 |  |  |  | HR2699 (Lo-16bits)
2701 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2702 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2703 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2704 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2705 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2706 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2707 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2708 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2709 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2710 |  |  |  | HR2709 (Lo-16bits)
2711 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2712 |  |  |  | HR2711 (Lo-16bits)
2713 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2714 |  |  |  | HR2713 (Lo-16bits)
2715 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2716 |  |  |  | HR2715 (Lo-16bits)
2717 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2718 |  |  |  | HR2717 (Lo-16bits)
2719 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2720 |  |  |  | HR2719 (Lo-16bits)
2721 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2722 |  |  |  | HR2721 (Lo-16bits)
2723 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2724 |  |  |  | HR2723 (Lo-16bits)
2725 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2726 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2727 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2728 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2729 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2730 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2731 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2732 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2733 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2734 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2735 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2736 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2737 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2738 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2739 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2740 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2741 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2742 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2743 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2744 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2745 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2746 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2747 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2748 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2749 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2750 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2751 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2752 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2753 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2754 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2755 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2756 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2757 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2758 |  |  |  | HR2757 (Lo-16bits)
2759 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2760 |  |  |  | HR2759 (Lo-16bits)
2761 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2762 |  |  |  | HR2761 (Lo-16bits)
2763 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2764 |  |  |  | HR2763 (Lo-16bits)
2765 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2766 |  |  |  | HR2765 (Lo-16bits)
2767 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2768 |  |  |  | HR2767 (Lo-16bits)
2769 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2770 |  |  |  | HR2769 (Lo-16bits)
2771 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2772 |  |  |  | HR2771 (Lo-16bits)
2773 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2774 |  |  |  | HR2773 (Lo-16bits)
2775 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2776 |  |  |  | HR2775 (Lo-16bits)
2777 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2778 |  |  |  | HR2777 (Lo-16bits)
2779 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2780 |  |  |  | HR2779 (Lo-16bits)
2781 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2782 |  |  |  | HR2781 (Lo-16bits)
2783 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2784 |  |  |  | HR2783 (Lo-16bits)
2785 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2786 |  |  |  | HR2785 (Lo-16bits)
2787 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2788 |  |  |  | HR2787 (Lo-16bits)
2789 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2790 |  |  |  | HR2789 (Lo-16bits)
2791 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2792 |  |  |  | HR2791 (Lo-16bits)
2793 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2794 |  |  |  | HR2793 (Lo-16bits)
2795 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2796 |  |  |  | HR2795 (Lo-16bits)
2797 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2798 |  |  |  | HR2797 (Lo-16bits)
2799 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2800 |  |  |  | HR2799 (Lo-16bits)
2801 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2802 |  |  |  | HR2801 (Lo-16bits)
2803 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2804 |  |  |  | HR2803 (Lo-16bits)
2805 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2806 |  |  |  | HR2805 (Lo-16bits)
2807 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2808 |  |  |  | HR2807 (Lo-16bits)
2809 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2810 |  |  |  | HR2809 (Lo-16bits)
2811 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2812 |  |  |  | HR2811 (Lo-16bits)
2813 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2814 |  |  |  | HR2813 (Lo-16bits)
2815 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2816 |  |  |  | HR2815 (Lo-16bits)
2817 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2818 |  |  |  | HR2817 (Lo-16bits)
2819 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2820 |  |  |  | HR2819 (Lo-16bits)
2821 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2822 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2823 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2824 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2825 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2826 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2827 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2828 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2829 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2830 |  |  |  | HR2829 (Lo-16bits)
2831 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2832 |  |  |  | HR2831 (Lo-16bits)
2833 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2834 |  |  |  | HR2833 (Lo-16bits)
2835 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2836 |  |  |  | HR2835 (Lo-16bits)
2837 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2838 |  |  |  | HR2837 (Lo-16bits)
2839 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2840 |  |  |  | HR2839 (Lo-16bits)
2841 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2842 |  |  |  | HR2841 (Lo-16bits)
2843 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2844 |  |  |  | HR2843 (Lo-16bits)
2845 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2846 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2847 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2848 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2849 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2850 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2851 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2852 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2853 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2854 |  |  |  | HR2853 (Lo-16bits)
2855 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2856 |  |  |  | HR2855 (Lo-16bits)
2857 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2858 |  |  |  | HR2857 (Lo-16bits)
2859 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2860 |  |  |  | HR2859 (Lo-16bits)
2861 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2862 |  |  |  | HR2861 (Lo-16bits)
2863 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2864 |  |  |  | HR2863 (Lo-16bits)
2865 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2866 |  |  |  | HR2865 (Lo-16bits)
2867 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2868 |  |  |  | HR2867 (Lo-16bits)
2869 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2870 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2871 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2872 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2873 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2874 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2875 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2876 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2877 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2878 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2879 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2880 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2881 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2882 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2883 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2884 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2885 | DOC2:Idir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2886 | DOC2:Idir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2887 | DOC2:Idir>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2888 | DOC2:Idir>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2889 |  |  |  | HR2888 (Lo-16bits)
2890 | DOC2:Idir>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2891 |  |  |  | HR2890 (Lo-16bits)
2892 | DOC2:Idir>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2893 |  |  |  | HR2892 (Lo-16bits)
2894 | DOC2:Idir>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2895 |  |  |  | HR2894 (Lo-16bits)
2896 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2897 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2898 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2899 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2900 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2901 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2902 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2903 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2904 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2905 |  |  |  | HR2904 (Lo-16bits)
2906 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2907 |  |  |  | HR2906 (Lo-16bits)
2908 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2909 |  |  |  | HR2908 (Lo-16bits)
2910 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2911 |  |  |  | HR2910 (Lo-16bits)
2912 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2913 |  |  |  | HR2912 (Lo-16bits)
2914 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2915 |  |  |  | HR2914 (Lo-16bits)
2916 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2917 |  |  |  | HR2916 (Lo-16bits)
2918 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2919 |  |  |  | HR2918 (Lo-16bits)
2920 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2921 |  |  |  | HR2920 (Lo-16bits)
2922 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2923 |  |  |  | HR2922 (Lo-16bits)
2924 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2925 |  |  |  | HR2924 (Lo-16bits)
2926 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2927 |  |  |  | HR2926 (Lo-16bits)
2928 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2929 |  |  |  | HR2928 (Lo-16bits)
2930 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2931 |  |  |  | HR2930 (Lo-16bits)
2932 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2933 |  |  |  | HR2932 (Lo-16bits)
2934 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2935 |  |  |  | HR2934 (Lo-16bits)
2936 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2937 |  |  |  | HR2936 (Lo-16bits)
2938 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2939 |  |  |  | HR2938 (Lo-16bits)
2940 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2941 |  |  |  | HR2940 (Lo-16bits)
2942 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2943 |  |  |  | HR2942 (Lo-16bits)
2944 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2945 |  |  |  | HR2944 (Lo-16bits)
2946 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2947 |  |  |  | HR2946 (Lo-16bits)
2948 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2949 |  |  |  | HR2948 (Lo-16bits)
2950 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2951 |  |  |  | HR2950 (Lo-16bits)
2952 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2953 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2954 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2955 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2956 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2957 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2958 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2959 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2960 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2961 |  |  |  | HR2960 (Lo-16bits)
2962 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2963 |  |  |  | HR2962 (Lo-16bits)
2964 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2965 |  |  |  | HR2964 (Lo-16bits)
2966 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2967 |  |  |  | HR2966 (Lo-16bits)
2968 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2969 |  |  |  | HR2968 (Lo-16bits)
2970 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2971 |  |  |  | HR2970 (Lo-16bits)
2972 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2973 |  |  |  | HR2972 (Lo-16bits)
2974 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2975 |  |  |  | HR2974 (Lo-16bits)
2976 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2977 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2978 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2979 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2980 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2981 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2982 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2983 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2984 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2985 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2986 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2987 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2988 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2989 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2990 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2991 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2992 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2993 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2994 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2995 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2996 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2997 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2998 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2999 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3000 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3001 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3002 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3003 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3004 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3005 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3006 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3007 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3008 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3009 |  |  |  | HR3008 (Lo-16bits)
3010 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3011 |  |  |  | HR3010 (Lo-16bits)
3012 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3013 |  |  |  | HR3012 (Lo-16bits)
3014 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3015 |  |  |  | HR3014 (Lo-16bits)
3016 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3017 |  |  |  | HR3016 (Lo-16bits)
3018 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3019 |  |  |  | HR3018 (Lo-16bits)
3020 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3021 |  |  |  | HR3020 (Lo-16bits)
3022 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3023 |  |  |  | HR3022 (Lo-16bits)
3024 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3025 |  |  |  | HR3024 (Lo-16bits)
3026 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3027 |  |  |  | HR3026 (Lo-16bits)
3028 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3029 |  |  |  | HR3028 (Lo-16bits)
3030 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3031 |  |  |  | HR3030 (Lo-16bits)
3032 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3033 |  |  |  | HR3032 (Lo-16bits)
3034 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3035 |  |  |  | HR3034 (Lo-16bits)
3036 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3037 |  |  |  | HR3036 (Lo-16bits)
3038 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3039 |  |  |  | HR3038 (Lo-16bits)
3040 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3041 |  |  |  | HR3040 (Lo-16bits)
3042 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3043 |  |  |  | HR3042 (Lo-16bits)
3044 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3045 |  |  |  | HR3044 (Lo-16bits)
3046 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3047 |  |  |  | HR3046 (Lo-16bits)
3048 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3049 |  |  |  | HR3048 (Lo-16bits)
3050 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3051 |  |  |  | HR3050 (Lo-16bits)
3052 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3053 |  |  |  | HR3052 (Lo-16bits)
3054 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3055 |  |  |  | HR3054 (Lo-16bits)
3056 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3057 |  |  |  | HR3056 (Lo-16bits)
3058 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3059 |  |  |  | HR3058 (Lo-16bits)
3060 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3061 |  |  |  | HR3060 (Lo-16bits)
3062 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3063 |  |  |  | HR3062 (Lo-16bits)
3064 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3065 |  |  |  | HR3064 (Lo-16bits)
3066 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3067 |  |  |  | HR3066 (Lo-16bits)
3068 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3069 |  |  |  | HR3068 (Lo-16bits)
3070 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3071 |  |  |  | HR3070 (Lo-16bits)
3072 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3073 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3074 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3075 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3076 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3077 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3078 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3079 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3080 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3081 |  |  |  | HR3080 (Lo-16bits)
3082 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3083 |  |  |  | HR3082 (Lo-16bits)
3084 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3085 |  |  |  | HR3084 (Lo-16bits)
3086 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3087 |  |  |  | HR3086 (Lo-16bits)
3088 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3089 |  |  |  | HR3088 (Lo-16bits)
3090 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3091 |  |  |  | HR3090 (Lo-16bits)
3092 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3093 |  |  |  | HR3092 (Lo-16bits)
3094 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3095 |  |  |  | HR3094 (Lo-16bits)
3096 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3097 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3098 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3099 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3100 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3101 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3102 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3103 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3104 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3105 |  |  |  | HR3104 (Lo-16bits)
3106 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3107 |  |  |  | HR3106 (Lo-16bits)
3108 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3109 |  |  |  | HR3108 (Lo-16bits)
3110 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3111 |  |  |  | HR3110 (Lo-16bits)
3112 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3113 |  |  |  | HR3112 (Lo-16bits)
3114 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3115 |  |  |  | HR3114 (Lo-16bits)
3116 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3117 |  |  |  | HR3116 (Lo-16bits)
3118 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3119 |  |  |  | HR3118 (Lo-16bits)
3120 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3121 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3122 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3123 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3124 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3125 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3126 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3127 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3128 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3129 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3130 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3131 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3132 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3133 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3134 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3135 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3136 | DOC3:Idir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3137 | DOC3:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3138 | DOC3:Idir>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3139 | DOC3:Idir>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3140 |  |  |  | HR3139 (Lo-16bits)
3141 | DOC3:Idir>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3142 |  |  |  | HR3141 (Lo-16bits)
3143 | DOC3:Idir>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3144 |  |  |  | HR3143 (Lo-16bits)
3145 | DOC3:Idir>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3146 |  |  |  | HR3145 (Lo-16bits)
3147 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3148 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3149 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3150 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3151 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3152 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3153 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3154 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3155 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3156 |  |  |  | HR3155 (Lo-16bits)
3157 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3158 |  |  |  | HR3157 (Lo-16bits)
3159 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3160 |  |  |  | HR3159 (Lo-16bits)
3161 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3162 |  |  |  | HR3161 (Lo-16bits)
3163 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3164 |  |  |  | HR3163 (Lo-16bits)
3165 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3166 |  |  |  | HR3165 (Lo-16bits)
3167 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3168 |  |  |  | HR3167 (Lo-16bits)
3169 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3170 |  |  |  | HR3169 (Lo-16bits)
3171 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3172 |  |  |  | HR3171 (Lo-16bits)
3173 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3174 |  |  |  | HR3173 (Lo-16bits)
3175 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3176 |  |  |  | HR3175 (Lo-16bits)
3177 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3178 |  |  |  | HR3177 (Lo-16bits)
3179 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3180 |  |  |  | HR3179 (Lo-16bits)
3181 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3182 |  |  |  | HR3181 (Lo-16bits)
3183 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3184 |  |  |  | HR3183 (Lo-16bits)
3185 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3186 |  |  |  | HR3185 (Lo-16bits)
3187 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3188 |  |  |  | HR3187 (Lo-16bits)
3189 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3190 |  |  |  | HR3189 (Lo-16bits)
3191 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3192 |  |  |  | HR3191 (Lo-16bits)
3193 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3194 |  |  |  | HR3193 (Lo-16bits)
3195 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3196 |  |  |  | HR3195 (Lo-16bits)
3197 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3198 |  |  |  | HR3197 (Lo-16bits)
3199 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3200 |  |  |  | HR3199 (Lo-16bits)
3201 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3202 |  |  |  | HR3201 (Lo-16bits)
3203 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3204 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3205 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3206 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3207 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3208 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3209 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3210 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3211 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3212 |  |  |  | HR3211 (Lo-16bits)
3213 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3214 |  |  |  | HR3213 (Lo-16bits)
3215 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3216 |  |  |  | HR3215 (Lo-16bits)
3217 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3218 |  |  |  | HR3217 (Lo-16bits)
3219 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3220 |  |  |  | HR3219 (Lo-16bits)
3221 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3222 |  |  |  | HR3221 (Lo-16bits)
3223 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3224 |  |  |  | HR3223 (Lo-16bits)
3225 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3226 |  |  |  | HR3225 (Lo-16bits)
3227 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3228 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3229 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3230 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3231 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3232 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3233 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3234 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3235 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3236 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3237 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3238 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3239 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3240 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3241 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3242 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3243 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3244 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3245 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3246 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3247 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3248 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3249 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3250 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3251 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3252 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3253 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3254 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3255 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3256 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3257 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3258 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3259 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3260 |  |  |  | HR3259 (Lo-16bits)
3261 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3262 |  |  |  | HR3261 (Lo-16bits)
3263 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3264 |  |  |  | HR3263 (Lo-16bits)
3265 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3266 |  |  |  | HR3265 (Lo-16bits)
3267 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3268 |  |  |  | HR3267 (Lo-16bits)
3269 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3270 |  |  |  | HR3269 (Lo-16bits)
3271 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3272 |  |  |  | HR3271 (Lo-16bits)
3273 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3274 |  |  |  | HR3273 (Lo-16bits)
3275 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3276 |  |  |  | HR3275 (Lo-16bits)
3277 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3278 |  |  |  | HR3277 (Lo-16bits)
3279 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3280 |  |  |  | HR3279 (Lo-16bits)
3281 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3282 |  |  |  | HR3281 (Lo-16bits)
3283 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3284 |  |  |  | HR3283 (Lo-16bits)
3285 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3286 |  |  |  | HR3285 (Lo-16bits)
3287 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3288 |  |  |  | HR3287 (Lo-16bits)
3289 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3290 |  |  |  | HR3289 (Lo-16bits)
3291 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3292 |  |  |  | HR3291 (Lo-16bits)
3293 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3294 |  |  |  | HR3293 (Lo-16bits)
3295 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3296 |  |  |  | HR3295 (Lo-16bits)
3297 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3298 |  |  |  | HR3297 (Lo-16bits)
3299 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3300 |  |  |  | HR3299 (Lo-16bits)
3301 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3302 |  |  |  | HR3301 (Lo-16bits)
3303 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3304 |  |  |  | HR3303 (Lo-16bits)
3305 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3306 |  |  |  | HR3305 (Lo-16bits)
3307 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3308 |  |  |  | HR3307 (Lo-16bits)
3309 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3310 |  |  |  | HR3309 (Lo-16bits)
3311 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3312 |  |  |  | HR3311 (Lo-16bits)
3313 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3314 |  |  |  | HR3313 (Lo-16bits)
3315 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3316 |  |  |  | HR3315 (Lo-16bits)
3317 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3318 |  |  |  | HR3317 (Lo-16bits)
3319 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3320 |  |  |  | HR3319 (Lo-16bits)
3321 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3322 |  |  |  | HR3321 (Lo-16bits)
3323 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3324 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3325 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3326 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3327 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3328 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3329 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3330 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3331 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3332 |  |  |  | HR3331 (Lo-16bits)
3333 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3334 |  |  |  | HR3333 (Lo-16bits)
3335 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3336 |  |  |  | HR3335 (Lo-16bits)
3337 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3338 |  |  |  | HR3337 (Lo-16bits)
3339 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3340 |  |  |  | HR3339 (Lo-16bits)
3341 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3342 |  |  |  | HR3341 (Lo-16bits)
3343 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3344 |  |  |  | HR3343 (Lo-16bits)
3345 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3346 |  |  |  | HR3345 (Lo-16bits)
3347 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3348 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3349 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3350 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3351 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3352 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3353 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3354 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3355 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3356 |  |  |  | HR3355 (Lo-16bits)
3357 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3358 |  |  |  | HR3357 (Lo-16bits)
3359 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3360 |  |  |  | HR3359 (Lo-16bits)
3361 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3362 |  |  |  | HR3361 (Lo-16bits)
3363 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3364 |  |  |  | HR3363 (Lo-16bits)
3365 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3366 |  |  |  | HR3365 (Lo-16bits)
3367 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3368 |  |  |  | HR3367 (Lo-16bits)
3369 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3370 |  |  |  | HR3369 (Lo-16bits)
3371 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3372 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3373 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3374 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3375 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3376 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3377 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3378 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3379 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3380 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3381 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3382 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3383 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3384 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3385 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3386 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3387 | DOC4:Idir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3388 | DOC4:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3389 | DOC4:Idir>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3390 | DOC4:Idir>>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3391 |  |  |  | HR3390 (Lo-16bits)
3392 | DOC4:Idir>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3393 |  |  |  | HR3392 (Lo-16bits)
3394 | DOC4:Idir>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3395 |  |  |  | HR3394 (Lo-16bits)
3396 | DOC4:Idir>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3397 |  |  |  | HR3396 (Lo-16bits)
3398 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3399 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3400 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3401 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3402 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3403 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3404 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3405 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3406 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3407 |  |  |  | HR3406 (Lo-16bits)
3408 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3409 |  |  |  | HR3408 (Lo-16bits)
3410 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3411 |  |  |  | HR3410 (Lo-16bits)
3412 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3413 |  |  |  | HR3412 (Lo-16bits)
3414 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3415 |  |  |  | HR3414 (Lo-16bits)
3416 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3417 |  |  |  | HR3416 (Lo-16bits)
3418 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3419 |  |  |  | HR3418 (Lo-16bits)
3420 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3421 |  |  |  | HR3420 (Lo-16bits)
3422 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3423 |  |  |  | HR3422 (Lo-16bits)
3424 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3425 |  |  |  | HR3424 (Lo-16bits)
3426 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3427 |  |  |  | HR3426 (Lo-16bits)
3428 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3429 |  |  |  | HR3428 (Lo-16bits)
3430 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3431 |  |  |  | HR3430 (Lo-16bits)
3432 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3433 |  |  |  | HR3432 (Lo-16bits)
3434 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3435 |  |  |  | HR3434 (Lo-16bits)
3436 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3437 |  |  |  | HR3436 (Lo-16bits)
3438 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3439 |  |  |  | HR3438 (Lo-16bits)
3440 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3441 |  |  |  | HR3440 (Lo-16bits)
3442 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3443 |  |  |  | HR3442 (Lo-16bits)
3444 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3445 |  |  |  | HR3444 (Lo-16bits)
3446 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3447 |  |  |  | HR3446 (Lo-16bits)
3448 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3449 |  |  |  | HR3448 (Lo-16bits)
3450 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3451 |  |  |  | HR3450 (Lo-16bits)
3452 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3453 |  |  |  | HR3452 (Lo-16bits)
3454 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3455 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3456 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3457 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3458 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3459 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3460 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3461 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3462 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3463 |  |  |  | HR3462 (Lo-16bits)
3464 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3465 |  |  |  | HR3464 (Lo-16bits)
3466 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3467 |  |  |  | HR3466 (Lo-16bits)
3468 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3469 |  |  |  | HR3468 (Lo-16bits)
3470 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3471 |  |  |  | HR3470 (Lo-16bits)
3472 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3473 |  |  |  | HR3472 (Lo-16bits)
3474 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3475 |  |  |  | HR3474 (Lo-16bits)
3476 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3477 |  |  |  | HR3476 (Lo-16bits)
3478 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3479 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3480 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3481 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3482 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3483 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3484 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3485 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3486 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3487 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3488 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3489 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3490 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3491 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3492 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3493 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3494 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3495 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3496 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3497 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3498 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3499 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3500 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3501 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3502 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3503 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3504 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3505 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3506 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3507 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3508 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3509 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3510 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3511 |  |  |  | HR3510 (Lo-16bits)
3512 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3513 |  |  |  | HR3512 (Lo-16bits)
3514 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3515 |  |  |  | HR3514 (Lo-16bits)
3516 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3517 |  |  |  | HR3516 (Lo-16bits)
3518 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3519 |  |  |  | HR3518 (Lo-16bits)
3520 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3521 |  |  |  | HR3520 (Lo-16bits)
3522 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3523 |  |  |  | HR3522 (Lo-16bits)
3524 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3525 |  |  |  | HR3524 (Lo-16bits)
3526 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3527 |  |  |  | HR3526 (Lo-16bits)
3528 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3529 |  |  |  | HR3528 (Lo-16bits)
3530 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3531 |  |  |  | HR3530 (Lo-16bits)
3532 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3533 |  |  |  | HR3532 (Lo-16bits)
3534 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3535 |  |  |  | HR3534 (Lo-16bits)
3536 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3537 |  |  |  | HR3536 (Lo-16bits)
3538 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3539 |  |  |  | HR3538 (Lo-16bits)
3540 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3541 |  |  |  | HR3540 (Lo-16bits)
3542 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3543 |  |  |  | HR3542 (Lo-16bits)
3544 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3545 |  |  |  | HR3544 (Lo-16bits)
3546 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3547 |  |  |  | HR3546 (Lo-16bits)
3548 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3549 |  |  |  | HR3548 (Lo-16bits)
3550 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3551 |  |  |  | HR3550 (Lo-16bits)
3552 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3553 |  |  |  | HR3552 (Lo-16bits)
3554 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3555 |  |  |  | HR3554 (Lo-16bits)
3556 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3557 |  |  |  | HR3556 (Lo-16bits)
3558 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3559 |  |  |  | HR3558 (Lo-16bits)
3560 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3561 |  |  |  | HR3560 (Lo-16bits)
3562 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3563 |  |  |  | HR3562 (Lo-16bits)
3564 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3565 |  |  |  | HR3564 (Lo-16bits)
3566 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3567 |  |  |  | HR3566 (Lo-16bits)
3568 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3569 |  |  |  | HR3568 (Lo-16bits)
3570 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3571 |  |  |  | HR3570 (Lo-16bits)
3572 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3573 |  |  |  | HR3572 (Lo-16bits)
3574 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3575 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3576 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3577 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3578 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3579 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3580 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3581 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3582 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3583 |  |  |  | HR3582 (Lo-16bits)
3584 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3585 |  |  |  | HR3584 (Lo-16bits)
3586 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3587 |  |  |  | HR3586 (Lo-16bits)
3588 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3589 |  |  |  | HR3588 (Lo-16bits)
3590 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3591 |  |  |  | HR3590 (Lo-16bits)
3592 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3593 |  |  |  | HR3592 (Lo-16bits)
3594 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3595 |  |  |  | HR3594 (Lo-16bits)
3596 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3597 |  |  |  | HR3596 (Lo-16bits)
3598 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3599 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3600 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3601 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3602 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3603 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3604 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3605 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3606 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3607 |  |  |  | HR3606 (Lo-16bits)
3608 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3609 |  |  |  | HR3608 (Lo-16bits)
3610 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3611 |  |  |  | HR3610 (Lo-16bits)
3612 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3613 |  |  |  | HR3612 (Lo-16bits)
3614 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3615 |  |  |  | HR3614 (Lo-16bits)
3616 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3617 |  |  |  | HR3616 (Lo-16bits)
3618 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3619 |  |  |  | HR3618 (Lo-16bits)
3620 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3621 |  |  |  | HR3620 (Lo-16bits)
3622 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3623 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3624 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3625 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3626 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3627 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3628 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3629 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3630 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3631 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3632 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3633 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3634 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3635 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3636 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3637 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3638 | NEF1:I0> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3639 | NEF1:I0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3640 | NEF1:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3641 | NEF1:I0> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3642 | NEF1:I0> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3643 |  |  |  | HR3642 (Lo-16bits)
3644 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3645 |  |  |  | HR3644 (Lo-16bits)
3646 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3647 |  |  |  | HR3646 (Lo-16bits)
3648 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3649 |  |  |  | HR3648 (Lo-16bits)
3650 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3651 |  |  |  | HR3650 (Lo-16bits)
3652 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3653 |  |  |  | HR3652 (Lo-16bits)
3654 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3655 |  |  |  | HR3654 (Lo-16bits)
3656 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3657 |  |  |  | HR3656 (Lo-16bits)
3658 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3659 |  |  |  | HR3658 (Lo-16bits)
3660 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3661 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3662 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3663 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3664 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3665 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3666 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3667 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3668 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3669 |  |  |  | HR3668 (Lo-16bits)
3670 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3671 |  |  |  | HR3670 (Lo-16bits)
3672 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3673 |  |  |  | HR3672 (Lo-16bits)
3674 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3675 |  |  |  | HR3674 (Lo-16bits)
3676 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3677 |  |  |  | HR3676 (Lo-16bits)
3678 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3679 |  |  |  | HR3678 (Lo-16bits)
3680 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3681 |  |  |  | HR3680 (Lo-16bits)
3682 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3683 |  |  |  | HR3682 (Lo-16bits)
3684 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3685 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3686 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3687 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3688 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3689 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3690 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3691 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3692 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3693 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3694 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3695 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3696 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3697 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3698 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3699 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3700 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3701 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3702 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3703 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3704 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3705 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3706 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3707 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3708 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3709 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3710 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3711 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3712 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3713 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3714 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3715 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3716 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3717 |  |  |  | HR3716 (Lo-16bits)
3718 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3719 |  |  |  | HR3718 (Lo-16bits)
3720 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3721 |  |  |  | HR3720 (Lo-16bits)
3722 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3723 |  |  |  | HR3722 (Lo-16bits)
3724 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3725 |  |  |  | HR3724 (Lo-16bits)
3726 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3727 |  |  |  | HR3726 (Lo-16bits)
3728 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3729 |  |  |  | HR3728 (Lo-16bits)
3730 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3731 |  |  |  | HR3730 (Lo-16bits)
3732 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3733 |  |  |  | HR3732 (Lo-16bits)
3734 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3735 |  |  |  | HR3734 (Lo-16bits)
3736 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3737 |  |  |  | HR3736 (Lo-16bits)
3738 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3739 |  |  |  | HR3738 (Lo-16bits)
3740 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3741 |  |  |  | HR3740 (Lo-16bits)
3742 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3743 |  |  |  | HR3742 (Lo-16bits)
3744 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3745 |  |  |  | HR3744 (Lo-16bits)
3746 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3747 |  |  |  | HR3746 (Lo-16bits)
3748 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3749 |  |  |  | HR3748 (Lo-16bits)
3750 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3751 |  |  |  | HR3750 (Lo-16bits)
3752 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3753 |  |  |  | HR3752 (Lo-16bits)
3754 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3755 |  |  |  | HR3754 (Lo-16bits)
3756 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3757 |  |  |  | HR3756 (Lo-16bits)
3758 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3759 |  |  |  | HR3758 (Lo-16bits)
3760 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3761 |  |  |  | HR3760 (Lo-16bits)
3762 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3763 |  |  |  | HR3762 (Lo-16bits)
3764 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3765 |  |  |  | HR3764 (Lo-16bits)
3766 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3767 |  |  |  | HR3766 (Lo-16bits)
3768 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3769 |  |  |  | HR3768 (Lo-16bits)
3770 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3771 |  |  |  | HR3770 (Lo-16bits)
3772 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3773 |  |  |  | HR3772 (Lo-16bits)
3774 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3775 |  |  |  | HR3774 (Lo-16bits)
3776 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3777 |  |  |  | HR3776 (Lo-16bits)
3778 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3779 |  |  |  | HR3778 (Lo-16bits)
3780 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3781 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3782 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3783 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3784 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3785 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3786 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3787 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3788 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3789 |  |  |  | HR3788 (Lo-16bits)
3790 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3791 |  |  |  | HR3790 (Lo-16bits)
3792 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3793 |  |  |  | HR3792 (Lo-16bits)
3794 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3795 |  |  |  | HR3794 (Lo-16bits)
3796 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3797 |  |  |  | HR3796 (Lo-16bits)
3798 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3799 |  |  |  | HR3798 (Lo-16bits)
3800 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3801 |  |  |  | HR3800 (Lo-16bits)
3802 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3803 |  |  |  | HR3802 (Lo-16bits)
3804 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3805 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3806 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3807 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3808 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3809 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3810 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3811 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3812 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3813 |  |  |  | HR3812 (Lo-16bits)
3814 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3815 |  |  |  | HR3814 (Lo-16bits)
3816 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3817 |  |  |  | HR3816 (Lo-16bits)
3818 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3819 |  |  |  | HR3818 (Lo-16bits)
3820 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3821 |  |  |  | HR3820 (Lo-16bits)
3822 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3823 |  |  |  | HR3822 (Lo-16bits)
3824 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3825 |  |  |  | HR3824 (Lo-16bits)
3826 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3827 |  |  |  | HR3826 (Lo-16bits)
3828 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3829 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3830 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3831 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3832 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3833 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3834 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3835 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3836 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3837 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3838 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3839 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3840 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3841 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3842 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3843 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3844 | NEF1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
3845 |  |  |  | HR3844 (Lo-16bits)
3846 | NEF1:Delay type | RW | 1 | 0=DT;1=IDMT
3847 | NEF1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
3848 |  |  |  | HR3847 (Lo-16bits)
3849 | NEF1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
3850 | NEF1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3851 | NEF1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3852 | NEF1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
3853 | NEF1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
3854 |  |  |  | HR3853 (Lo-16bits)
3855 | NEF1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
3856 |  |  |  | HR3855 (Lo-16bits)
3857 | NEF1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
3858 |  |  |  | HR3857 (Lo-16bits)
3859 | NEF1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
3860 |  |  |  | HR3859 (Lo-16bits)
3861 | NEF1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
3862 | NEF1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
3863 | NEF2:I0>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3864 | NEF2:I0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3865 | NEF2:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3866 | NEF2:I0>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3867 | NEF2:I0>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3868 |  |  |  | HR3867 (Lo-16bits)
3869 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3870 |  |  |  | HR3869 (Lo-16bits)
3871 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3872 |  |  |  | HR3871 (Lo-16bits)
3873 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3874 |  |  |  | HR3873 (Lo-16bits)
3875 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3876 |  |  |  | HR3875 (Lo-16bits)
3877 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3878 |  |  |  | HR3877 (Lo-16bits)
3879 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3880 |  |  |  | HR3879 (Lo-16bits)
3881 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3882 |  |  |  | HR3881 (Lo-16bits)
3883 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3884 |  |  |  | HR3883 (Lo-16bits)
3885 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3886 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3887 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3888 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3889 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3890 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3891 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3892 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3893 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3894 |  |  |  | HR3893 (Lo-16bits)
3895 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3896 |  |  |  | HR3895 (Lo-16bits)
3897 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3898 |  |  |  | HR3897 (Lo-16bits)
3899 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3900 |  |  |  | HR3899 (Lo-16bits)
3901 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3902 |  |  |  | HR3901 (Lo-16bits)
3903 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3904 |  |  |  | HR3903 (Lo-16bits)
3905 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3906 |  |  |  | HR3905 (Lo-16bits)
3907 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3908 |  |  |  | HR3907 (Lo-16bits)
3909 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3910 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3911 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3912 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3913 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3914 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3915 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3916 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3917 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3918 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3919 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3920 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3921 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3922 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3923 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3924 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3925 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3926 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3927 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3928 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3929 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3930 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3931 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3932 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3933 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3934 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3935 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3936 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3937 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3938 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3939 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3940 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3941 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3942 |  |  |  | HR3941 (Lo-16bits)
3943 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3944 |  |  |  | HR3943 (Lo-16bits)
3945 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3946 |  |  |  | HR3945 (Lo-16bits)
3947 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3948 |  |  |  | HR3947 (Lo-16bits)
3949 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3950 |  |  |  | HR3949 (Lo-16bits)
3951 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3952 |  |  |  | HR3951 (Lo-16bits)
3953 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3954 |  |  |  | HR3953 (Lo-16bits)
3955 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3956 |  |  |  | HR3955 (Lo-16bits)
3957 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3958 |  |  |  | HR3957 (Lo-16bits)
3959 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3960 |  |  |  | HR3959 (Lo-16bits)
3961 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3962 |  |  |  | HR3961 (Lo-16bits)
3963 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3964 |  |  |  | HR3963 (Lo-16bits)
3965 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3966 |  |  |  | HR3965 (Lo-16bits)
3967 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3968 |  |  |  | HR3967 (Lo-16bits)
3969 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3970 |  |  |  | HR3969 (Lo-16bits)
3971 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3972 |  |  |  | HR3971 (Lo-16bits)
3973 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3974 |  |  |  | HR3973 (Lo-16bits)
3975 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3976 |  |  |  | HR3975 (Lo-16bits)
3977 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3978 |  |  |  | HR3977 (Lo-16bits)
3979 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3980 |  |  |  | HR3979 (Lo-16bits)
3981 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3982 |  |  |  | HR3981 (Lo-16bits)
3983 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3984 |  |  |  | HR3983 (Lo-16bits)
3985 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3986 |  |  |  | HR3985 (Lo-16bits)
3987 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3988 |  |  |  | HR3987 (Lo-16bits)
3989 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3990 |  |  |  | HR3989 (Lo-16bits)
3991 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3992 |  |  |  | HR3991 (Lo-16bits)
3993 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3994 |  |  |  | HR3993 (Lo-16bits)
3995 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3996 |  |  |  | HR3995 (Lo-16bits)
3997 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3998 |  |  |  | HR3997 (Lo-16bits)
3999 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4000 |  |  |  | HR3999 (Lo-16bits)
4001 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4002 |  |  |  | HR4001 (Lo-16bits)
4003 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4004 |  |  |  | HR4003 (Lo-16bits)
4005 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4006 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4007 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4008 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4009 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4010 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4011 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4012 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4013 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4014 |  |  |  | HR4013 (Lo-16bits)
4015 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4016 |  |  |  | HR4015 (Lo-16bits)
4017 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4018 |  |  |  | HR4017 (Lo-16bits)
4019 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4020 |  |  |  | HR4019 (Lo-16bits)
4021 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4022 |  |  |  | HR4021 (Lo-16bits)
4023 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4024 |  |  |  | HR4023 (Lo-16bits)
4025 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4026 |  |  |  | HR4025 (Lo-16bits)
4027 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4028 |  |  |  | HR4027 (Lo-16bits)
4029 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4030 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4031 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4032 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4033 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4034 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4035 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4036 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4037 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4038 |  |  |  | HR4037 (Lo-16bits)
4039 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4040 |  |  |  | HR4039 (Lo-16bits)
4041 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4042 |  |  |  | HR4041 (Lo-16bits)
4043 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4044 |  |  |  | HR4043 (Lo-16bits)
4045 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4046 |  |  |  | HR4045 (Lo-16bits)
4047 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4048 |  |  |  | HR4047 (Lo-16bits)
4049 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4050 |  |  |  | HR4049 (Lo-16bits)
4051 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4052 |  |  |  | HR4051 (Lo-16bits)
4053 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4054 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4055 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4056 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4057 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4058 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4059 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4060 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4061 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4062 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4063 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4064 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4065 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4066 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4067 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4068 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4069 | NEF2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4070 |  |  |  | HR4069 (Lo-16bits)
4071 | NEF2:Delay type | RW | 1 | 0=DT;1=IDMT
4072 | NEF2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4073 |  |  |  | HR4072 (Lo-16bits)
4074 | NEF2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4075 | NEF2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4076 | NEF2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4077 | NEF2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4078 | NEF2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4079 |  |  |  | HR4078 (Lo-16bits)
4080 | NEF2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4081 |  |  |  | HR4080 (Lo-16bits)
4082 | NEF2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4083 |  |  |  | HR4082 (Lo-16bits)
4084 | NEF2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4085 |  |  |  | HR4084 (Lo-16bits)
4086 | NEF2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4087 | NEF2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4088 | NEF3:I0>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4089 | NEF3:I0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4090 | NEF3:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4091 | NEF3:I0>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4092 | NEF3:I0>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4093 |  |  |  | HR4092 (Lo-16bits)
4094 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4095 |  |  |  | HR4094 (Lo-16bits)
4096 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4097 |  |  |  | HR4096 (Lo-16bits)
4098 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4099 |  |  |  | HR4098 (Lo-16bits)
4100 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4101 |  |  |  | HR4100 (Lo-16bits)
4102 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4103 |  |  |  | HR4102 (Lo-16bits)
4104 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4105 |  |  |  | HR4104 (Lo-16bits)
4106 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4107 |  |  |  | HR4106 (Lo-16bits)
4108 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4109 |  |  |  | HR4108 (Lo-16bits)
4110 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4111 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4112 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4113 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4114 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4115 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4116 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4117 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4118 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4119 |  |  |  | HR4118 (Lo-16bits)
4120 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4121 |  |  |  | HR4120 (Lo-16bits)
4122 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4123 |  |  |  | HR4122 (Lo-16bits)
4124 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4125 |  |  |  | HR4124 (Lo-16bits)
4126 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4127 |  |  |  | HR4126 (Lo-16bits)
4128 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4129 |  |  |  | HR4128 (Lo-16bits)
4130 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4131 |  |  |  | HR4130 (Lo-16bits)
4132 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4133 |  |  |  | HR4132 (Lo-16bits)
4134 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4135 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4136 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4137 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4138 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4139 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4140 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4141 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4142 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4143 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4144 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4145 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4146 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4147 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4148 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4149 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4150 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4151 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4152 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4153 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4154 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4155 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4156 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4157 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4158 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4159 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4160 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4161 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4162 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4163 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4164 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4165 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4166 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4167 |  |  |  | HR4166 (Lo-16bits)
4168 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4169 |  |  |  | HR4168 (Lo-16bits)
4170 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4171 |  |  |  | HR4170 (Lo-16bits)
4172 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4173 |  |  |  | HR4172 (Lo-16bits)
4174 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4175 |  |  |  | HR4174 (Lo-16bits)
4176 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4177 |  |  |  | HR4176 (Lo-16bits)
4178 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4179 |  |  |  | HR4178 (Lo-16bits)
4180 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4181 |  |  |  | HR4180 (Lo-16bits)
4182 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4183 |  |  |  | HR4182 (Lo-16bits)
4184 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4185 |  |  |  | HR4184 (Lo-16bits)
4186 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4187 |  |  |  | HR4186 (Lo-16bits)
4188 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4189 |  |  |  | HR4188 (Lo-16bits)
4190 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4191 |  |  |  | HR4190 (Lo-16bits)
4192 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4193 |  |  |  | HR4192 (Lo-16bits)
4194 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4195 |  |  |  | HR4194 (Lo-16bits)
4196 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4197 |  |  |  | HR4196 (Lo-16bits)
4198 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4199 |  |  |  | HR4198 (Lo-16bits)
4200 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4201 |  |  |  | HR4200 (Lo-16bits)
4202 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4203 |  |  |  | HR4202 (Lo-16bits)
4204 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4205 |  |  |  | HR4204 (Lo-16bits)
4206 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4207 |  |  |  | HR4206 (Lo-16bits)
4208 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4209 |  |  |  | HR4208 (Lo-16bits)
4210 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4211 |  |  |  | HR4210 (Lo-16bits)
4212 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4213 |  |  |  | HR4212 (Lo-16bits)
4214 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4215 |  |  |  | HR4214 (Lo-16bits)
4216 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4217 |  |  |  | HR4216 (Lo-16bits)
4218 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4219 |  |  |  | HR4218 (Lo-16bits)
4220 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4221 |  |  |  | HR4220 (Lo-16bits)
4222 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4223 |  |  |  | HR4222 (Lo-16bits)
4224 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4225 |  |  |  | HR4224 (Lo-16bits)
4226 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4227 |  |  |  | HR4226 (Lo-16bits)
4228 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4229 |  |  |  | HR4228 (Lo-16bits)
4230 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4231 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4232 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4233 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4234 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4235 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4236 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4237 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4238 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4239 |  |  |  | HR4238 (Lo-16bits)
4240 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4241 |  |  |  | HR4240 (Lo-16bits)
4242 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4243 |  |  |  | HR4242 (Lo-16bits)
4244 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4245 |  |  |  | HR4244 (Lo-16bits)
4246 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4247 |  |  |  | HR4246 (Lo-16bits)
4248 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4249 |  |  |  | HR4248 (Lo-16bits)
4250 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4251 |  |  |  | HR4250 (Lo-16bits)
4252 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4253 |  |  |  | HR4252 (Lo-16bits)
4254 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4255 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4256 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4257 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4258 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4259 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4260 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4261 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4262 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4263 |  |  |  | HR4262 (Lo-16bits)
4264 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4265 |  |  |  | HR4264 (Lo-16bits)
4266 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4267 |  |  |  | HR4266 (Lo-16bits)
4268 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4269 |  |  |  | HR4268 (Lo-16bits)
4270 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4271 |  |  |  | HR4270 (Lo-16bits)
4272 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4273 |  |  |  | HR4272 (Lo-16bits)
4274 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4275 |  |  |  | HR4274 (Lo-16bits)
4276 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4277 |  |  |  | HR4276 (Lo-16bits)
4278 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4279 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4280 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4281 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4282 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4283 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4284 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4285 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4286 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4287 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4288 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4289 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4290 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4291 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4292 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4293 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4294 | NEF3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4295 |  |  |  | HR4294 (Lo-16bits)
4296 | NEF3:Delay type | RW | 1 | 0=DT;1=IDMT
4297 | NEF3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4298 |  |  |  | HR4297 (Lo-16bits)
4299 | NEF3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4300 | NEF3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4301 | NEF3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4302 | NEF3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4303 | NEF3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4304 |  |  |  | HR4303 (Lo-16bits)
4305 | NEF3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4306 |  |  |  | HR4305 (Lo-16bits)
4307 | NEF3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4308 |  |  |  | HR4307 (Lo-16bits)
4309 | NEF3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4310 |  |  |  | HR4309 (Lo-16bits)
4311 | NEF3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4312 | NEF3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4313 | NEF4:I0>>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4314 | NEF4:I0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4315 | NEF4:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4316 | NEF4:I0>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4317 | NEF4:I0>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4318 |  |  |  | HR4317 (Lo-16bits)
4319 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4320 |  |  |  | HR4319 (Lo-16bits)
4321 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4322 |  |  |  | HR4321 (Lo-16bits)
4323 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4324 |  |  |  | HR4323 (Lo-16bits)
4325 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4326 |  |  |  | HR4325 (Lo-16bits)
4327 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4328 |  |  |  | HR4327 (Lo-16bits)
4329 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4330 |  |  |  | HR4329 (Lo-16bits)
4331 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4332 |  |  |  | HR4331 (Lo-16bits)
4333 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4334 |  |  |  | HR4333 (Lo-16bits)
4335 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4336 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4337 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4338 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4339 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4340 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4341 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4342 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4343 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4344 |  |  |  | HR4343 (Lo-16bits)
4345 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4346 |  |  |  | HR4345 (Lo-16bits)
4347 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4348 |  |  |  | HR4347 (Lo-16bits)
4349 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4350 |  |  |  | HR4349 (Lo-16bits)
4351 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4352 |  |  |  | HR4351 (Lo-16bits)
4353 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4354 |  |  |  | HR4353 (Lo-16bits)
4355 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4356 |  |  |  | HR4355 (Lo-16bits)
4357 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4358 |  |  |  | HR4357 (Lo-16bits)
4359 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4360 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4361 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4362 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4363 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4364 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4365 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4366 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4367 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4368 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4369 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4370 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4371 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4372 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4373 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4374 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4375 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4376 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4377 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4378 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4379 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4380 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4381 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4382 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4383 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4384 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4385 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4386 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4387 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4388 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4389 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4390 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4391 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4392 |  |  |  | HR4391 (Lo-16bits)
4393 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4394 |  |  |  | HR4393 (Lo-16bits)
4395 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4396 |  |  |  | HR4395 (Lo-16bits)
4397 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4398 |  |  |  | HR4397 (Lo-16bits)
4399 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4400 |  |  |  | HR4399 (Lo-16bits)
4401 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4402 |  |  |  | HR4401 (Lo-16bits)
4403 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4404 |  |  |  | HR4403 (Lo-16bits)
4405 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4406 |  |  |  | HR4405 (Lo-16bits)
4407 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4408 |  |  |  | HR4407 (Lo-16bits)
4409 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4410 |  |  |  | HR4409 (Lo-16bits)
4411 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4412 |  |  |  | HR4411 (Lo-16bits)
4413 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4414 |  |  |  | HR4413 (Lo-16bits)
4415 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4416 |  |  |  | HR4415 (Lo-16bits)
4417 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4418 |  |  |  | HR4417 (Lo-16bits)
4419 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4420 |  |  |  | HR4419 (Lo-16bits)
4421 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4422 |  |  |  | HR4421 (Lo-16bits)
4423 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4424 |  |  |  | HR4423 (Lo-16bits)
4425 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4426 |  |  |  | HR4425 (Lo-16bits)
4427 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4428 |  |  |  | HR4427 (Lo-16bits)
4429 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4430 |  |  |  | HR4429 (Lo-16bits)
4431 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4432 |  |  |  | HR4431 (Lo-16bits)
4433 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4434 |  |  |  | HR4433 (Lo-16bits)
4435 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4436 |  |  |  | HR4435 (Lo-16bits)
4437 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4438 |  |  |  | HR4437 (Lo-16bits)
4439 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4440 |  |  |  | HR4439 (Lo-16bits)
4441 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4442 |  |  |  | HR4441 (Lo-16bits)
4443 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4444 |  |  |  | HR4443 (Lo-16bits)
4445 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4446 |  |  |  | HR4445 (Lo-16bits)
4447 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4448 |  |  |  | HR4447 (Lo-16bits)
4449 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4450 |  |  |  | HR4449 (Lo-16bits)
4451 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4452 |  |  |  | HR4451 (Lo-16bits)
4453 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4454 |  |  |  | HR4453 (Lo-16bits)
4455 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4456 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4457 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4458 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4459 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4460 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4461 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4462 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4463 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4464 |  |  |  | HR4463 (Lo-16bits)
4465 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4466 |  |  |  | HR4465 (Lo-16bits)
4467 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4468 |  |  |  | HR4467 (Lo-16bits)
4469 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4470 |  |  |  | HR4469 (Lo-16bits)
4471 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4472 |  |  |  | HR4471 (Lo-16bits)
4473 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4474 |  |  |  | HR4473 (Lo-16bits)
4475 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4476 |  |  |  | HR4475 (Lo-16bits)
4477 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4478 |  |  |  | HR4477 (Lo-16bits)
4479 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4480 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4481 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4482 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4483 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4484 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4485 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4486 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4487 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4488 |  |  |  | HR4487 (Lo-16bits)
4489 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4490 |  |  |  | HR4489 (Lo-16bits)
4491 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4492 |  |  |  | HR4491 (Lo-16bits)
4493 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4494 |  |  |  | HR4493 (Lo-16bits)
4495 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4496 |  |  |  | HR4495 (Lo-16bits)
4497 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4498 |  |  |  | HR4497 (Lo-16bits)
4499 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4500 |  |  |  | HR4499 (Lo-16bits)
4501 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4502 |  |  |  | HR4501 (Lo-16bits)
4503 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4504 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4505 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4506 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4507 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4508 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4509 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4510 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4511 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4512 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4513 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4514 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4515 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4516 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4517 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4518 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4519 | NEF4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4520 |  |  |  | HR4519 (Lo-16bits)
4521 | NEF4:Delay type | RW | 1 | 0=DT;1=IDMT
4522 | NEF4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4523 |  |  |  | HR4522 (Lo-16bits)
4524 | NEF4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4525 | NEF4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4526 | NEF4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4527 | NEF4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4528 | NEF4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4529 |  |  |  | HR4528 (Lo-16bits)
4530 | NEF4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4531 |  |  |  | HR4530 (Lo-16bits)
4532 | NEF4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4533 |  |  |  | HR4532 (Lo-16bits)
4534 | NEF4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4535 |  |  |  | HR4534 (Lo-16bits)
4536 | NEF4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4537 | NEF4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4538 | DEF1:I0dir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4539 | DEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4540 | DEF1:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4541 | DEF1:I0dir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4542 | DEF1:I0dir> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4543 |  |  |  | HR4542 (Lo-16bits)
4544 | DEF1:I0dir> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4545 |  |  |  | HR4544 (Lo-16bits)
4546 | DEF1:I0dir> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4547 |  |  |  | HR4546 (Lo-16bits)
4548 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4549 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4550 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4551 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4552 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4553 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4554 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4555 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4556 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4557 |  |  |  | HR4556 (Lo-16bits)
4558 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4559 |  |  |  | HR4558 (Lo-16bits)
4560 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4561 |  |  |  | HR4560 (Lo-16bits)
4562 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4563 |  |  |  | HR4562 (Lo-16bits)
4564 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4565 |  |  |  | HR4564 (Lo-16bits)
4566 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4567 |  |  |  | HR4566 (Lo-16bits)
4568 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4569 |  |  |  | HR4568 (Lo-16bits)
4570 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4571 |  |  |  | HR4570 (Lo-16bits)
4572 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4573 |  |  |  | HR4572 (Lo-16bits)
4574 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4575 |  |  |  | HR4574 (Lo-16bits)
4576 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4577 |  |  |  | HR4576 (Lo-16bits)
4578 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4579 |  |  |  | HR4578 (Lo-16bits)
4580 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4581 |  |  |  | HR4580 (Lo-16bits)
4582 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4583 |  |  |  | HR4582 (Lo-16bits)
4584 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4585 |  |  |  | HR4584 (Lo-16bits)
4586 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4587 |  |  |  | HR4586 (Lo-16bits)
4588 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4589 |  |  |  | HR4588 (Lo-16bits)
4590 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4591 |  |  |  | HR4590 (Lo-16bits)
4592 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4593 |  |  |  | HR4592 (Lo-16bits)
4594 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4595 |  |  |  | HR4594 (Lo-16bits)
4596 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4597 |  |  |  | HR4596 (Lo-16bits)
4598 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4599 |  |  |  | HR4598 (Lo-16bits)
4600 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4601 |  |  |  | HR4600 (Lo-16bits)
4602 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4603 |  |  |  | HR4602 (Lo-16bits)
4604 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4605 |  |  |  | HR4604 (Lo-16bits)
4606 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4607 |  |  |  | HR4606 (Lo-16bits)
4608 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4609 |  |  |  | HR4608 (Lo-16bits)
4610 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4611 |  |  |  | HR4610 (Lo-16bits)
4612 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4613 |  |  |  | HR4612 (Lo-16bits)
4614 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4615 |  |  |  | HR4614 (Lo-16bits)
4616 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4617 |  |  |  | HR4616 (Lo-16bits)
4618 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4619 |  |  |  | HR4618 (Lo-16bits)
4620 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4621 |  |  |  | HR4620 (Lo-16bits)
4622 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4623 |  |  |  | HR4622 (Lo-16bits)
4624 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4625 |  |  |  | HR4624 (Lo-16bits)
4626 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4627 |  |  |  | HR4626 (Lo-16bits)
4628 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4629 |  |  |  | HR4628 (Lo-16bits)
4630 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4631 |  |  |  | HR4630 (Lo-16bits)
4632 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4633 |  |  |  | HR4632 (Lo-16bits)
4634 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4635 |  |  |  | HR4634 (Lo-16bits)
4636 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4637 |  |  |  | HR4636 (Lo-16bits)
4638 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4639 |  |  |  | HR4638 (Lo-16bits)
4640 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4641 |  |  |  | HR4640 (Lo-16bits)
4642 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4643 |  |  |  | HR4642 (Lo-16bits)
4644 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4645 |  |  |  | HR4644 (Lo-16bits)
4646 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4647 |  |  |  | HR4646 (Lo-16bits)
4648 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4649 |  |  |  | HR4648 (Lo-16bits)
4650 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4651 |  |  |  | HR4650 (Lo-16bits)
4652 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4653 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4654 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4655 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4656 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4657 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4658 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4659 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4660 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4661 |  |  |  | HR4660 (Lo-16bits)
4662 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4663 |  |  |  | HR4662 (Lo-16bits)
4664 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4665 |  |  |  | HR4664 (Lo-16bits)
4666 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4667 |  |  |  | HR4666 (Lo-16bits)
4668 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4669 |  |  |  | HR4668 (Lo-16bits)
4670 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4671 |  |  |  | HR4670 (Lo-16bits)
4672 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4673 |  |  |  | HR4672 (Lo-16bits)
4674 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4675 |  |  |  | HR4674 (Lo-16bits)
4676 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4677 |  |  |  | HR4676 (Lo-16bits)
4678 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4679 |  |  |  | HR4678 (Lo-16bits)
4680 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4681 |  |  |  | HR4680 (Lo-16bits)
4682 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4683 |  |  |  | HR4682 (Lo-16bits)
4684 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4685 |  |  |  | HR4684 (Lo-16bits)
4686 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4687 |  |  |  | HR4686 (Lo-16bits)
4688 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4689 |  |  |  | HR4688 (Lo-16bits)
4690 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4691 |  |  |  | HR4690 (Lo-16bits)
4692 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4693 |  |  |  | HR4692 (Lo-16bits)
4694 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4695 |  |  |  | HR4694 (Lo-16bits)
4696 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4697 |  |  |  | HR4696 (Lo-16bits)
4698 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4699 |  |  |  | HR4698 (Lo-16bits)
4700 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4701 |  |  |  | HR4700 (Lo-16bits)
4702 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4703 |  |  |  | HR4702 (Lo-16bits)
4704 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4705 |  |  |  | HR4704 (Lo-16bits)
4706 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4707 |  |  |  | HR4706 (Lo-16bits)
4708 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4709 |  |  |  | HR4708 (Lo-16bits)
4710 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4711 |  |  |  | HR4710 (Lo-16bits)
4712 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4713 |  |  |  | HR4712 (Lo-16bits)
4714 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4715 |  |  |  | HR4714 (Lo-16bits)
4716 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4717 |  |  |  | HR4716 (Lo-16bits)
4718 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4719 |  |  |  | HR4718 (Lo-16bits)
4720 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4721 |  |  |  | HR4720 (Lo-16bits)
4722 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4723 |  |  |  | HR4722 (Lo-16bits)
4724 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4725 |  |  |  | HR4724 (Lo-16bits)
4726 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4727 |  |  |  | HR4726 (Lo-16bits)
4728 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4729 |  |  |  | HR4728 (Lo-16bits)
4730 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4731 |  |  |  | HR4730 (Lo-16bits)
4732 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4733 |  |  |  | HR4732 (Lo-16bits)
4734 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4735 |  |  |  | HR4734 (Lo-16bits)
4736 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4737 |  |  |  | HR4736 (Lo-16bits)
4738 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4739 |  |  |  | HR4738 (Lo-16bits)
4740 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4741 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4742 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4743 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4744 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4745 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4746 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4747 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4748 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4749 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4750 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4751 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4752 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4753 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4754 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4755 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4756 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4757 |  |  |  | HR4756 (Lo-16bits)
4758 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4759 |  |  |  | HR4758 (Lo-16bits)
4760 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4761 |  |  |  | HR4760 (Lo-16bits)
4762 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4763 |  |  |  | HR4762 (Lo-16bits)
4764 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4765 |  |  |  | HR4764 (Lo-16bits)
4766 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4767 |  |  |  | HR4766 (Lo-16bits)
4768 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4769 |  |  |  | HR4768 (Lo-16bits)
4770 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4771 |  |  |  | HR4770 (Lo-16bits)
4772 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4773 |  |  |  | HR4772 (Lo-16bits)
4774 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4775 |  |  |  | HR4774 (Lo-16bits)
4776 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4777 |  |  |  | HR4776 (Lo-16bits)
4778 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4779 |  |  |  | HR4778 (Lo-16bits)
4780 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4781 |  |  |  | HR4780 (Lo-16bits)
4782 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4783 |  |  |  | HR4782 (Lo-16bits)
4784 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4785 |  |  |  | HR4784 (Lo-16bits)
4786 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4787 |  |  |  | HR4786 (Lo-16bits)
4788 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4789 |  |  |  | HR4788 (Lo-16bits)
4790 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4791 |  |  |  | HR4790 (Lo-16bits)
4792 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4793 |  |  |  | HR4792 (Lo-16bits)
4794 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4795 |  |  |  | HR4794 (Lo-16bits)
4796 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4797 |  |  |  | HR4796 (Lo-16bits)
4798 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4799 |  |  |  | HR4798 (Lo-16bits)
4800 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4801 |  |  |  | HR4800 (Lo-16bits)
4802 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4803 |  |  |  | HR4802 (Lo-16bits)
4804 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4805 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4806 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4807 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4808 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4809 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4810 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4811 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4812 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4813 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4814 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4815 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4816 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4817 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4818 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4819 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4820 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4821 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4822 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4823 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4824 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4825 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4826 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4827 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4828 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4829 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4830 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4831 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4832 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4833 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4834 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4835 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4836 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4837 |  |  |  | HR4836 (Lo-16bits)
4838 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4839 |  |  |  | HR4838 (Lo-16bits)
4840 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4841 |  |  |  | HR4840 (Lo-16bits)
4842 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4843 |  |  |  | HR4842 (Lo-16bits)
4844 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4845 |  |  |  | HR4844 (Lo-16bits)
4846 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4847 |  |  |  | HR4846 (Lo-16bits)
4848 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4849 |  |  |  | HR4848 (Lo-16bits)
4850 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4851 |  |  |  | HR4850 (Lo-16bits)
4852 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4853 |  |  |  | HR4852 (Lo-16bits)
4854 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4855 |  |  |  | HR4854 (Lo-16bits)
4856 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4857 |  |  |  | HR4856 (Lo-16bits)
4858 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4859 |  |  |  | HR4858 (Lo-16bits)
4860 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4861 |  |  |  | HR4860 (Lo-16bits)
4862 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4863 |  |  |  | HR4862 (Lo-16bits)
4864 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4865 |  |  |  | HR4864 (Lo-16bits)
4866 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4867 |  |  |  | HR4866 (Lo-16bits)
4868 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4869 |  |  |  | HR4868 (Lo-16bits)
4870 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4871 |  |  |  | HR4870 (Lo-16bits)
4872 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4873 |  |  |  | HR4872 (Lo-16bits)
4874 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4875 |  |  |  | HR4874 (Lo-16bits)
4876 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4877 |  |  |  | HR4876 (Lo-16bits)
4878 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4879 |  |  |  | HR4878 (Lo-16bits)
4880 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4881 |  |  |  | HR4880 (Lo-16bits)
4882 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4883 |  |  |  | HR4882 (Lo-16bits)
4884 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4885 |  |  |  | HR4884 (Lo-16bits)
4886 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4887 |  |  |  | HR4886 (Lo-16bits)
4888 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4889 |  |  |  | HR4888 (Lo-16bits)
4890 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4891 |  |  |  | HR4890 (Lo-16bits)
4892 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4893 |  |  |  | HR4892 (Lo-16bits)
4894 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4895 |  |  |  | HR4894 (Lo-16bits)
4896 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4897 |  |  |  | HR4896 (Lo-16bits)
4898 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4899 |  |  |  | HR4898 (Lo-16bits)
4900 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4901 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4902 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4903 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4904 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4905 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4906 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4907 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4908 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4909 |  |  |  | HR4908 (Lo-16bits)
4910 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4911 |  |  |  | HR4910 (Lo-16bits)
4912 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4913 |  |  |  | HR4912 (Lo-16bits)
4914 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4915 |  |  |  | HR4914 (Lo-16bits)
4916 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4917 |  |  |  | HR4916 (Lo-16bits)
4918 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4919 |  |  |  | HR4918 (Lo-16bits)
4920 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4921 |  |  |  | HR4920 (Lo-16bits)
4922 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4923 |  |  |  | HR4922 (Lo-16bits)
4924 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4925 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4926 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4927 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4928 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4929 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4930 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4931 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4932 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4933 |  |  |  | HR4932 (Lo-16bits)
4934 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4935 |  |  |  | HR4934 (Lo-16bits)
4936 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4937 |  |  |  | HR4936 (Lo-16bits)
4938 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4939 |  |  |  | HR4938 (Lo-16bits)
4940 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4941 |  |  |  | HR4940 (Lo-16bits)
4942 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4943 |  |  |  | HR4942 (Lo-16bits)
4944 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4945 |  |  |  | HR4944 (Lo-16bits)
4946 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4947 |  |  |  | HR4946 (Lo-16bits)
4948 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4949 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4950 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4951 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4952 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4953 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4954 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4955 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4956 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4957 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4958 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4959 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4960 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4961 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4962 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4963 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4964 | DEF2:I0dir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4965 | DEF2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4966 | DEF2:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4967 | DEF2:I0dir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4968 | DEF2:I0dir>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4969 |  |  |  | HR4968 (Lo-16bits)
4970 | DEF2:I0dir>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4971 |  |  |  | HR4970 (Lo-16bits)
4972 | DEF2:I0dir>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4973 |  |  |  | HR4972 (Lo-16bits)
4974 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4975 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4976 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4977 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4978 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4979 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4980 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4981 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4982 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4983 |  |  |  | HR4982 (Lo-16bits)
4984 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4985 |  |  |  | HR4984 (Lo-16bits)
4986 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4987 |  |  |  | HR4986 (Lo-16bits)
4988 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4989 |  |  |  | HR4988 (Lo-16bits)
4990 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4991 |  |  |  | HR4990 (Lo-16bits)
4992 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4993 |  |  |  | HR4992 (Lo-16bits)
4994 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4995 |  |  |  | HR4994 (Lo-16bits)
4996 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4997 |  |  |  | HR4996 (Lo-16bits)
4998 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4999 |  |  |  | HR4998 (Lo-16bits)
5000 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5001 |  |  |  | HR5000 (Lo-16bits)
5002 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5003 |  |  |  | HR5002 (Lo-16bits)
5004 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5005 |  |  |  | HR5004 (Lo-16bits)
5006 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5007 |  |  |  | HR5006 (Lo-16bits)
5008 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5009 |  |  |  | HR5008 (Lo-16bits)
5010 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5011 |  |  |  | HR5010 (Lo-16bits)
5012 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5013 |  |  |  | HR5012 (Lo-16bits)
5014 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5015 |  |  |  | HR5014 (Lo-16bits)
5016 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5017 |  |  |  | HR5016 (Lo-16bits)
5018 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5019 |  |  |  | HR5018 (Lo-16bits)
5020 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5021 |  |  |  | HR5020 (Lo-16bits)
5022 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5023 |  |  |  | HR5022 (Lo-16bits)
5024 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5025 |  |  |  | HR5024 (Lo-16bits)
5026 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5027 |  |  |  | HR5026 (Lo-16bits)
5028 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5029 |  |  |  | HR5028 (Lo-16bits)
5030 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5031 |  |  |  | HR5030 (Lo-16bits)
5032 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5033 |  |  |  | HR5032 (Lo-16bits)
5034 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5035 |  |  |  | HR5034 (Lo-16bits)
5036 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5037 |  |  |  | HR5036 (Lo-16bits)
5038 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5039 |  |  |  | HR5038 (Lo-16bits)
5040 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5041 |  |  |  | HR5040 (Lo-16bits)
5042 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5043 |  |  |  | HR5042 (Lo-16bits)
5044 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5045 |  |  |  | HR5044 (Lo-16bits)
5046 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5047 |  |  |  | HR5046 (Lo-16bits)
5048 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5049 |  |  |  | HR5048 (Lo-16bits)
5050 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5051 |  |  |  | HR5050 (Lo-16bits)
5052 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5053 |  |  |  | HR5052 (Lo-16bits)
5054 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5055 |  |  |  | HR5054 (Lo-16bits)
5056 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5057 |  |  |  | HR5056 (Lo-16bits)
5058 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5059 |  |  |  | HR5058 (Lo-16bits)
5060 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5061 |  |  |  | HR5060 (Lo-16bits)
5062 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5063 |  |  |  | HR5062 (Lo-16bits)
5064 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5065 |  |  |  | HR5064 (Lo-16bits)
5066 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5067 |  |  |  | HR5066 (Lo-16bits)
5068 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5069 |  |  |  | HR5068 (Lo-16bits)
5070 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5071 |  |  |  | HR5070 (Lo-16bits)
5072 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5073 |  |  |  | HR5072 (Lo-16bits)
5074 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5075 |  |  |  | HR5074 (Lo-16bits)
5076 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5077 |  |  |  | HR5076 (Lo-16bits)
5078 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5079 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5080 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5081 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5082 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5083 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5084 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5085 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5086 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5087 |  |  |  | HR5086 (Lo-16bits)
5088 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5089 |  |  |  | HR5088 (Lo-16bits)
5090 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5091 |  |  |  | HR5090 (Lo-16bits)
5092 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5093 |  |  |  | HR5092 (Lo-16bits)
5094 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5095 |  |  |  | HR5094 (Lo-16bits)
5096 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5097 |  |  |  | HR5096 (Lo-16bits)
5098 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5099 |  |  |  | HR5098 (Lo-16bits)
5100 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5101 |  |  |  | HR5100 (Lo-16bits)
5102 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5103 |  |  |  | HR5102 (Lo-16bits)
5104 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5105 |  |  |  | HR5104 (Lo-16bits)
5106 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5107 |  |  |  | HR5106 (Lo-16bits)
5108 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5109 |  |  |  | HR5108 (Lo-16bits)
5110 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5111 |  |  |  | HR5110 (Lo-16bits)
5112 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5113 |  |  |  | HR5112 (Lo-16bits)
5114 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5115 |  |  |  | HR5114 (Lo-16bits)
5116 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5117 |  |  |  | HR5116 (Lo-16bits)
5118 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5119 |  |  |  | HR5118 (Lo-16bits)
5120 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5121 |  |  |  | HR5120 (Lo-16bits)
5122 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5123 |  |  |  | HR5122 (Lo-16bits)
5124 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5125 |  |  |  | HR5124 (Lo-16bits)
5126 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5127 |  |  |  | HR5126 (Lo-16bits)
5128 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5129 |  |  |  | HR5128 (Lo-16bits)
5130 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5131 |  |  |  | HR5130 (Lo-16bits)
5132 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5133 |  |  |  | HR5132 (Lo-16bits)
5134 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5135 |  |  |  | HR5134 (Lo-16bits)
5136 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5137 |  |  |  | HR5136 (Lo-16bits)
5138 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5139 |  |  |  | HR5138 (Lo-16bits)
5140 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5141 |  |  |  | HR5140 (Lo-16bits)
5142 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5143 |  |  |  | HR5142 (Lo-16bits)
5144 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5145 |  |  |  | HR5144 (Lo-16bits)
5146 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5147 |  |  |  | HR5146 (Lo-16bits)
5148 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5149 |  |  |  | HR5148 (Lo-16bits)
5150 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5151 |  |  |  | HR5150 (Lo-16bits)
5152 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5153 |  |  |  | HR5152 (Lo-16bits)
5154 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5155 |  |  |  | HR5154 (Lo-16bits)
5156 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5157 |  |  |  | HR5156 (Lo-16bits)
5158 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5159 |  |  |  | HR5158 (Lo-16bits)
5160 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5161 |  |  |  | HR5160 (Lo-16bits)
5162 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5163 |  |  |  | HR5162 (Lo-16bits)
5164 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5165 |  |  |  | HR5164 (Lo-16bits)
5166 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5167 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5168 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5169 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5170 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5171 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5172 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5173 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5174 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5175 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5176 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5177 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5178 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5179 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5180 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5181 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5182 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5183 |  |  |  | HR5182 (Lo-16bits)
5184 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5185 |  |  |  | HR5184 (Lo-16bits)
5186 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5187 |  |  |  | HR5186 (Lo-16bits)
5188 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5189 |  |  |  | HR5188 (Lo-16bits)
5190 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5191 |  |  |  | HR5190 (Lo-16bits)
5192 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5193 |  |  |  | HR5192 (Lo-16bits)
5194 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5195 |  |  |  | HR5194 (Lo-16bits)
5196 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5197 |  |  |  | HR5196 (Lo-16bits)
5198 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5199 |  |  |  | HR5198 (Lo-16bits)
5200 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5201 |  |  |  | HR5200 (Lo-16bits)
5202 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5203 |  |  |  | HR5202 (Lo-16bits)
5204 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5205 |  |  |  | HR5204 (Lo-16bits)
5206 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5207 |  |  |  | HR5206 (Lo-16bits)
5208 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5209 |  |  |  | HR5208 (Lo-16bits)
5210 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5211 |  |  |  | HR5210 (Lo-16bits)
5212 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5213 |  |  |  | HR5212 (Lo-16bits)
5214 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5215 |  |  |  | HR5214 (Lo-16bits)
5216 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5217 |  |  |  | HR5216 (Lo-16bits)
5218 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5219 |  |  |  | HR5218 (Lo-16bits)
5220 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5221 |  |  |  | HR5220 (Lo-16bits)
5222 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5223 |  |  |  | HR5222 (Lo-16bits)
5224 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5225 |  |  |  | HR5224 (Lo-16bits)
5226 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5227 |  |  |  | HR5226 (Lo-16bits)
5228 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5229 |  |  |  | HR5228 (Lo-16bits)
5230 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5231 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5232 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5233 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5234 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5235 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5236 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5237 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5238 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5239 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5240 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5241 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5242 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5243 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5244 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5245 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5246 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5247 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5248 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5249 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5250 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5251 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5252 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5253 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5254 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5255 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5256 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5257 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5258 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5259 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5260 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5261 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5262 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5263 |  |  |  | HR5262 (Lo-16bits)
5264 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5265 |  |  |  | HR5264 (Lo-16bits)
5266 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5267 |  |  |  | HR5266 (Lo-16bits)
5268 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5269 |  |  |  | HR5268 (Lo-16bits)
5270 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5271 |  |  |  | HR5270 (Lo-16bits)
5272 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5273 |  |  |  | HR5272 (Lo-16bits)
5274 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5275 |  |  |  | HR5274 (Lo-16bits)
5276 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5277 |  |  |  | HR5276 (Lo-16bits)
5278 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5279 |  |  |  | HR5278 (Lo-16bits)
5280 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5281 |  |  |  | HR5280 (Lo-16bits)
5282 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5283 |  |  |  | HR5282 (Lo-16bits)
5284 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5285 |  |  |  | HR5284 (Lo-16bits)
5286 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5287 |  |  |  | HR5286 (Lo-16bits)
5288 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5289 |  |  |  | HR5288 (Lo-16bits)
5290 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5291 |  |  |  | HR5290 (Lo-16bits)
5292 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5293 |  |  |  | HR5292 (Lo-16bits)
5294 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5295 |  |  |  | HR5294 (Lo-16bits)
5296 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5297 |  |  |  | HR5296 (Lo-16bits)
5298 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5299 |  |  |  | HR5298 (Lo-16bits)
5300 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5301 |  |  |  | HR5300 (Lo-16bits)
5302 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5303 |  |  |  | HR5302 (Lo-16bits)
5304 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5305 |  |  |  | HR5304 (Lo-16bits)
5306 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5307 |  |  |  | HR5306 (Lo-16bits)
5308 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5309 |  |  |  | HR5308 (Lo-16bits)
5310 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5311 |  |  |  | HR5310 (Lo-16bits)
5312 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5313 |  |  |  | HR5312 (Lo-16bits)
5314 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5315 |  |  |  | HR5314 (Lo-16bits)
5316 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5317 |  |  |  | HR5316 (Lo-16bits)
5318 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5319 |  |  |  | HR5318 (Lo-16bits)
5320 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5321 |  |  |  | HR5320 (Lo-16bits)
5322 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5323 |  |  |  | HR5322 (Lo-16bits)
5324 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5325 |  |  |  | HR5324 (Lo-16bits)
5326 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5327 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5328 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5329 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5330 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5331 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5332 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5333 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5334 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5335 |  |  |  | HR5334 (Lo-16bits)
5336 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5337 |  |  |  | HR5336 (Lo-16bits)
5338 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5339 |  |  |  | HR5338 (Lo-16bits)
5340 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5341 |  |  |  | HR5340 (Lo-16bits)
5342 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5343 |  |  |  | HR5342 (Lo-16bits)
5344 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5345 |  |  |  | HR5344 (Lo-16bits)
5346 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5347 |  |  |  | HR5346 (Lo-16bits)
5348 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5349 |  |  |  | HR5348 (Lo-16bits)
5350 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5351 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5352 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5353 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5354 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5355 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5356 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5357 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5358 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5359 |  |  |  | HR5358 (Lo-16bits)
5360 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5361 |  |  |  | HR5360 (Lo-16bits)
5362 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5363 |  |  |  | HR5362 (Lo-16bits)
5364 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5365 |  |  |  | HR5364 (Lo-16bits)
5366 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5367 |  |  |  | HR5366 (Lo-16bits)
5368 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5369 |  |  |  | HR5368 (Lo-16bits)
5370 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5371 |  |  |  | HR5370 (Lo-16bits)
5372 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5373 |  |  |  | HR5372 (Lo-16bits)
5374 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5375 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5376 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5377 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5378 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5379 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5380 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5381 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5382 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5383 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5384 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5385 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5386 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5387 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5388 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5389 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5390 | DEF3:I0dir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5391 | DEF3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5392 | DEF3:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5393 | DEF3:I0dir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5394 | DEF3:I0dir>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5395 |  |  |  | HR5394 (Lo-16bits)
5396 | DEF3:I0dir>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5397 |  |  |  | HR5396 (Lo-16bits)
5398 | DEF3:I0dir>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5399 |  |  |  | HR5398 (Lo-16bits)
5400 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5401 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5402 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5403 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5404 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5405 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5406 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5407 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5408 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5409 |  |  |  | HR5408 (Lo-16bits)
5410 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5411 |  |  |  | HR5410 (Lo-16bits)
5412 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5413 |  |  |  | HR5412 (Lo-16bits)
5414 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5415 |  |  |  | HR5414 (Lo-16bits)
5416 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5417 |  |  |  | HR5416 (Lo-16bits)
5418 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5419 |  |  |  | HR5418 (Lo-16bits)
5420 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5421 |  |  |  | HR5420 (Lo-16bits)
5422 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5423 |  |  |  | HR5422 (Lo-16bits)
5424 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5425 |  |  |  | HR5424 (Lo-16bits)
5426 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5427 |  |  |  | HR5426 (Lo-16bits)
5428 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5429 |  |  |  | HR5428 (Lo-16bits)
5430 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5431 |  |  |  | HR5430 (Lo-16bits)
5432 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5433 |  |  |  | HR5432 (Lo-16bits)
5434 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5435 |  |  |  | HR5434 (Lo-16bits)
5436 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5437 |  |  |  | HR5436 (Lo-16bits)
5438 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5439 |  |  |  | HR5438 (Lo-16bits)
5440 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5441 |  |  |  | HR5440 (Lo-16bits)
5442 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5443 |  |  |  | HR5442 (Lo-16bits)
5444 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5445 |  |  |  | HR5444 (Lo-16bits)
5446 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5447 |  |  |  | HR5446 (Lo-16bits)
5448 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5449 |  |  |  | HR5448 (Lo-16bits)
5450 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5451 |  |  |  | HR5450 (Lo-16bits)
5452 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5453 |  |  |  | HR5452 (Lo-16bits)
5454 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5455 |  |  |  | HR5454 (Lo-16bits)
5456 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5457 |  |  |  | HR5456 (Lo-16bits)
5458 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5459 |  |  |  | HR5458 (Lo-16bits)
5460 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5461 |  |  |  | HR5460 (Lo-16bits)
5462 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5463 |  |  |  | HR5462 (Lo-16bits)
5464 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5465 |  |  |  | HR5464 (Lo-16bits)
5466 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5467 |  |  |  | HR5466 (Lo-16bits)
5468 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5469 |  |  |  | HR5468 (Lo-16bits)
5470 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5471 |  |  |  | HR5470 (Lo-16bits)
5472 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5473 |  |  |  | HR5472 (Lo-16bits)
5474 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5475 |  |  |  | HR5474 (Lo-16bits)
5476 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5477 |  |  |  | HR5476 (Lo-16bits)
5478 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5479 |  |  |  | HR5478 (Lo-16bits)
5480 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5481 |  |  |  | HR5480 (Lo-16bits)
5482 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5483 |  |  |  | HR5482 (Lo-16bits)
5484 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5485 |  |  |  | HR5484 (Lo-16bits)
5486 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5487 |  |  |  | HR5486 (Lo-16bits)
5488 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5489 |  |  |  | HR5488 (Lo-16bits)
5490 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5491 |  |  |  | HR5490 (Lo-16bits)
5492 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5493 |  |  |  | HR5492 (Lo-16bits)
5494 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5495 |  |  |  | HR5494 (Lo-16bits)
5496 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5497 |  |  |  | HR5496 (Lo-16bits)
5498 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5499 |  |  |  | HR5498 (Lo-16bits)
5500 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5501 |  |  |  | HR5500 (Lo-16bits)
5502 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5503 |  |  |  | HR5502 (Lo-16bits)
5504 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5505 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5506 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5507 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5508 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5509 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5510 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5511 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5512 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5513 |  |  |  | HR5512 (Lo-16bits)
5514 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5515 |  |  |  | HR5514 (Lo-16bits)
5516 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5517 |  |  |  | HR5516 (Lo-16bits)
5518 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5519 |  |  |  | HR5518 (Lo-16bits)
5520 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5521 |  |  |  | HR5520 (Lo-16bits)
5522 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5523 |  |  |  | HR5522 (Lo-16bits)
5524 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5525 |  |  |  | HR5524 (Lo-16bits)
5526 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5527 |  |  |  | HR5526 (Lo-16bits)
5528 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5529 |  |  |  | HR5528 (Lo-16bits)
5530 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5531 |  |  |  | HR5530 (Lo-16bits)
5532 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5533 |  |  |  | HR5532 (Lo-16bits)
5534 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5535 |  |  |  | HR5534 (Lo-16bits)
5536 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5537 |  |  |  | HR5536 (Lo-16bits)
5538 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5539 |  |  |  | HR5538 (Lo-16bits)
5540 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5541 |  |  |  | HR5540 (Lo-16bits)
5542 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5543 |  |  |  | HR5542 (Lo-16bits)
5544 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5545 |  |  |  | HR5544 (Lo-16bits)
5546 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5547 |  |  |  | HR5546 (Lo-16bits)
5548 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5549 |  |  |  | HR5548 (Lo-16bits)
5550 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5551 |  |  |  | HR5550 (Lo-16bits)
5552 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5553 |  |  |  | HR5552 (Lo-16bits)
5554 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5555 |  |  |  | HR5554 (Lo-16bits)
5556 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5557 |  |  |  | HR5556 (Lo-16bits)
5558 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5559 |  |  |  | HR5558 (Lo-16bits)
5560 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5561 |  |  |  | HR5560 (Lo-16bits)
5562 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5563 |  |  |  | HR5562 (Lo-16bits)
5564 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5565 |  |  |  | HR5564 (Lo-16bits)
5566 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5567 |  |  |  | HR5566 (Lo-16bits)
5568 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5569 |  |  |  | HR5568 (Lo-16bits)
5570 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5571 |  |  |  | HR5570 (Lo-16bits)
5572 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5573 |  |  |  | HR5572 (Lo-16bits)
5574 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5575 |  |  |  | HR5574 (Lo-16bits)
5576 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5577 |  |  |  | HR5576 (Lo-16bits)
5578 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5579 |  |  |  | HR5578 (Lo-16bits)
5580 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5581 |  |  |  | HR5580 (Lo-16bits)
5582 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5583 |  |  |  | HR5582 (Lo-16bits)
5584 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5585 |  |  |  | HR5584 (Lo-16bits)
5586 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5587 |  |  |  | HR5586 (Lo-16bits)
5588 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5589 |  |  |  | HR5588 (Lo-16bits)
5590 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5591 |  |  |  | HR5590 (Lo-16bits)
5592 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5593 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5594 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5595 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5596 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5597 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5598 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5599 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5600 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5601 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5602 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5603 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5604 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5605 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5606 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5607 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5608 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5609 |  |  |  | HR5608 (Lo-16bits)
5610 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5611 |  |  |  | HR5610 (Lo-16bits)
5612 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5613 |  |  |  | HR5612 (Lo-16bits)
5614 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5615 |  |  |  | HR5614 (Lo-16bits)
5616 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5617 |  |  |  | HR5616 (Lo-16bits)
5618 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5619 |  |  |  | HR5618 (Lo-16bits)
5620 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5621 |  |  |  | HR5620 (Lo-16bits)
5622 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5623 |  |  |  | HR5622 (Lo-16bits)
5624 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5625 |  |  |  | HR5624 (Lo-16bits)
5626 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5627 |  |  |  | HR5626 (Lo-16bits)
5628 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5629 |  |  |  | HR5628 (Lo-16bits)
5630 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5631 |  |  |  | HR5630 (Lo-16bits)
5632 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5633 |  |  |  | HR5632 (Lo-16bits)
5634 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5635 |  |  |  | HR5634 (Lo-16bits)
5636 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5637 |  |  |  | HR5636 (Lo-16bits)
5638 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5639 |  |  |  | HR5638 (Lo-16bits)
5640 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5641 |  |  |  | HR5640 (Lo-16bits)
5642 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5643 |  |  |  | HR5642 (Lo-16bits)
5644 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5645 |  |  |  | HR5644 (Lo-16bits)
5646 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5647 |  |  |  | HR5646 (Lo-16bits)
5648 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5649 |  |  |  | HR5648 (Lo-16bits)
5650 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5651 |  |  |  | HR5650 (Lo-16bits)
5652 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5653 |  |  |  | HR5652 (Lo-16bits)
5654 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5655 |  |  |  | HR5654 (Lo-16bits)
5656 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5657 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5658 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5659 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5660 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5661 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5662 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5663 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5664 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5665 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5666 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5667 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5668 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5669 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5670 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5671 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5672 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5673 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5674 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5675 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5676 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5677 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5678 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5679 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5680 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5681 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5682 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5683 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5684 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5685 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5686 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5687 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5688 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5689 |  |  |  | HR5688 (Lo-16bits)
5690 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5691 |  |  |  | HR5690 (Lo-16bits)
5692 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5693 |  |  |  | HR5692 (Lo-16bits)
5694 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5695 |  |  |  | HR5694 (Lo-16bits)
5696 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5697 |  |  |  | HR5696 (Lo-16bits)
5698 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5699 |  |  |  | HR5698 (Lo-16bits)
5700 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5701 |  |  |  | HR5700 (Lo-16bits)
5702 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5703 |  |  |  | HR5702 (Lo-16bits)
5704 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5705 |  |  |  | HR5704 (Lo-16bits)
5706 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5707 |  |  |  | HR5706 (Lo-16bits)
5708 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5709 |  |  |  | HR5708 (Lo-16bits)
5710 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5711 |  |  |  | HR5710 (Lo-16bits)
5712 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5713 |  |  |  | HR5712 (Lo-16bits)
5714 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5715 |  |  |  | HR5714 (Lo-16bits)
5716 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5717 |  |  |  | HR5716 (Lo-16bits)
5718 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5719 |  |  |  | HR5718 (Lo-16bits)
5720 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5721 |  |  |  | HR5720 (Lo-16bits)
5722 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5723 |  |  |  | HR5722 (Lo-16bits)
5724 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5725 |  |  |  | HR5724 (Lo-16bits)
5726 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5727 |  |  |  | HR5726 (Lo-16bits)
5728 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5729 |  |  |  | HR5728 (Lo-16bits)
5730 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5731 |  |  |  | HR5730 (Lo-16bits)
5732 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5733 |  |  |  | HR5732 (Lo-16bits)
5734 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5735 |  |  |  | HR5734 (Lo-16bits)
5736 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5737 |  |  |  | HR5736 (Lo-16bits)
5738 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5739 |  |  |  | HR5738 (Lo-16bits)
5740 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5741 |  |  |  | HR5740 (Lo-16bits)
5742 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5743 |  |  |  | HR5742 (Lo-16bits)
5744 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5745 |  |  |  | HR5744 (Lo-16bits)
5746 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5747 |  |  |  | HR5746 (Lo-16bits)
5748 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5749 |  |  |  | HR5748 (Lo-16bits)
5750 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5751 |  |  |  | HR5750 (Lo-16bits)
5752 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5753 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5754 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5755 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5756 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5757 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5758 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5759 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5760 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5761 |  |  |  | HR5760 (Lo-16bits)
5762 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5763 |  |  |  | HR5762 (Lo-16bits)
5764 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5765 |  |  |  | HR5764 (Lo-16bits)
5766 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5767 |  |  |  | HR5766 (Lo-16bits)
5768 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5769 |  |  |  | HR5768 (Lo-16bits)
5770 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5771 |  |  |  | HR5770 (Lo-16bits)
5772 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5773 |  |  |  | HR5772 (Lo-16bits)
5774 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5775 |  |  |  | HR5774 (Lo-16bits)
5776 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5777 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5778 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5779 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5780 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5781 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5782 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5783 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5784 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5785 |  |  |  | HR5784 (Lo-16bits)
5786 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5787 |  |  |  | HR5786 (Lo-16bits)
5788 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5789 |  |  |  | HR5788 (Lo-16bits)
5790 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5791 |  |  |  | HR5790 (Lo-16bits)
5792 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5793 |  |  |  | HR5792 (Lo-16bits)
5794 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5795 |  |  |  | HR5794 (Lo-16bits)
5796 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5797 |  |  |  | HR5796 (Lo-16bits)
5798 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5799 |  |  |  | HR5798 (Lo-16bits)
5800 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5801 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5802 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5803 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5804 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5805 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5806 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5807 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5808 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5809 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5810 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5811 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5812 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5813 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5814 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5815 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5816 | DEF4:I0dir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5817 | DEF4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5818 | DEF4:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5819 | DEF4:I0dir>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5820 | DEF4:I0dir>>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5821 |  |  |  | HR5820 (Lo-16bits)
5822 | DEF4:I0dir>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5823 |  |  |  | HR5822 (Lo-16bits)
5824 | DEF4:I0dir>>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5825 |  |  |  | HR5824 (Lo-16bits)
5826 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5827 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5828 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5829 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5830 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5831 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5832 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5833 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5834 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5835 |  |  |  | HR5834 (Lo-16bits)
5836 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5837 |  |  |  | HR5836 (Lo-16bits)
5838 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5839 |  |  |  | HR5838 (Lo-16bits)
5840 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5841 |  |  |  | HR5840 (Lo-16bits)
5842 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5843 |  |  |  | HR5842 (Lo-16bits)
5844 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5845 |  |  |  | HR5844 (Lo-16bits)
5846 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5847 |  |  |  | HR5846 (Lo-16bits)
5848 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5849 |  |  |  | HR5848 (Lo-16bits)
5850 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5851 |  |  |  | HR5850 (Lo-16bits)
5852 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5853 |  |  |  | HR5852 (Lo-16bits)
5854 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5855 |  |  |  | HR5854 (Lo-16bits)
5856 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5857 |  |  |  | HR5856 (Lo-16bits)
5858 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5859 |  |  |  | HR5858 (Lo-16bits)
5860 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5861 |  |  |  | HR5860 (Lo-16bits)
5862 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5863 |  |  |  | HR5862 (Lo-16bits)
5864 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5865 |  |  |  | HR5864 (Lo-16bits)
5866 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5867 |  |  |  | HR5866 (Lo-16bits)
5868 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5869 |  |  |  | HR5868 (Lo-16bits)
5870 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5871 |  |  |  | HR5870 (Lo-16bits)
5872 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5873 |  |  |  | HR5872 (Lo-16bits)
5874 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5875 |  |  |  | HR5874 (Lo-16bits)
5876 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5877 |  |  |  | HR5876 (Lo-16bits)
5878 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5879 |  |  |  | HR5878 (Lo-16bits)
5880 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5881 |  |  |  | HR5880 (Lo-16bits)
5882 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5883 |  |  |  | HR5882 (Lo-16bits)
5884 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5885 |  |  |  | HR5884 (Lo-16bits)
5886 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5887 |  |  |  | HR5886 (Lo-16bits)
5888 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5889 |  |  |  | HR5888 (Lo-16bits)
5890 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5891 |  |  |  | HR5890 (Lo-16bits)
5892 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5893 |  |  |  | HR5892 (Lo-16bits)
5894 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5895 |  |  |  | HR5894 (Lo-16bits)
5896 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5897 |  |  |  | HR5896 (Lo-16bits)
5898 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5899 |  |  |  | HR5898 (Lo-16bits)
5900 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5901 |  |  |  | HR5900 (Lo-16bits)
5902 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5903 |  |  |  | HR5902 (Lo-16bits)
5904 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5905 |  |  |  | HR5904 (Lo-16bits)
5906 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5907 |  |  |  | HR5906 (Lo-16bits)
5908 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5909 |  |  |  | HR5908 (Lo-16bits)
5910 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5911 |  |  |  | HR5910 (Lo-16bits)
5912 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5913 |  |  |  | HR5912 (Lo-16bits)
5914 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5915 |  |  |  | HR5914 (Lo-16bits)
5916 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5917 |  |  |  | HR5916 (Lo-16bits)
5918 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5919 |  |  |  | HR5918 (Lo-16bits)
5920 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5921 |  |  |  | HR5920 (Lo-16bits)
5922 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5923 |  |  |  | HR5922 (Lo-16bits)
5924 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5925 |  |  |  | HR5924 (Lo-16bits)
5926 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5927 |  |  |  | HR5926 (Lo-16bits)
5928 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5929 |  |  |  | HR5928 (Lo-16bits)
5930 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5931 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5932 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5933 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5934 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5935 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5936 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5937 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5938 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5939 |  |  |  | HR5938 (Lo-16bits)
5940 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5941 |  |  |  | HR5940 (Lo-16bits)
5942 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5943 |  |  |  | HR5942 (Lo-16bits)
5944 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5945 |  |  |  | HR5944 (Lo-16bits)
5946 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5947 |  |  |  | HR5946 (Lo-16bits)
5948 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5949 |  |  |  | HR5948 (Lo-16bits)
5950 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5951 |  |  |  | HR5950 (Lo-16bits)
5952 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5953 |  |  |  | HR5952 (Lo-16bits)
5954 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5955 |  |  |  | HR5954 (Lo-16bits)
5956 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5957 |  |  |  | HR5956 (Lo-16bits)
5958 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5959 |  |  |  | HR5958 (Lo-16bits)
5960 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5961 |  |  |  | HR5960 (Lo-16bits)
5962 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5963 |  |  |  | HR5962 (Lo-16bits)
5964 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5965 |  |  |  | HR5964 (Lo-16bits)
5966 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5967 |  |  |  | HR5966 (Lo-16bits)
5968 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5969 |  |  |  | HR5968 (Lo-16bits)
5970 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5971 |  |  |  | HR5970 (Lo-16bits)
5972 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5973 |  |  |  | HR5972 (Lo-16bits)
5974 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5975 |  |  |  | HR5974 (Lo-16bits)
5976 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5977 |  |  |  | HR5976 (Lo-16bits)
5978 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5979 |  |  |  | HR5978 (Lo-16bits)
5980 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5981 |  |  |  | HR5980 (Lo-16bits)
5982 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5983 |  |  |  | HR5982 (Lo-16bits)
5984 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5985 |  |  |  | HR5984 (Lo-16bits)
5986 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5987 |  |  |  | HR5986 (Lo-16bits)
5988 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5989 |  |  |  | HR5988 (Lo-16bits)
5990 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5991 |  |  |  | HR5990 (Lo-16bits)
5992 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5993 |  |  |  | HR5992 (Lo-16bits)
5994 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5995 |  |  |  | HR5994 (Lo-16bits)
5996 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5997 |  |  |  | HR5996 (Lo-16bits)
5998 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5999 |  |  |  | HR5998 (Lo-16bits)
6000 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6001 |  |  |  | HR6000 (Lo-16bits)
6002 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6003 |  |  |  | HR6002 (Lo-16bits)
6004 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6005 |  |  |  | HR6004 (Lo-16bits)
6006 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6007 |  |  |  | HR6006 (Lo-16bits)
6008 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6009 |  |  |  | HR6008 (Lo-16bits)
6010 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6011 |  |  |  | HR6010 (Lo-16bits)
6012 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6013 |  |  |  | HR6012 (Lo-16bits)
6014 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6015 |  |  |  | HR6014 (Lo-16bits)
6016 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6017 |  |  |  | HR6016 (Lo-16bits)
6018 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6019 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6020 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6021 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6022 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6023 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6024 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6025 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6026 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6027 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6028 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6029 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6030 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6031 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6032 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6033 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6034 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6035 |  |  |  | HR6034 (Lo-16bits)
6036 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6037 |  |  |  | HR6036 (Lo-16bits)
6038 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6039 |  |  |  | HR6038 (Lo-16bits)
6040 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6041 |  |  |  | HR6040 (Lo-16bits)
6042 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6043 |  |  |  | HR6042 (Lo-16bits)
6044 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6045 |  |  |  | HR6044 (Lo-16bits)
6046 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6047 |  |  |  | HR6046 (Lo-16bits)
6048 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6049 |  |  |  | HR6048 (Lo-16bits)
6050 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6051 |  |  |  | HR6050 (Lo-16bits)
6052 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6053 |  |  |  | HR6052 (Lo-16bits)
6054 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6055 |  |  |  | HR6054 (Lo-16bits)
6056 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6057 |  |  |  | HR6056 (Lo-16bits)
6058 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6059 |  |  |  | HR6058 (Lo-16bits)
6060 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6061 |  |  |  | HR6060 (Lo-16bits)
6062 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6063 |  |  |  | HR6062 (Lo-16bits)
6064 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6065 |  |  |  | HR6064 (Lo-16bits)
6066 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6067 |  |  |  | HR6066 (Lo-16bits)
6068 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6069 |  |  |  | HR6068 (Lo-16bits)
6070 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6071 |  |  |  | HR6070 (Lo-16bits)
6072 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6073 |  |  |  | HR6072 (Lo-16bits)
6074 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6075 |  |  |  | HR6074 (Lo-16bits)
6076 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6077 |  |  |  | HR6076 (Lo-16bits)
6078 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6079 |  |  |  | HR6078 (Lo-16bits)
6080 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6081 |  |  |  | HR6080 (Lo-16bits)
6082 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6083 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6084 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6085 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6086 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6087 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6088 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6089 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6090 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6091 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6092 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6093 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6094 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6095 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6096 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6097 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6098 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6099 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6100 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6101 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6102 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6103 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6104 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6105 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6106 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6107 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6108 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6109 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6110 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6111 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6112 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6113 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6114 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6115 |  |  |  | HR6114 (Lo-16bits)
6116 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6117 |  |  |  | HR6116 (Lo-16bits)
6118 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6119 |  |  |  | HR6118 (Lo-16bits)
6120 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6121 |  |  |  | HR6120 (Lo-16bits)
6122 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6123 |  |  |  | HR6122 (Lo-16bits)
6124 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6125 |  |  |  | HR6124 (Lo-16bits)
6126 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6127 |  |  |  | HR6126 (Lo-16bits)
6128 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6129 |  |  |  | HR6128 (Lo-16bits)
6130 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6131 |  |  |  | HR6130 (Lo-16bits)
6132 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6133 |  |  |  | HR6132 (Lo-16bits)
6134 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6135 |  |  |  | HR6134 (Lo-16bits)
6136 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6137 |  |  |  | HR6136 (Lo-16bits)
6138 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6139 |  |  |  | HR6138 (Lo-16bits)
6140 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6141 |  |  |  | HR6140 (Lo-16bits)
6142 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6143 |  |  |  | HR6142 (Lo-16bits)
6144 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6145 |  |  |  | HR6144 (Lo-16bits)
6146 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6147 |  |  |  | HR6146 (Lo-16bits)
6148 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6149 |  |  |  | HR6148 (Lo-16bits)
6150 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6151 |  |  |  | HR6150 (Lo-16bits)
6152 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6153 |  |  |  | HR6152 (Lo-16bits)
6154 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6155 |  |  |  | HR6154 (Lo-16bits)
6156 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6157 |  |  |  | HR6156 (Lo-16bits)
6158 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6159 |  |  |  | HR6158 (Lo-16bits)
6160 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6161 |  |  |  | HR6160 (Lo-16bits)
6162 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6163 |  |  |  | HR6162 (Lo-16bits)
6164 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6165 |  |  |  | HR6164 (Lo-16bits)
6166 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6167 |  |  |  | HR6166 (Lo-16bits)
6168 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6169 |  |  |  | HR6168 (Lo-16bits)
6170 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6171 |  |  |  | HR6170 (Lo-16bits)
6172 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6173 |  |  |  | HR6172 (Lo-16bits)
6174 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6175 |  |  |  | HR6174 (Lo-16bits)
6176 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6177 |  |  |  | HR6176 (Lo-16bits)
6178 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6179 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6180 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6181 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6182 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6183 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6184 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6185 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6186 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6187 |  |  |  | HR6186 (Lo-16bits)
6188 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6189 |  |  |  | HR6188 (Lo-16bits)
6190 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6191 |  |  |  | HR6190 (Lo-16bits)
6192 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6193 |  |  |  | HR6192 (Lo-16bits)
6194 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6195 |  |  |  | HR6194 (Lo-16bits)
6196 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6197 |  |  |  | HR6196 (Lo-16bits)
6198 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6199 |  |  |  | HR6198 (Lo-16bits)
6200 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6201 |  |  |  | HR6200 (Lo-16bits)
6202 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6203 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6204 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6205 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6206 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6207 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6208 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6209 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6210 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6211 |  |  |  | HR6210 (Lo-16bits)
6212 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6213 |  |  |  | HR6212 (Lo-16bits)
6214 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6215 |  |  |  | HR6214 (Lo-16bits)
6216 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6217 |  |  |  | HR6216 (Lo-16bits)
6218 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6219 |  |  |  | HR6218 (Lo-16bits)
6220 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6221 |  |  |  | HR6220 (Lo-16bits)
6222 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6223 |  |  |  | HR6222 (Lo-16bits)
6224 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6225 |  |  |  | HR6224 (Lo-16bits)
6226 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6227 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6228 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6229 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6230 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6231 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6232 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6233 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6234 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6235 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6236 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6237 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6238 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6239 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6240 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6241 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6242 | IEF1:I0Int> condition | R | 1 | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
6243 | IEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
6244 | CUB1:I2> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6245 | CUB1:I2> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6246 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6247 |  |  |  | HR6246 (Lo-16bits)
6248 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6249 |  |  |  | HR6248 (Lo-16bits)
6250 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6251 |  |  |  | HR6250 (Lo-16bits)
6252 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6253 |  |  |  | HR6252 (Lo-16bits)
6254 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6255 |  |  |  | HR6254 (Lo-16bits)
6256 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6257 |  |  |  | HR6256 (Lo-16bits)
6258 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6259 |  |  |  | HR6258 (Lo-16bits)
6260 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6261 |  |  |  | HR6260 (Lo-16bits)
6262 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6263 |  |  |  | HR6262 (Lo-16bits)
6264 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6265 |  |  |  | HR6264 (Lo-16bits)
6266 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6267 |  |  |  | HR6266 (Lo-16bits)
6268 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6269 |  |  |  | HR6268 (Lo-16bits)
6270 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6271 |  |  |  | HR6270 (Lo-16bits)
6272 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6273 |  |  |  | HR6272 (Lo-16bits)
6274 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6275 |  |  |  | HR6274 (Lo-16bits)
6276 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6277 |  |  |  | HR6276 (Lo-16bits)
6278 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6279 |  |  |  | HR6278 (Lo-16bits)
6280 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6281 |  |  |  | HR6280 (Lo-16bits)
6282 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6283 |  |  |  | HR6282 (Lo-16bits)
6284 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6285 |  |  |  | HR6284 (Lo-16bits)
6286 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6287 |  |  |  | HR6286 (Lo-16bits)
6288 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6289 |  |  |  | HR6288 (Lo-16bits)
6290 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6291 |  |  |  | HR6290 (Lo-16bits)
6292 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6293 |  |  |  | HR6292 (Lo-16bits)
6294 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6295 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6296 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6297 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6298 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6299 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6300 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6301 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6302 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6303 |  |  |  | HR6302 (Lo-16bits)
6304 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6305 |  |  |  | HR6304 (Lo-16bits)
6306 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6307 |  |  |  | HR6306 (Lo-16bits)
6308 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6309 |  |  |  | HR6308 (Lo-16bits)
6310 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6311 |  |  |  | HR6310 (Lo-16bits)
6312 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6313 |  |  |  | HR6312 (Lo-16bits)
6314 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6315 |  |  |  | HR6314 (Lo-16bits)
6316 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6317 |  |  |  | HR6316 (Lo-16bits)
6318 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6319 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6320 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6321 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6322 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6323 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6324 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6325 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6326 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6327 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6328 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6329 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6330 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6331 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6332 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6333 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6334 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6335 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6336 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6337 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6338 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6339 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6340 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6341 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6342 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6343 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6344 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6345 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6346 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6347 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6348 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6349 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6350 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6351 |  |  |  | HR6350 (Lo-16bits)
6352 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6353 |  |  |  | HR6352 (Lo-16bits)
6354 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6355 |  |  |  | HR6354 (Lo-16bits)
6356 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6357 |  |  |  | HR6356 (Lo-16bits)
6358 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6359 |  |  |  | HR6358 (Lo-16bits)
6360 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6361 |  |  |  | HR6360 (Lo-16bits)
6362 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6363 |  |  |  | HR6362 (Lo-16bits)
6364 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6365 |  |  |  | HR6364 (Lo-16bits)
6366 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6367 |  |  |  | HR6366 (Lo-16bits)
6368 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6369 |  |  |  | HR6368 (Lo-16bits)
6370 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6371 |  |  |  | HR6370 (Lo-16bits)
6372 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6373 |  |  |  | HR6372 (Lo-16bits)
6374 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6375 |  |  |  | HR6374 (Lo-16bits)
6376 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6377 |  |  |  | HR6376 (Lo-16bits)
6378 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6379 |  |  |  | HR6378 (Lo-16bits)
6380 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6381 |  |  |  | HR6380 (Lo-16bits)
6382 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6383 |  |  |  | HR6382 (Lo-16bits)
6384 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6385 |  |  |  | HR6384 (Lo-16bits)
6386 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6387 |  |  |  | HR6386 (Lo-16bits)
6388 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6389 |  |  |  | HR6388 (Lo-16bits)
6390 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6391 |  |  |  | HR6390 (Lo-16bits)
6392 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6393 |  |  |  | HR6392 (Lo-16bits)
6394 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6395 |  |  |  | HR6394 (Lo-16bits)
6396 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6397 |  |  |  | HR6396 (Lo-16bits)
6398 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6399 |  |  |  | HR6398 (Lo-16bits)
6400 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6401 |  |  |  | HR6400 (Lo-16bits)
6402 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6403 |  |  |  | HR6402 (Lo-16bits)
6404 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6405 |  |  |  | HR6404 (Lo-16bits)
6406 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6407 |  |  |  | HR6406 (Lo-16bits)
6408 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6409 |  |  |  | HR6408 (Lo-16bits)
6410 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6411 |  |  |  | HR6410 (Lo-16bits)
6412 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6413 |  |  |  | HR6412 (Lo-16bits)
6414 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6415 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6416 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6417 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6418 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6419 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6420 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6421 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6422 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6423 |  |  |  | HR6422 (Lo-16bits)
6424 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6425 |  |  |  | HR6424 (Lo-16bits)
6426 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6427 |  |  |  | HR6426 (Lo-16bits)
6428 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6429 |  |  |  | HR6428 (Lo-16bits)
6430 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6431 |  |  |  | HR6430 (Lo-16bits)
6432 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6433 |  |  |  | HR6432 (Lo-16bits)
6434 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6435 |  |  |  | HR6434 (Lo-16bits)
6436 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6437 |  |  |  | HR6436 (Lo-16bits)
6438 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6439 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6440 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6441 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6442 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6443 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6444 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6445 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6446 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6447 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6448 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6449 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6450 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6451 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6452 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6453 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6454 | CUB2:I2>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6455 | CUB2:I2>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6456 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6457 |  |  |  | HR6456 (Lo-16bits)
6458 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6459 |  |  |  | HR6458 (Lo-16bits)
6460 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6461 |  |  |  | HR6460 (Lo-16bits)
6462 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6463 |  |  |  | HR6462 (Lo-16bits)
6464 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6465 |  |  |  | HR6464 (Lo-16bits)
6466 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6467 |  |  |  | HR6466 (Lo-16bits)
6468 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6469 |  |  |  | HR6468 (Lo-16bits)
6470 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6471 |  |  |  | HR6470 (Lo-16bits)
6472 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6473 |  |  |  | HR6472 (Lo-16bits)
6474 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6475 |  |  |  | HR6474 (Lo-16bits)
6476 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6477 |  |  |  | HR6476 (Lo-16bits)
6478 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6479 |  |  |  | HR6478 (Lo-16bits)
6480 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6481 |  |  |  | HR6480 (Lo-16bits)
6482 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6483 |  |  |  | HR6482 (Lo-16bits)
6484 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6485 |  |  |  | HR6484 (Lo-16bits)
6486 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6487 |  |  |  | HR6486 (Lo-16bits)
6488 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6489 |  |  |  | HR6488 (Lo-16bits)
6490 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6491 |  |  |  | HR6490 (Lo-16bits)
6492 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6493 |  |  |  | HR6492 (Lo-16bits)
6494 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6495 |  |  |  | HR6494 (Lo-16bits)
6496 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6497 |  |  |  | HR6496 (Lo-16bits)
6498 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6499 |  |  |  | HR6498 (Lo-16bits)
6500 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6501 |  |  |  | HR6500 (Lo-16bits)
6502 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6503 |  |  |  | HR6502 (Lo-16bits)
6504 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6505 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6506 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6507 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6508 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6509 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6510 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6511 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6512 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6513 |  |  |  | HR6512 (Lo-16bits)
6514 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6515 |  |  |  | HR6514 (Lo-16bits)
6516 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6517 |  |  |  | HR6516 (Lo-16bits)
6518 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6519 |  |  |  | HR6518 (Lo-16bits)
6520 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6521 |  |  |  | HR6520 (Lo-16bits)
6522 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6523 |  |  |  | HR6522 (Lo-16bits)
6524 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6525 |  |  |  | HR6524 (Lo-16bits)
6526 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6527 |  |  |  | HR6526 (Lo-16bits)
6528 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6529 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6530 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6531 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6532 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6533 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6534 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6535 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6536 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6537 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6538 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6539 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6540 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6541 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6542 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6543 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6544 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6545 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6546 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6547 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6548 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6549 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6550 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6551 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6552 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6553 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6554 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6555 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6556 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6557 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6558 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6559 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6560 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6561 |  |  |  | HR6560 (Lo-16bits)
6562 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6563 |  |  |  | HR6562 (Lo-16bits)
6564 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6565 |  |  |  | HR6564 (Lo-16bits)
6566 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6567 |  |  |  | HR6566 (Lo-16bits)
6568 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6569 |  |  |  | HR6568 (Lo-16bits)
6570 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6571 |  |  |  | HR6570 (Lo-16bits)
6572 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6573 |  |  |  | HR6572 (Lo-16bits)
6574 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6575 |  |  |  | HR6574 (Lo-16bits)
6576 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6577 |  |  |  | HR6576 (Lo-16bits)
6578 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6579 |  |  |  | HR6578 (Lo-16bits)
6580 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6581 |  |  |  | HR6580 (Lo-16bits)
6582 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6583 |  |  |  | HR6582 (Lo-16bits)
6584 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6585 |  |  |  | HR6584 (Lo-16bits)
6586 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6587 |  |  |  | HR6586 (Lo-16bits)
6588 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6589 |  |  |  | HR6588 (Lo-16bits)
6590 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6591 |  |  |  | HR6590 (Lo-16bits)
6592 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6593 |  |  |  | HR6592 (Lo-16bits)
6594 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6595 |  |  |  | HR6594 (Lo-16bits)
6596 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6597 |  |  |  | HR6596 (Lo-16bits)
6598 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6599 |  |  |  | HR6598 (Lo-16bits)
6600 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6601 |  |  |  | HR6600 (Lo-16bits)
6602 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6603 |  |  |  | HR6602 (Lo-16bits)
6604 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6605 |  |  |  | HR6604 (Lo-16bits)
6606 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6607 |  |  |  | HR6606 (Lo-16bits)
6608 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6609 |  |  |  | HR6608 (Lo-16bits)
6610 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6611 |  |  |  | HR6610 (Lo-16bits)
6612 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6613 |  |  |  | HR6612 (Lo-16bits)
6614 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6615 |  |  |  | HR6614 (Lo-16bits)
6616 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6617 |  |  |  | HR6616 (Lo-16bits)
6618 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6619 |  |  |  | HR6618 (Lo-16bits)
6620 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6621 |  |  |  | HR6620 (Lo-16bits)
6622 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6623 |  |  |  | HR6622 (Lo-16bits)
6624 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6625 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6626 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6627 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6628 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6629 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6630 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6631 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6632 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6633 |  |  |  | HR6632 (Lo-16bits)
6634 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6635 |  |  |  | HR6634 (Lo-16bits)
6636 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6637 |  |  |  | HR6636 (Lo-16bits)
6638 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6639 |  |  |  | HR6638 (Lo-16bits)
6640 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6641 |  |  |  | HR6640 (Lo-16bits)
6642 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6643 |  |  |  | HR6642 (Lo-16bits)
6644 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6645 |  |  |  | HR6644 (Lo-16bits)
6646 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6647 |  |  |  | HR6646 (Lo-16bits)
6648 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6649 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6650 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6651 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6652 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6653 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6654 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6655 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6656 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6657 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6658 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6659 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6660 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6661 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6662 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6663 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6664 | CUB3:I2>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6665 | CUB3:I2>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6666 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6667 |  |  |  | HR6666 (Lo-16bits)
6668 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6669 |  |  |  | HR6668 (Lo-16bits)
6670 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6671 |  |  |  | HR6670 (Lo-16bits)
6672 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6673 |  |  |  | HR6672 (Lo-16bits)
6674 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6675 |  |  |  | HR6674 (Lo-16bits)
6676 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6677 |  |  |  | HR6676 (Lo-16bits)
6678 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6679 |  |  |  | HR6678 (Lo-16bits)
6680 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6681 |  |  |  | HR6680 (Lo-16bits)
6682 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6683 |  |  |  | HR6682 (Lo-16bits)
6684 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6685 |  |  |  | HR6684 (Lo-16bits)
6686 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6687 |  |  |  | HR6686 (Lo-16bits)
6688 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6689 |  |  |  | HR6688 (Lo-16bits)
6690 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6691 |  |  |  | HR6690 (Lo-16bits)
6692 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6693 |  |  |  | HR6692 (Lo-16bits)
6694 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6695 |  |  |  | HR6694 (Lo-16bits)
6696 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6697 |  |  |  | HR6696 (Lo-16bits)
6698 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6699 |  |  |  | HR6698 (Lo-16bits)
6700 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6701 |  |  |  | HR6700 (Lo-16bits)
6702 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6703 |  |  |  | HR6702 (Lo-16bits)
6704 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6705 |  |  |  | HR6704 (Lo-16bits)
6706 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6707 |  |  |  | HR6706 (Lo-16bits)
6708 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6709 |  |  |  | HR6708 (Lo-16bits)
6710 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6711 |  |  |  | HR6710 (Lo-16bits)
6712 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6713 |  |  |  | HR6712 (Lo-16bits)
6714 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6715 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6716 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6717 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6718 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6719 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6720 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6721 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6722 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6723 |  |  |  | HR6722 (Lo-16bits)
6724 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6725 |  |  |  | HR6724 (Lo-16bits)
6726 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6727 |  |  |  | HR6726 (Lo-16bits)
6728 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6729 |  |  |  | HR6728 (Lo-16bits)
6730 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6731 |  |  |  | HR6730 (Lo-16bits)
6732 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6733 |  |  |  | HR6732 (Lo-16bits)
6734 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6735 |  |  |  | HR6734 (Lo-16bits)
6736 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6737 |  |  |  | HR6736 (Lo-16bits)
6738 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6739 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6740 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6741 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6742 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6743 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6744 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6745 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6746 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6747 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6748 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6749 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6750 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6751 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6752 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6753 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6754 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6755 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6756 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6757 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6758 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6759 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6760 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6761 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6762 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6763 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6764 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6765 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6766 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6767 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6768 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6769 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6770 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6771 |  |  |  | HR6770 (Lo-16bits)
6772 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6773 |  |  |  | HR6772 (Lo-16bits)
6774 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6775 |  |  |  | HR6774 (Lo-16bits)
6776 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6777 |  |  |  | HR6776 (Lo-16bits)
6778 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6779 |  |  |  | HR6778 (Lo-16bits)
6780 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6781 |  |  |  | HR6780 (Lo-16bits)
6782 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6783 |  |  |  | HR6782 (Lo-16bits)
6784 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6785 |  |  |  | HR6784 (Lo-16bits)
6786 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6787 |  |  |  | HR6786 (Lo-16bits)
6788 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6789 |  |  |  | HR6788 (Lo-16bits)
6790 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6791 |  |  |  | HR6790 (Lo-16bits)
6792 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6793 |  |  |  | HR6792 (Lo-16bits)
6794 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6795 |  |  |  | HR6794 (Lo-16bits)
6796 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6797 |  |  |  | HR6796 (Lo-16bits)
6798 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6799 |  |  |  | HR6798 (Lo-16bits)
6800 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6801 |  |  |  | HR6800 (Lo-16bits)
6802 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6803 |  |  |  | HR6802 (Lo-16bits)
6804 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6805 |  |  |  | HR6804 (Lo-16bits)
6806 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6807 |  |  |  | HR6806 (Lo-16bits)
6808 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6809 |  |  |  | HR6808 (Lo-16bits)
6810 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6811 |  |  |  | HR6810 (Lo-16bits)
6812 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6813 |  |  |  | HR6812 (Lo-16bits)
6814 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6815 |  |  |  | HR6814 (Lo-16bits)
6816 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6817 |  |  |  | HR6816 (Lo-16bits)
6818 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6819 |  |  |  | HR6818 (Lo-16bits)
6820 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6821 |  |  |  | HR6820 (Lo-16bits)
6822 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6823 |  |  |  | HR6822 (Lo-16bits)
6824 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6825 |  |  |  | HR6824 (Lo-16bits)
6826 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6827 |  |  |  | HR6826 (Lo-16bits)
6828 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6829 |  |  |  | HR6828 (Lo-16bits)
6830 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6831 |  |  |  | HR6830 (Lo-16bits)
6832 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6833 |  |  |  | HR6832 (Lo-16bits)
6834 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6835 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6836 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6837 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6838 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6839 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6840 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6841 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6842 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6843 |  |  |  | HR6842 (Lo-16bits)
6844 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6845 |  |  |  | HR6844 (Lo-16bits)
6846 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6847 |  |  |  | HR6846 (Lo-16bits)
6848 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6849 |  |  |  | HR6848 (Lo-16bits)
6850 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6851 |  |  |  | HR6850 (Lo-16bits)
6852 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6853 |  |  |  | HR6852 (Lo-16bits)
6854 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6855 |  |  |  | HR6854 (Lo-16bits)
6856 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6857 |  |  |  | HR6856 (Lo-16bits)
6858 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6859 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6860 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6861 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6862 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6863 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6864 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6865 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6866 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6867 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6868 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6869 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6870 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6871 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6872 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6873 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6874 | CUB4:I2>>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6875 | CUB4:I2>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6876 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6877 |  |  |  | HR6876 (Lo-16bits)
6878 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6879 |  |  |  | HR6878 (Lo-16bits)
6880 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6881 |  |  |  | HR6880 (Lo-16bits)
6882 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6883 |  |  |  | HR6882 (Lo-16bits)
6884 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6885 |  |  |  | HR6884 (Lo-16bits)
6886 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6887 |  |  |  | HR6886 (Lo-16bits)
6888 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6889 |  |  |  | HR6888 (Lo-16bits)
6890 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6891 |  |  |  | HR6890 (Lo-16bits)
6892 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6893 |  |  |  | HR6892 (Lo-16bits)
6894 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6895 |  |  |  | HR6894 (Lo-16bits)
6896 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6897 |  |  |  | HR6896 (Lo-16bits)
6898 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6899 |  |  |  | HR6898 (Lo-16bits)
6900 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6901 |  |  |  | HR6900 (Lo-16bits)
6902 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6903 |  |  |  | HR6902 (Lo-16bits)
6904 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6905 |  |  |  | HR6904 (Lo-16bits)
6906 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6907 |  |  |  | HR6906 (Lo-16bits)
6908 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6909 |  |  |  | HR6908 (Lo-16bits)
6910 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6911 |  |  |  | HR6910 (Lo-16bits)
6912 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6913 |  |  |  | HR6912 (Lo-16bits)
6914 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6915 |  |  |  | HR6914 (Lo-16bits)
6916 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6917 |  |  |  | HR6916 (Lo-16bits)
6918 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6919 |  |  |  | HR6918 (Lo-16bits)
6920 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6921 |  |  |  | HR6920 (Lo-16bits)
6922 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6923 |  |  |  | HR6922 (Lo-16bits)
6924 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6925 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6926 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6927 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6928 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6929 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6930 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6931 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6932 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6933 |  |  |  | HR6932 (Lo-16bits)
6934 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6935 |  |  |  | HR6934 (Lo-16bits)
6936 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6937 |  |  |  | HR6936 (Lo-16bits)
6938 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6939 |  |  |  | HR6938 (Lo-16bits)
6940 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6941 |  |  |  | HR6940 (Lo-16bits)
6942 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6943 |  |  |  | HR6942 (Lo-16bits)
6944 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6945 |  |  |  | HR6944 (Lo-16bits)
6946 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6947 |  |  |  | HR6946 (Lo-16bits)
6948 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6949 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6950 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6951 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6952 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6953 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6954 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6955 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6956 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6957 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6958 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6959 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6960 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6961 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6962 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6963 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6964 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6965 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6966 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6967 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6968 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6969 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6970 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6971 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6972 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6973 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6974 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6975 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6976 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6977 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6978 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6979 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6980 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6981 |  |  |  | HR6980 (Lo-16bits)
6982 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6983 |  |  |  | HR6982 (Lo-16bits)
6984 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6985 |  |  |  | HR6984 (Lo-16bits)
6986 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6987 |  |  |  | HR6986 (Lo-16bits)
6988 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6989 |  |  |  | HR6988 (Lo-16bits)
6990 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6991 |  |  |  | HR6990 (Lo-16bits)
6992 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6993 |  |  |  | HR6992 (Lo-16bits)
6994 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6995 |  |  |  | HR6994 (Lo-16bits)
6996 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6997 |  |  |  | HR6996 (Lo-16bits)
6998 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6999 |  |  |  | HR6998 (Lo-16bits)
7000 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7001 |  |  |  | HR7000 (Lo-16bits)
7002 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7003 |  |  |  | HR7002 (Lo-16bits)
7004 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7005 |  |  |  | HR7004 (Lo-16bits)
7006 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7007 |  |  |  | HR7006 (Lo-16bits)
7008 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7009 |  |  |  | HR7008 (Lo-16bits)
7010 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7011 |  |  |  | HR7010 (Lo-16bits)
7012 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7013 |  |  |  | HR7012 (Lo-16bits)
7014 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7015 |  |  |  | HR7014 (Lo-16bits)
7016 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7017 |  |  |  | HR7016 (Lo-16bits)
7018 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7019 |  |  |  | HR7018 (Lo-16bits)
7020 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7021 |  |  |  | HR7020 (Lo-16bits)
7022 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7023 |  |  |  | HR7022 (Lo-16bits)
7024 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7025 |  |  |  | HR7024 (Lo-16bits)
7026 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7027 |  |  |  | HR7026 (Lo-16bits)
7028 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7029 |  |  |  | HR7028 (Lo-16bits)
7030 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7031 |  |  |  | HR7030 (Lo-16bits)
7032 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7033 |  |  |  | HR7032 (Lo-16bits)
7034 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7035 |  |  |  | HR7034 (Lo-16bits)
7036 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7037 |  |  |  | HR7036 (Lo-16bits)
7038 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7039 |  |  |  | HR7038 (Lo-16bits)
7040 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7041 |  |  |  | HR7040 (Lo-16bits)
7042 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7043 |  |  |  | HR7042 (Lo-16bits)
7044 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7045 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7046 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7047 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7048 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7049 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7050 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7051 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7052 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7053 |  |  |  | HR7052 (Lo-16bits)
7054 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7055 |  |  |  | HR7054 (Lo-16bits)
7056 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7057 |  |  |  | HR7056 (Lo-16bits)
7058 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7059 |  |  |  | HR7058 (Lo-16bits)
7060 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7061 |  |  |  | HR7060 (Lo-16bits)
7062 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7063 |  |  |  | HR7062 (Lo-16bits)
7064 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7065 |  |  |  | HR7064 (Lo-16bits)
7066 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7067 |  |  |  | HR7066 (Lo-16bits)
7068 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7069 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7070 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7071 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7072 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7073 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7074 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7075 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7076 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7077 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7078 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7079 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7080 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7081 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7082 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7083 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7084 | HOC1:Ih> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7085 | HOC1:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7086 |  |  |  | HR7085 (Lo-16bits)
7087 | HOC1:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7088 |  |  |  | HR7087 (Lo-16bits)
7089 | HOC1:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7090 |  |  |  | HR7089 (Lo-16bits)
7091 | HOC1:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7092 |  |  |  | HR7091 (Lo-16bits)
7093 | HOC1:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7094 |  |  |  | HR7093 (Lo-16bits)
7095 | HOC1:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7096 |  |  |  | HR7095 (Lo-16bits)
7097 | HOC1:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7098 |  |  |  | HR7097 (Lo-16bits)
7099 | HOC1:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7100 |  |  |  | HR7099 (Lo-16bits)
7101 | HOC1:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7102 |  |  |  | HR7101 (Lo-16bits)
7103 | HOC1:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7104 |  |  |  | HR7103 (Lo-16bits)
7105 | HOC2:Ih>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7106 | HOC2:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7107 |  |  |  | HR7106 (Lo-16bits)
7108 | HOC2:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7109 |  |  |  | HR7108 (Lo-16bits)
7110 | HOC2:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7111 |  |  |  | HR7110 (Lo-16bits)
7112 | HOC2:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7113 |  |  |  | HR7112 (Lo-16bits)
7114 | HOC2:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7115 |  |  |  | HR7114 (Lo-16bits)
7116 | HOC2:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7117 |  |  |  | HR7116 (Lo-16bits)
7118 | HOC2:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7119 |  |  |  | HR7118 (Lo-16bits)
7120 | HOC2:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7121 |  |  |  | HR7120 (Lo-16bits)
7122 | HOC2:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7123 |  |  |  | HR7122 (Lo-16bits)
7124 | HOC2:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7125 |  |  |  | HR7124 (Lo-16bits)
7126 | HOC3:Ih>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7127 | HOC3:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7128 |  |  |  | HR7127 (Lo-16bits)
7129 | HOC3:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7130 |  |  |  | HR7129 (Lo-16bits)
7131 | HOC3:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7132 |  |  |  | HR7131 (Lo-16bits)
7133 | HOC3:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7134 |  |  |  | HR7133 (Lo-16bits)
7135 | HOC3:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7136 |  |  |  | HR7135 (Lo-16bits)
7137 | HOC3:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7138 |  |  |  | HR7137 (Lo-16bits)
7139 | HOC3:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7140 |  |  |  | HR7139 (Lo-16bits)
7141 | HOC3:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7142 |  |  |  | HR7141 (Lo-16bits)
7143 | HOC3:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7144 |  |  |  | HR7143 (Lo-16bits)
7145 | HOC3:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7146 |  |  |  | HR7145 (Lo-16bits)
7147 | HOC4:Ih>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7148 | HOC4:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7149 |  |  |  | HR7148 (Lo-16bits)
7150 | HOC4:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7151 |  |  |  | HR7150 (Lo-16bits)
7152 | HOC4:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7153 |  |  |  | HR7152 (Lo-16bits)
7154 | HOC4:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7155 |  |  |  | HR7154 (Lo-16bits)
7156 | HOC4:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7157 |  |  |  | HR7156 (Lo-16bits)
7158 | HOC4:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7159 |  |  |  | HR7158 (Lo-16bits)
7160 | HOC4:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7161 |  |  |  | HR7160 (Lo-16bits)
7162 | HOC4:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7163 |  |  |  | HR7162 (Lo-16bits)
7164 | HOC4:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7165 |  |  |  | HR7164 (Lo-16bits)
7166 | HOC4:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7167 |  |  |  | HR7166 (Lo-16bits)
7168 | CLP1:CLP condition | R | 1 | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
7169 | CBF1:CBFP condition | R | 1 | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
7170 | MST1:Motor is now | R | 1 | 0=Stopped;1=Starting;2=Running;3=Stalled
7171 | TRF1:Transformer is now | R | 1 | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
7172 | DIF1:Idx> condition | R | 2 | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On (Hi-16bits)
7173 |  |  |  | HR7172 (Lo-16bits)
7174 | DIF1:REFHV> condition | R | 2 | 0b=HV REF Blocked;1b=HV REF Trip (Hi-16bits)
7175 |  |  |  | HR7174 (Lo-16bits)
7176 | DIF1:REFLV> condition | R | 2 | 0b=LV REF Blocked;1b=LV REF Trip (Hi-16bits)
7177 |  |  |  | HR7176 (Lo-16bits)
7178 | DIF1:L1 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7179 | DIF1:L2 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7180 | DIF1:L3 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7181 | REF1:I0d> condition | R | 1 | 0=Normal;1=Trip;2=Blocked
7182 | TOLT1:TT> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7183 | TOLT1:TT> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7184 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7185 | TOLT1:TT> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7186 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7187 | TOLT1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7188 | TOLT1:Temp C or F deg | RW | 1 | 0=C;1=F
7189 | TOLT1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7190 | TOLT1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7191 | TOLT1:TT> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7192 |  |  |  | HR7191 (Lo-16bits)
7193 | TOLF1:TF> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7194 | TOLF1:TF> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7195 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7196 | TOLF1:TF> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7197 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7198 | TOLF1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7199 | TOLF1:Temp C or F deg | RW | 1 | 0=C;1=F
7200 | TOLF1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7201 | TOLF1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7202 | TOLF1:Set or Estimate tau (t const) | RW | 1 | 0=Set;1=Estimate
7203 | TOLF1:TF> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7204 |  |  |  | HR7203 (Lo-16bits)
7205 | TOLM1:TM> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7206 | TOLM1:TM> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7207 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7208 | TOLM1:TM> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7209 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7210 | TOLM1:Motor status | R | 1 | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
7211 | TOLM1:Temp C or F deg | RW | 1 | 0=C;1=F
7212 | TOLM1:NPS Biasing in use | RW | 1 | 0=No NPS biasing;1=NPS Biasing in use
7213 | TOLM1:Time constants | RW | 1 | 0=Single;1=Multiple
7214 | TOLM1:Estimate Short TC and timings | RW | 1 | 0=Set manually;1=Estimate (on-line)
7215 | TOLM1:T const dyn. balancing | RW | 1 | 0=Fixed;1=Dynamic
7216 | TOLM1:Dev.Temp (tmax) | RW | 1 | 0=A;1=B;2=F;3=H;4=Manual set
7217 | TOLM1:Amb. T Selection | RW | 1 | 0=Manual set;1=RTD
7218 | TOLM1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7219 | TOLM1:TM> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7220 |  |  |  | HR7219 (Lo-16bits)
7221 | LCR1:ISt> condition | R | 1 | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
7222 | FSP1:N> condition | R | 1 | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
7223 | NUC1:I< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7224 | MJP1:Im> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7225 | OV1:U> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7226 | OV1:U> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7227 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7228 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7229 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7230 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7231 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7232 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7233 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7234 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7235 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7236 |  |  |  | HR7235 (Lo-16bits)
7237 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7238 |  |  |  | HR7237 (Lo-16bits)
7239 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7240 |  |  |  | HR7239 (Lo-16bits)
7241 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7242 |  |  |  | HR7241 (Lo-16bits)
7243 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7244 |  |  |  | HR7243 (Lo-16bits)
7245 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7246 |  |  |  | HR7245 (Lo-16bits)
7247 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7248 |  |  |  | HR7247 (Lo-16bits)
7249 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7250 |  |  |  | HR7249 (Lo-16bits)
7251 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7252 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7253 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7254 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7255 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7256 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7257 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7258 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7259 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7260 |  |  |  | HR7259 (Lo-16bits)
7261 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7262 |  |  |  | HR7261 (Lo-16bits)
7263 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7264 |  |  |  | HR7263 (Lo-16bits)
7265 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7266 |  |  |  | HR7265 (Lo-16bits)
7267 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7268 |  |  |  | HR7267 (Lo-16bits)
7269 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7270 |  |  |  | HR7269 (Lo-16bits)
7271 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7272 |  |  |  | HR7271 (Lo-16bits)
7273 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7274 |  |  |  | HR7273 (Lo-16bits)
7275 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7276 |  |  |  | HR7275 (Lo-16bits)
7277 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7278 |  |  |  | HR7277 (Lo-16bits)
7279 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7280 |  |  |  | HR7279 (Lo-16bits)
7281 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7282 |  |  |  | HR7281 (Lo-16bits)
7283 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7284 |  |  |  | HR7283 (Lo-16bits)
7285 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7286 |  |  |  | HR7285 (Lo-16bits)
7287 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7288 |  |  |  | HR7287 (Lo-16bits)
7289 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7290 |  |  |  | HR7289 (Lo-16bits)
7291 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7292 |  |  |  | HR7291 (Lo-16bits)
7293 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7294 |  |  |  | HR7293 (Lo-16bits)
7295 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7296 |  |  |  | HR7295 (Lo-16bits)
7297 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7298 |  |  |  | HR7297 (Lo-16bits)
7299 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7300 |  |  |  | HR7299 (Lo-16bits)
7301 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7302 |  |  |  | HR7301 (Lo-16bits)
7303 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7304 |  |  |  | HR7303 (Lo-16bits)
7305 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7306 |  |  |  | HR7305 (Lo-16bits)
7307 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7308 |  |  |  | HR7307 (Lo-16bits)
7309 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7310 |  |  |  | HR7309 (Lo-16bits)
7311 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7312 |  |  |  | HR7311 (Lo-16bits)
7313 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7314 |  |  |  | HR7313 (Lo-16bits)
7315 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7316 |  |  |  | HR7315 (Lo-16bits)
7317 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7318 |  |  |  | HR7317 (Lo-16bits)
7319 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7320 |  |  |  | HR7319 (Lo-16bits)
7321 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7322 |  |  |  | HR7321 (Lo-16bits)
7323 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7324 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7325 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7326 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7327 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7328 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7329 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7330 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7331 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7332 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7333 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7334 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7335 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7336 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7337 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7338 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7339 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7340 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7341 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7342 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7343 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7344 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7345 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7346 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7347 | OV2:U>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7348 | OV2:U>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7349 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7350 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7351 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7352 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7353 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7354 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7355 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7356 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7357 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7358 |  |  |  | HR7357 (Lo-16bits)
7359 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7360 |  |  |  | HR7359 (Lo-16bits)
7361 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7362 |  |  |  | HR7361 (Lo-16bits)
7363 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7364 |  |  |  | HR7363 (Lo-16bits)
7365 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7366 |  |  |  | HR7365 (Lo-16bits)
7367 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7368 |  |  |  | HR7367 (Lo-16bits)
7369 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7370 |  |  |  | HR7369 (Lo-16bits)
7371 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7372 |  |  |  | HR7371 (Lo-16bits)
7373 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7374 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7375 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7376 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7377 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7378 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7379 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7380 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7381 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7382 |  |  |  | HR7381 (Lo-16bits)
7383 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7384 |  |  |  | HR7383 (Lo-16bits)
7385 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7386 |  |  |  | HR7385 (Lo-16bits)
7387 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7388 |  |  |  | HR7387 (Lo-16bits)
7389 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7390 |  |  |  | HR7389 (Lo-16bits)
7391 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7392 |  |  |  | HR7391 (Lo-16bits)
7393 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7394 |  |  |  | HR7393 (Lo-16bits)
7395 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7396 |  |  |  | HR7395 (Lo-16bits)
7397 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7398 |  |  |  | HR7397 (Lo-16bits)
7399 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7400 |  |  |  | HR7399 (Lo-16bits)
7401 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7402 |  |  |  | HR7401 (Lo-16bits)
7403 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7404 |  |  |  | HR7403 (Lo-16bits)
7405 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7406 |  |  |  | HR7405 (Lo-16bits)
7407 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7408 |  |  |  | HR7407 (Lo-16bits)
7409 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7410 |  |  |  | HR7409 (Lo-16bits)
7411 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7412 |  |  |  | HR7411 (Lo-16bits)
7413 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7414 |  |  |  | HR7413 (Lo-16bits)
7415 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7416 |  |  |  | HR7415 (Lo-16bits)
7417 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7418 |  |  |  | HR7417 (Lo-16bits)
7419 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7420 |  |  |  | HR7419 (Lo-16bits)
7421 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7422 |  |  |  | HR7421 (Lo-16bits)
7423 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7424 |  |  |  | HR7423 (Lo-16bits)
7425 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7426 |  |  |  | HR7425 (Lo-16bits)
7427 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7428 |  |  |  | HR7427 (Lo-16bits)
7429 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7430 |  |  |  | HR7429 (Lo-16bits)
7431 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7432 |  |  |  | HR7431 (Lo-16bits)
7433 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7434 |  |  |  | HR7433 (Lo-16bits)
7435 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7436 |  |  |  | HR7435 (Lo-16bits)
7437 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7438 |  |  |  | HR7437 (Lo-16bits)
7439 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7440 |  |  |  | HR7439 (Lo-16bits)
7441 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7442 |  |  |  | HR7441 (Lo-16bits)
7443 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7444 |  |  |  | HR7443 (Lo-16bits)
7445 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7446 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7447 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7448 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7449 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7450 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7451 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7452 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7453 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7454 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7455 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7456 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7457 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7458 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7459 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7460 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7461 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7462 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7463 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7464 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7465 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7466 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7467 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7468 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7469 | OV3:U>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7470 | OV3:U>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7471 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7472 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7473 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7474 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7475 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7476 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7477 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7478 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7479 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7480 |  |  |  | HR7479 (Lo-16bits)
7481 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7482 |  |  |  | HR7481 (Lo-16bits)
7483 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7484 |  |  |  | HR7483 (Lo-16bits)
7485 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7486 |  |  |  | HR7485 (Lo-16bits)
7487 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7488 |  |  |  | HR7487 (Lo-16bits)
7489 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7490 |  |  |  | HR7489 (Lo-16bits)
7491 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7492 |  |  |  | HR7491 (Lo-16bits)
7493 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7494 |  |  |  | HR7493 (Lo-16bits)
7495 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7496 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7497 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7498 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7499 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7500 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7501 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7502 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7503 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7504 |  |  |  | HR7503 (Lo-16bits)
7505 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7506 |  |  |  | HR7505 (Lo-16bits)
7507 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7508 |  |  |  | HR7507 (Lo-16bits)
7509 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7510 |  |  |  | HR7509 (Lo-16bits)
7511 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7512 |  |  |  | HR7511 (Lo-16bits)
7513 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7514 |  |  |  | HR7513 (Lo-16bits)
7515 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7516 |  |  |  | HR7515 (Lo-16bits)
7517 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7518 |  |  |  | HR7517 (Lo-16bits)
7519 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7520 |  |  |  | HR7519 (Lo-16bits)
7521 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7522 |  |  |  | HR7521 (Lo-16bits)
7523 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7524 |  |  |  | HR7523 (Lo-16bits)
7525 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7526 |  |  |  | HR7525 (Lo-16bits)
7527 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7528 |  |  |  | HR7527 (Lo-16bits)
7529 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7530 |  |  |  | HR7529 (Lo-16bits)
7531 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7532 |  |  |  | HR7531 (Lo-16bits)
7533 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7534 |  |  |  | HR7533 (Lo-16bits)
7535 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7536 |  |  |  | HR7535 (Lo-16bits)
7537 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7538 |  |  |  | HR7537 (Lo-16bits)
7539 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7540 |  |  |  | HR7539 (Lo-16bits)
7541 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7542 |  |  |  | HR7541 (Lo-16bits)
7543 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7544 |  |  |  | HR7543 (Lo-16bits)
7545 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7546 |  |  |  | HR7545 (Lo-16bits)
7547 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7548 |  |  |  | HR7547 (Lo-16bits)
7549 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7550 |  |  |  | HR7549 (Lo-16bits)
7551 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7552 |  |  |  | HR7551 (Lo-16bits)
7553 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7554 |  |  |  | HR7553 (Lo-16bits)
7555 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7556 |  |  |  | HR7555 (Lo-16bits)
7557 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7558 |  |  |  | HR7557 (Lo-16bits)
7559 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7560 |  |  |  | HR7559 (Lo-16bits)
7561 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7562 |  |  |  | HR7561 (Lo-16bits)
7563 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7564 |  |  |  | HR7563 (Lo-16bits)
7565 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7566 |  |  |  | HR7565 (Lo-16bits)
7567 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7568 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7569 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7570 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7571 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7572 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7573 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7574 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7575 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7576 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7577 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7578 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7579 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7580 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7581 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7582 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7583 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7584 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7585 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7586 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7587 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7588 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7589 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7590 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7591 | OV4:U>>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7592 | OV4:U>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7593 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7594 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7595 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7596 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7597 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7598 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7599 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7600 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7601 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7602 |  |  |  | HR7601 (Lo-16bits)
7603 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7604 |  |  |  | HR7603 (Lo-16bits)
7605 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7606 |  |  |  | HR7605 (Lo-16bits)
7607 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7608 |  |  |  | HR7607 (Lo-16bits)
7609 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7610 |  |  |  | HR7609 (Lo-16bits)
7611 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7612 |  |  |  | HR7611 (Lo-16bits)
7613 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7614 |  |  |  | HR7613 (Lo-16bits)
7615 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7616 |  |  |  | HR7615 (Lo-16bits)
7617 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7618 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7619 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7620 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7621 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7622 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7623 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7624 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7625 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7626 |  |  |  | HR7625 (Lo-16bits)
7627 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7628 |  |  |  | HR7627 (Lo-16bits)
7629 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7630 |  |  |  | HR7629 (Lo-16bits)
7631 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7632 |  |  |  | HR7631 (Lo-16bits)
7633 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7634 |  |  |  | HR7633 (Lo-16bits)
7635 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7636 |  |  |  | HR7635 (Lo-16bits)
7637 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7638 |  |  |  | HR7637 (Lo-16bits)
7639 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7640 |  |  |  | HR7639 (Lo-16bits)
7641 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7642 |  |  |  | HR7641 (Lo-16bits)
7643 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7644 |  |  |  | HR7643 (Lo-16bits)
7645 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7646 |  |  |  | HR7645 (Lo-16bits)
7647 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7648 |  |  |  | HR7647 (Lo-16bits)
7649 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7650 |  |  |  | HR7649 (Lo-16bits)
7651 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7652 |  |  |  | HR7651 (Lo-16bits)
7653 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7654 |  |  |  | HR7653 (Lo-16bits)
7655 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7656 |  |  |  | HR7655 (Lo-16bits)
7657 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7658 |  |  |  | HR7657 (Lo-16bits)
7659 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7660 |  |  |  | HR7659 (Lo-16bits)
7661 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7662 |  |  |  | HR7661 (Lo-16bits)
7663 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7664 |  |  |  | HR7663 (Lo-16bits)
7665 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7666 |  |  |  | HR7665 (Lo-16bits)
7667 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7668 |  |  |  | HR7667 (Lo-16bits)
7669 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7670 |  |  |  | HR7669 (Lo-16bits)
7671 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7672 |  |  |  | HR7671 (Lo-16bits)
7673 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7674 |  |  |  | HR7673 (Lo-16bits)
7675 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7676 |  |  |  | HR7675 (Lo-16bits)
7677 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7678 |  |  |  | HR7677 (Lo-16bits)
7679 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7680 |  |  |  | HR7679 (Lo-16bits)
7681 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7682 |  |  |  | HR7681 (Lo-16bits)
7683 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7684 |  |  |  | HR7683 (Lo-16bits)
7685 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7686 |  |  |  | HR7685 (Lo-16bits)
7687 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7688 |  |  |  | HR7687 (Lo-16bits)
7689 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7690 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7691 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7692 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7693 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7694 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7695 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7696 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7697 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7698 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7699 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7700 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7701 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7702 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7703 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7704 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7705 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7706 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7707 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7708 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7709 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7710 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7711 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7712 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7713 | UV1:U< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7714 | UV1:U< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7715 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7716 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7717 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7718 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7719 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7720 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7721 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7722 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7723 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7724 |  |  |  | HR7723 (Lo-16bits)
7725 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7726 |  |  |  | HR7725 (Lo-16bits)
7727 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7728 |  |  |  | HR7727 (Lo-16bits)
7729 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7730 |  |  |  | HR7729 (Lo-16bits)
7731 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7732 |  |  |  | HR7731 (Lo-16bits)
7733 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7734 |  |  |  | HR7733 (Lo-16bits)
7735 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7736 |  |  |  | HR7735 (Lo-16bits)
7737 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7738 |  |  |  | HR7737 (Lo-16bits)
7739 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7740 |  |  |  | HR7739 (Lo-16bits)
7741 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7742 |  |  |  | HR7741 (Lo-16bits)
7743 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7744 |  |  |  | HR7743 (Lo-16bits)
7745 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7746 |  |  |  | HR7745 (Lo-16bits)
7747 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7748 |  |  |  | HR7747 (Lo-16bits)
7749 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7750 |  |  |  | HR7749 (Lo-16bits)
7751 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7752 |  |  |  | HR7751 (Lo-16bits)
7753 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7754 |  |  |  | HR7753 (Lo-16bits)
7755 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7756 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7757 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7758 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7759 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7760 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7761 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7762 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7763 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7764 |  |  |  | HR7763 (Lo-16bits)
7765 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7766 |  |  |  | HR7765 (Lo-16bits)
7767 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7768 |  |  |  | HR7767 (Lo-16bits)
7769 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7770 |  |  |  | HR7769 (Lo-16bits)
7771 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7772 |  |  |  | HR7771 (Lo-16bits)
7773 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7774 |  |  |  | HR7773 (Lo-16bits)
7775 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7776 |  |  |  | HR7775 (Lo-16bits)
7777 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7778 |  |  |  | HR7777 (Lo-16bits)
7779 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7780 |  |  |  | HR7779 (Lo-16bits)
7781 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7782 |  |  |  | HR7781 (Lo-16bits)
7783 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7784 |  |  |  | HR7783 (Lo-16bits)
7785 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7786 |  |  |  | HR7785 (Lo-16bits)
7787 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7788 |  |  |  | HR7787 (Lo-16bits)
7789 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7790 |  |  |  | HR7789 (Lo-16bits)
7791 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7792 |  |  |  | HR7791 (Lo-16bits)
7793 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7794 |  |  |  | HR7793 (Lo-16bits)
7795 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7796 |  |  |  | HR7795 (Lo-16bits)
7797 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7798 |  |  |  | HR7797 (Lo-16bits)
7799 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7800 |  |  |  | HR7799 (Lo-16bits)
7801 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7802 |  |  |  | HR7801 (Lo-16bits)
7803 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7804 |  |  |  | HR7803 (Lo-16bits)
7805 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7806 |  |  |  | HR7805 (Lo-16bits)
7807 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7808 |  |  |  | HR7807 (Lo-16bits)
7809 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7810 |  |  |  | HR7809 (Lo-16bits)
7811 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7812 |  |  |  | HR7811 (Lo-16bits)
7813 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7814 |  |  |  | HR7813 (Lo-16bits)
7815 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7816 |  |  |  | HR7815 (Lo-16bits)
7817 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7818 |  |  |  | HR7817 (Lo-16bits)
7819 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7820 |  |  |  | HR7819 (Lo-16bits)
7821 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7822 |  |  |  | HR7821 (Lo-16bits)
7823 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7824 |  |  |  | HR7823 (Lo-16bits)
7825 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7826 |  |  |  | HR7825 (Lo-16bits)
7827 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7828 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7829 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7830 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7831 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7832 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7833 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7834 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7835 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7836 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7837 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7838 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7839 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7840 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7841 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7842 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7843 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7844 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7845 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7846 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7847 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7848 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7849 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7850 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7851 | UV2:U<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7852 | UV2:U<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7853 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7854 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7855 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7856 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7857 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7858 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7859 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7860 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7861 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7862 |  |  |  | HR7861 (Lo-16bits)
7863 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7864 |  |  |  | HR7863 (Lo-16bits)
7865 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7866 |  |  |  | HR7865 (Lo-16bits)
7867 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7868 |  |  |  | HR7867 (Lo-16bits)
7869 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7870 |  |  |  | HR7869 (Lo-16bits)
7871 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7872 |  |  |  | HR7871 (Lo-16bits)
7873 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7874 |  |  |  | HR7873 (Lo-16bits)
7875 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7876 |  |  |  | HR7875 (Lo-16bits)
7877 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7878 |  |  |  | HR7877 (Lo-16bits)
7879 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7880 |  |  |  | HR7879 (Lo-16bits)
7881 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7882 |  |  |  | HR7881 (Lo-16bits)
7883 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7884 |  |  |  | HR7883 (Lo-16bits)
7885 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7886 |  |  |  | HR7885 (Lo-16bits)
7887 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7888 |  |  |  | HR7887 (Lo-16bits)
7889 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7890 |  |  |  | HR7889 (Lo-16bits)
7891 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7892 |  |  |  | HR7891 (Lo-16bits)
7893 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7894 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7895 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7896 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7897 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7898 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7899 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7900 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7901 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7902 |  |  |  | HR7901 (Lo-16bits)
7903 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7904 |  |  |  | HR7903 (Lo-16bits)
7905 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7906 |  |  |  | HR7905 (Lo-16bits)
7907 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7908 |  |  |  | HR7907 (Lo-16bits)
7909 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7910 |  |  |  | HR7909 (Lo-16bits)
7911 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7912 |  |  |  | HR7911 (Lo-16bits)
7913 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7914 |  |  |  | HR7913 (Lo-16bits)
7915 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7916 |  |  |  | HR7915 (Lo-16bits)
7917 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7918 |  |  |  | HR7917 (Lo-16bits)
7919 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7920 |  |  |  | HR7919 (Lo-16bits)
7921 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7922 |  |  |  | HR7921 (Lo-16bits)
7923 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7924 |  |  |  | HR7923 (Lo-16bits)
7925 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7926 |  |  |  | HR7925 (Lo-16bits)
7927 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7928 |  |  |  | HR7927 (Lo-16bits)
7929 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7930 |  |  |  | HR7929 (Lo-16bits)
7931 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7932 |  |  |  | HR7931 (Lo-16bits)
7933 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7934 |  |  |  | HR7933 (Lo-16bits)
7935 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7936 |  |  |  | HR7935 (Lo-16bits)
7937 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7938 |  |  |  | HR7937 (Lo-16bits)
7939 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7940 |  |  |  | HR7939 (Lo-16bits)
7941 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7942 |  |  |  | HR7941 (Lo-16bits)
7943 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7944 |  |  |  | HR7943 (Lo-16bits)
7945 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7946 |  |  |  | HR7945 (Lo-16bits)
7947 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7948 |  |  |  | HR7947 (Lo-16bits)
7949 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7950 |  |  |  | HR7949 (Lo-16bits)
7951 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7952 |  |  |  | HR7951 (Lo-16bits)
7953 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7954 |  |  |  | HR7953 (Lo-16bits)
7955 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7956 |  |  |  | HR7955 (Lo-16bits)
7957 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7958 |  |  |  | HR7957 (Lo-16bits)
7959 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7960 |  |  |  | HR7959 (Lo-16bits)
7961 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7962 |  |  |  | HR7961 (Lo-16bits)
7963 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7964 |  |  |  | HR7963 (Lo-16bits)
7965 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7966 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7967 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7968 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7969 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7970 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7971 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7972 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7973 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7974 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7975 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7976 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7977 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7978 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7979 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7980 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7981 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7982 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7983 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7984 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7985 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7986 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7987 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7988 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7989 | UV3:U<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7990 | UV3:U<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7991 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7992 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7993 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7994 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7995 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7996 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7997 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7998 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7999 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8000 |  |  |  | HR7999 (Lo-16bits)
8001 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8002 |  |  |  | HR8001 (Lo-16bits)
8003 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8004 |  |  |  | HR8003 (Lo-16bits)
8005 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8006 |  |  |  | HR8005 (Lo-16bits)
8007 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8008 |  |  |  | HR8007 (Lo-16bits)
8009 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8010 |  |  |  | HR8009 (Lo-16bits)
8011 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8012 |  |  |  | HR8011 (Lo-16bits)
8013 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8014 |  |  |  | HR8013 (Lo-16bits)
8015 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8016 |  |  |  | HR8015 (Lo-16bits)
8017 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8018 |  |  |  | HR8017 (Lo-16bits)
8019 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8020 |  |  |  | HR8019 (Lo-16bits)
8021 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8022 |  |  |  | HR8021 (Lo-16bits)
8023 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8024 |  |  |  | HR8023 (Lo-16bits)
8025 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8026 |  |  |  | HR8025 (Lo-16bits)
8027 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8028 |  |  |  | HR8027 (Lo-16bits)
8029 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8030 |  |  |  | HR8029 (Lo-16bits)
8031 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8032 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8033 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8034 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8035 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8036 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8037 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8038 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8039 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8040 |  |  |  | HR8039 (Lo-16bits)
8041 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8042 |  |  |  | HR8041 (Lo-16bits)
8043 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8044 |  |  |  | HR8043 (Lo-16bits)
8045 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8046 |  |  |  | HR8045 (Lo-16bits)
8047 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8048 |  |  |  | HR8047 (Lo-16bits)
8049 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8050 |  |  |  | HR8049 (Lo-16bits)
8051 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8052 |  |  |  | HR8051 (Lo-16bits)
8053 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8054 |  |  |  | HR8053 (Lo-16bits)
8055 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8056 |  |  |  | HR8055 (Lo-16bits)
8057 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8058 |  |  |  | HR8057 (Lo-16bits)
8059 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8060 |  |  |  | HR8059 (Lo-16bits)
8061 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8062 |  |  |  | HR8061 (Lo-16bits)
8063 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8064 |  |  |  | HR8063 (Lo-16bits)
8065 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8066 |  |  |  | HR8065 (Lo-16bits)
8067 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8068 |  |  |  | HR8067 (Lo-16bits)
8069 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8070 |  |  |  | HR8069 (Lo-16bits)
8071 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8072 |  |  |  | HR8071 (Lo-16bits)
8073 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8074 |  |  |  | HR8073 (Lo-16bits)
8075 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8076 |  |  |  | HR8075 (Lo-16bits)
8077 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8078 |  |  |  | HR8077 (Lo-16bits)
8079 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8080 |  |  |  | HR8079 (Lo-16bits)
8081 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8082 |  |  |  | HR8081 (Lo-16bits)
8083 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8084 |  |  |  | HR8083 (Lo-16bits)
8085 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8086 |  |  |  | HR8085 (Lo-16bits)
8087 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8088 |  |  |  | HR8087 (Lo-16bits)
8089 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8090 |  |  |  | HR8089 (Lo-16bits)
8091 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8092 |  |  |  | HR8091 (Lo-16bits)
8093 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8094 |  |  |  | HR8093 (Lo-16bits)
8095 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8096 |  |  |  | HR8095 (Lo-16bits)
8097 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8098 |  |  |  | HR8097 (Lo-16bits)
8099 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8100 |  |  |  | HR8099 (Lo-16bits)
8101 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8102 |  |  |  | HR8101 (Lo-16bits)
8103 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8104 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8105 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8106 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8107 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8108 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8109 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8110 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8111 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8112 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8113 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8114 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8115 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8116 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8117 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8118 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8119 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8120 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8121 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8122 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8123 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8124 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8125 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8126 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8127 | UV4:U<<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
8128 | UV4:U<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
8129 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8130 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8131 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8132 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8133 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8134 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8135 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8136 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8137 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8138 |  |  |  | HR8137 (Lo-16bits)
8139 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8140 |  |  |  | HR8139 (Lo-16bits)
8141 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8142 |  |  |  | HR8141 (Lo-16bits)
8143 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8144 |  |  |  | HR8143 (Lo-16bits)
8145 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8146 |  |  |  | HR8145 (Lo-16bits)
8147 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8148 |  |  |  | HR8147 (Lo-16bits)
8149 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8150 |  |  |  | HR8149 (Lo-16bits)
8151 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8152 |  |  |  | HR8151 (Lo-16bits)
8153 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8154 |  |  |  | HR8153 (Lo-16bits)
8155 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8156 |  |  |  | HR8155 (Lo-16bits)
8157 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8158 |  |  |  | HR8157 (Lo-16bits)
8159 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8160 |  |  |  | HR8159 (Lo-16bits)
8161 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8162 |  |  |  | HR8161 (Lo-16bits)
8163 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8164 |  |  |  | HR8163 (Lo-16bits)
8165 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8166 |  |  |  | HR8165 (Lo-16bits)
8167 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8168 |  |  |  | HR8167 (Lo-16bits)
8169 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8170 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8171 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8172 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8173 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8174 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8175 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8176 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8177 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8178 |  |  |  | HR8177 (Lo-16bits)
8179 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8180 |  |  |  | HR8179 (Lo-16bits)
8181 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8182 |  |  |  | HR8181 (Lo-16bits)
8183 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8184 |  |  |  | HR8183 (Lo-16bits)
8185 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8186 |  |  |  | HR8185 (Lo-16bits)
8187 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8188 |  |  |  | HR8187 (Lo-16bits)
8189 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8190 |  |  |  | HR8189 (Lo-16bits)
8191 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8192 |  |  |  | HR8191 (Lo-16bits)
8193 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8194 |  |  |  | HR8193 (Lo-16bits)
8195 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8196 |  |  |  | HR8195 (Lo-16bits)
8197 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8198 |  |  |  | HR8197 (Lo-16bits)
8199 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8200 |  |  |  | HR8199 (Lo-16bits)
8201 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8202 |  |  |  | HR8201 (Lo-16bits)
8203 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8204 |  |  |  | HR8203 (Lo-16bits)
8205 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8206 |  |  |  | HR8205 (Lo-16bits)
8207 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8208 |  |  |  | HR8207 (Lo-16bits)
8209 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8210 |  |  |  | HR8209 (Lo-16bits)
8211 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8212 |  |  |  | HR8211 (Lo-16bits)
8213 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8214 |  |  |  | HR8213 (Lo-16bits)
8215 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8216 |  |  |  | HR8215 (Lo-16bits)
8217 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8218 |  |  |  | HR8217 (Lo-16bits)
8219 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8220 |  |  |  | HR8219 (Lo-16bits)
8221 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8222 |  |  |  | HR8221 (Lo-16bits)
8223 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8224 |  |  |  | HR8223 (Lo-16bits)
8225 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8226 |  |  |  | HR8225 (Lo-16bits)
8227 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8228 |  |  |  | HR8227 (Lo-16bits)
8229 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8230 |  |  |  | HR8229 (Lo-16bits)
8231 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8232 |  |  |  | HR8231 (Lo-16bits)
8233 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8234 |  |  |  | HR8233 (Lo-16bits)
8235 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8236 |  |  |  | HR8235 (Lo-16bits)
8237 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8238 |  |  |  | HR8237 (Lo-16bits)
8239 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8240 |  |  |  | HR8239 (Lo-16bits)
8241 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8242 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8243 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8244 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8245 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8246 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8247 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8248 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8249 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8250 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8251 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8252 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8253 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8254 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8255 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8256 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8257 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8258 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8259 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8260 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8261 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8262 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8263 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8264 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8265 | NOV1:U0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8266 | NOV1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8267 | NOV2:U0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8268 | NOV2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8269 | NOV3:U0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8270 | NOV3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8271 | NOV4:U0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8272 | NOV4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8273 | VUB1:U1/2 >/< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8274 | VUB1:U1/2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8275 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8276 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8277 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8278 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8279 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8280 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8281 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8282 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8283 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8284 |  |  |  | HR8283 (Lo-16bits)
8285 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8286 |  |  |  | HR8285 (Lo-16bits)
8287 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8288 |  |  |  | HR8287 (Lo-16bits)
8289 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8290 |  |  |  | HR8289 (Lo-16bits)
8291 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8292 |  |  |  | HR8291 (Lo-16bits)
8293 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8294 |  |  |  | HR8293 (Lo-16bits)
8295 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8296 |  |  |  | HR8295 (Lo-16bits)
8297 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8298 |  |  |  | HR8297 (Lo-16bits)
8299 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8300 |  |  |  | HR8299 (Lo-16bits)
8301 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8302 |  |  |  | HR8301 (Lo-16bits)
8303 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8304 |  |  |  | HR8303 (Lo-16bits)
8305 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8306 |  |  |  | HR8305 (Lo-16bits)
8307 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8308 |  |  |  | HR8307 (Lo-16bits)
8309 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8310 |  |  |  | HR8309 (Lo-16bits)
8311 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8312 |  |  |  | HR8311 (Lo-16bits)
8313 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8314 |  |  |  | HR8313 (Lo-16bits)
8315 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8316 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8317 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8318 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8319 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8320 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8321 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8322 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8323 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8324 |  |  |  | HR8323 (Lo-16bits)
8325 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8326 |  |  |  | HR8325 (Lo-16bits)
8327 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8328 |  |  |  | HR8327 (Lo-16bits)
8329 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8330 |  |  |  | HR8329 (Lo-16bits)
8331 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8332 |  |  |  | HR8331 (Lo-16bits)
8333 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8334 |  |  |  | HR8333 (Lo-16bits)
8335 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8336 |  |  |  | HR8335 (Lo-16bits)
8337 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8338 |  |  |  | HR8337 (Lo-16bits)
8339 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8340 |  |  |  | HR8339 (Lo-16bits)
8341 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8342 |  |  |  | HR8341 (Lo-16bits)
8343 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8344 |  |  |  | HR8343 (Lo-16bits)
8345 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8346 |  |  |  | HR8345 (Lo-16bits)
8347 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8348 |  |  |  | HR8347 (Lo-16bits)
8349 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8350 |  |  |  | HR8349 (Lo-16bits)
8351 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8352 |  |  |  | HR8351 (Lo-16bits)
8353 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8354 |  |  |  | HR8353 (Lo-16bits)
8355 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8356 |  |  |  | HR8355 (Lo-16bits)
8357 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8358 |  |  |  | HR8357 (Lo-16bits)
8359 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8360 |  |  |  | HR8359 (Lo-16bits)
8361 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8362 |  |  |  | HR8361 (Lo-16bits)
8363 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8364 |  |  |  | HR8363 (Lo-16bits)
8365 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8366 |  |  |  | HR8365 (Lo-16bits)
8367 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8368 |  |  |  | HR8367 (Lo-16bits)
8369 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8370 |  |  |  | HR8369 (Lo-16bits)
8371 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8372 |  |  |  | HR8371 (Lo-16bits)
8373 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8374 |  |  |  | HR8373 (Lo-16bits)
8375 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8376 |  |  |  | HR8375 (Lo-16bits)
8377 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8378 |  |  |  | HR8377 (Lo-16bits)
8379 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8380 |  |  |  | HR8379 (Lo-16bits)
8381 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8382 |  |  |  | HR8381 (Lo-16bits)
8383 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8384 |  |  |  | HR8383 (Lo-16bits)
8385 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8386 |  |  |  | HR8385 (Lo-16bits)
8387 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8388 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8389 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8390 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8391 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8392 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8393 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8394 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8395 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8396 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8397 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8398 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8399 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8400 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8401 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8402 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8403 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8404 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8405 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8406 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8407 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8408 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8409 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8410 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8411 | VUB2:U1/2 >>/<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8412 | VUB2:U1/2 >>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8413 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8414 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8415 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8416 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8417 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8418 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8419 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8420 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8421 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8422 |  |  |  | HR8421 (Lo-16bits)
8423 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8424 |  |  |  | HR8423 (Lo-16bits)
8425 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8426 |  |  |  | HR8425 (Lo-16bits)
8427 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8428 |  |  |  | HR8427 (Lo-16bits)
8429 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8430 |  |  |  | HR8429 (Lo-16bits)
8431 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8432 |  |  |  | HR8431 (Lo-16bits)
8433 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8434 |  |  |  | HR8433 (Lo-16bits)
8435 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8436 |  |  |  | HR8435 (Lo-16bits)
8437 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8438 |  |  |  | HR8437 (Lo-16bits)
8439 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8440 |  |  |  | HR8439 (Lo-16bits)
8441 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8442 |  |  |  | HR8441 (Lo-16bits)
8443 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8444 |  |  |  | HR8443 (Lo-16bits)
8445 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8446 |  |  |  | HR8445 (Lo-16bits)
8447 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8448 |  |  |  | HR8447 (Lo-16bits)
8449 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8450 |  |  |  | HR8449 (Lo-16bits)
8451 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8452 |  |  |  | HR8451 (Lo-16bits)
8453 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8454 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8455 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8456 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8457 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8458 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8459 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8460 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8461 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8462 |  |  |  | HR8461 (Lo-16bits)
8463 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8464 |  |  |  | HR8463 (Lo-16bits)
8465 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8466 |  |  |  | HR8465 (Lo-16bits)
8467 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8468 |  |  |  | HR8467 (Lo-16bits)
8469 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8470 |  |  |  | HR8469 (Lo-16bits)
8471 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8472 |  |  |  | HR8471 (Lo-16bits)
8473 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8474 |  |  |  | HR8473 (Lo-16bits)
8475 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8476 |  |  |  | HR8475 (Lo-16bits)
8477 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8478 |  |  |  | HR8477 (Lo-16bits)
8479 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8480 |  |  |  | HR8479 (Lo-16bits)
8481 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8482 |  |  |  | HR8481 (Lo-16bits)
8483 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8484 |  |  |  | HR8483 (Lo-16bits)
8485 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8486 |  |  |  | HR8485 (Lo-16bits)
8487 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8488 |  |  |  | HR8487 (Lo-16bits)
8489 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8490 |  |  |  | HR8489 (Lo-16bits)
8491 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8492 |  |  |  | HR8491 (Lo-16bits)
8493 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8494 |  |  |  | HR8493 (Lo-16bits)
8495 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8496 |  |  |  | HR8495 (Lo-16bits)
8497 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8498 |  |  |  | HR8497 (Lo-16bits)
8499 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8500 |  |  |  | HR8499 (Lo-16bits)
8501 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8502 |  |  |  | HR8501 (Lo-16bits)
8503 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8504 |  |  |  | HR8503 (Lo-16bits)
8505 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8506 |  |  |  | HR8505 (Lo-16bits)
8507 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8508 |  |  |  | HR8507 (Lo-16bits)
8509 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8510 |  |  |  | HR8509 (Lo-16bits)
8511 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8512 |  |  |  | HR8511 (Lo-16bits)
8513 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8514 |  |  |  | HR8513 (Lo-16bits)
8515 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8516 |  |  |  | HR8515 (Lo-16bits)
8517 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8518 |  |  |  | HR8517 (Lo-16bits)
8519 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8520 |  |  |  | HR8519 (Lo-16bits)
8521 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8522 |  |  |  | HR8521 (Lo-16bits)
8523 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8524 |  |  |  | HR8523 (Lo-16bits)
8525 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8526 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8527 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8528 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8529 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8530 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8531 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8532 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8533 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8534 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8535 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8536 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8537 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8538 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8539 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8540 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8541 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8542 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8543 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8544 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8545 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8546 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8547 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8548 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8549 | VUB3:U1/2 >>>/<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8550 | VUB3:U1/2 >>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8551 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8552 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8553 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8554 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8555 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8556 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8557 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8558 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8559 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8560 |  |  |  | HR8559 (Lo-16bits)
8561 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8562 |  |  |  | HR8561 (Lo-16bits)
8563 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8564 |  |  |  | HR8563 (Lo-16bits)
8565 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8566 |  |  |  | HR8565 (Lo-16bits)
8567 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8568 |  |  |  | HR8567 (Lo-16bits)
8569 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8570 |  |  |  | HR8569 (Lo-16bits)
8571 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8572 |  |  |  | HR8571 (Lo-16bits)
8573 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8574 |  |  |  | HR8573 (Lo-16bits)
8575 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8576 |  |  |  | HR8575 (Lo-16bits)
8577 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8578 |  |  |  | HR8577 (Lo-16bits)
8579 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8580 |  |  |  | HR8579 (Lo-16bits)
8581 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8582 |  |  |  | HR8581 (Lo-16bits)
8583 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8584 |  |  |  | HR8583 (Lo-16bits)
8585 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8586 |  |  |  | HR8585 (Lo-16bits)
8587 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8588 |  |  |  | HR8587 (Lo-16bits)
8589 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8590 |  |  |  | HR8589 (Lo-16bits)
8591 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8592 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8593 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8594 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8595 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8596 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8597 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8598 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8599 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8600 |  |  |  | HR8599 (Lo-16bits)
8601 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8602 |  |  |  | HR8601 (Lo-16bits)
8603 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8604 |  |  |  | HR8603 (Lo-16bits)
8605 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8606 |  |  |  | HR8605 (Lo-16bits)
8607 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8608 |  |  |  | HR8607 (Lo-16bits)
8609 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8610 |  |  |  | HR8609 (Lo-16bits)
8611 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8612 |  |  |  | HR8611 (Lo-16bits)
8613 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8614 |  |  |  | HR8613 (Lo-16bits)
8615 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8616 |  |  |  | HR8615 (Lo-16bits)
8617 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8618 |  |  |  | HR8617 (Lo-16bits)
8619 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8620 |  |  |  | HR8619 (Lo-16bits)
8621 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8622 |  |  |  | HR8621 (Lo-16bits)
8623 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8624 |  |  |  | HR8623 (Lo-16bits)
8625 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8626 |  |  |  | HR8625 (Lo-16bits)
8627 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8628 |  |  |  | HR8627 (Lo-16bits)
8629 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8630 |  |  |  | HR8629 (Lo-16bits)
8631 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8632 |  |  |  | HR8631 (Lo-16bits)
8633 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8634 |  |  |  | HR8633 (Lo-16bits)
8635 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8636 |  |  |  | HR8635 (Lo-16bits)
8637 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8638 |  |  |  | HR8637 (Lo-16bits)
8639 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8640 |  |  |  | HR8639 (Lo-16bits)
8641 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8642 |  |  |  | HR8641 (Lo-16bits)
8643 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8644 |  |  |  | HR8643 (Lo-16bits)
8645 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8646 |  |  |  | HR8645 (Lo-16bits)
8647 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8648 |  |  |  | HR8647 (Lo-16bits)
8649 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8650 |  |  |  | HR8649 (Lo-16bits)
8651 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8652 |  |  |  | HR8651 (Lo-16bits)
8653 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8654 |  |  |  | HR8653 (Lo-16bits)
8655 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8656 |  |  |  | HR8655 (Lo-16bits)
8657 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8658 |  |  |  | HR8657 (Lo-16bits)
8659 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8660 |  |  |  | HR8659 (Lo-16bits)
8661 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8662 |  |  |  | HR8661 (Lo-16bits)
8663 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8664 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8665 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8666 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8667 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8668 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8669 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8670 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8671 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8672 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8673 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8674 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8675 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8676 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8677 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8678 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8679 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8680 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8681 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8682 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8683 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8684 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8685 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8686 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8687 | VUB4:U1/2 >>>>/<<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8688 | VUB4:U1/2 >>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8689 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8690 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8691 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8692 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8693 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8694 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8695 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8696 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8697 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8698 |  |  |  | HR8697 (Lo-16bits)
8699 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8700 |  |  |  | HR8699 (Lo-16bits)
8701 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8702 |  |  |  | HR8701 (Lo-16bits)
8703 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8704 |  |  |  | HR8703 (Lo-16bits)
8705 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8706 |  |  |  | HR8705 (Lo-16bits)
8707 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8708 |  |  |  | HR8707 (Lo-16bits)
8709 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8710 |  |  |  | HR8709 (Lo-16bits)
8711 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8712 |  |  |  | HR8711 (Lo-16bits)
8713 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8714 |  |  |  | HR8713 (Lo-16bits)
8715 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8716 |  |  |  | HR8715 (Lo-16bits)
8717 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8718 |  |  |  | HR8717 (Lo-16bits)
8719 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8720 |  |  |  | HR8719 (Lo-16bits)
8721 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8722 |  |  |  | HR8721 (Lo-16bits)
8723 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8724 |  |  |  | HR8723 (Lo-16bits)
8725 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8726 |  |  |  | HR8725 (Lo-16bits)
8727 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8728 |  |  |  | HR8727 (Lo-16bits)
8729 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8730 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8731 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8732 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8733 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8734 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8735 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8736 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8737 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8738 |  |  |  | HR8737 (Lo-16bits)
8739 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8740 |  |  |  | HR8739 (Lo-16bits)
8741 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8742 |  |  |  | HR8741 (Lo-16bits)
8743 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8744 |  |  |  | HR8743 (Lo-16bits)
8745 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8746 |  |  |  | HR8745 (Lo-16bits)
8747 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8748 |  |  |  | HR8747 (Lo-16bits)
8749 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8750 |  |  |  | HR8749 (Lo-16bits)
8751 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8752 |  |  |  | HR8751 (Lo-16bits)
8753 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8754 |  |  |  | HR8753 (Lo-16bits)
8755 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8756 |  |  |  | HR8755 (Lo-16bits)
8757 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8758 |  |  |  | HR8757 (Lo-16bits)
8759 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8760 |  |  |  | HR8759 (Lo-16bits)
8761 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8762 |  |  |  | HR8761 (Lo-16bits)
8763 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8764 |  |  |  | HR8763 (Lo-16bits)
8765 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8766 |  |  |  | HR8765 (Lo-16bits)
8767 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8768 |  |  |  | HR8767 (Lo-16bits)
8769 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8770 |  |  |  | HR8769 (Lo-16bits)
8771 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8772 |  |  |  | HR8771 (Lo-16bits)
8773 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8774 |  |  |  | HR8773 (Lo-16bits)
8775 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8776 |  |  |  | HR8775 (Lo-16bits)
8777 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8778 |  |  |  | HR8777 (Lo-16bits)
8779 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8780 |  |  |  | HR8779 (Lo-16bits)
8781 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8782 |  |  |  | HR8781 (Lo-16bits)
8783 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8784 |  |  |  | HR8783 (Lo-16bits)
8785 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8786 |  |  |  | HR8785 (Lo-16bits)
8787 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8788 |  |  |  | HR8787 (Lo-16bits)
8789 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8790 |  |  |  | HR8789 (Lo-16bits)
8791 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8792 |  |  |  | HR8791 (Lo-16bits)
8793 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8794 |  |  |  | HR8793 (Lo-16bits)
8795 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8796 |  |  |  | HR8795 (Lo-16bits)
8797 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8798 |  |  |  | HR8797 (Lo-16bits)
8799 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8800 |  |  |  | HR8799 (Lo-16bits)
8801 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8802 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8803 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8804 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8805 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8806 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8807 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8808 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8809 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8810 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8811 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8812 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8813 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8814 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8815 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8816 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8817 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8818 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8819 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8820 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8821 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8822 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8823 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8824 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8825 | PGS1:PS1 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8826 | PGS1:PS2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8827 | PGS1:PS3 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8828 | PGS1:PS4 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8829 | PGS1:PS5 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8830 | PGS1:PS6 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8831 | PGS1:PS7 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8832 | PGS1:PS8 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8833 | PGS1:PS9 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8834 | PGS1:PS10 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8835 | FRQC1:f> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8836 | FRQC1:f>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8837 | FRQC1:f>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8838 | FRQC1:f>>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8839 | FRQC1:f< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8840 | FRQC1:f<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8841 | FRQC1:f<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8842 | FRQC1:f<<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8843 | FRQV1:f</> [81O/81U] mode | R(W) | 1 | 0=Disabled;1=Activated
8844 | FRQV1:f> Enable | R(W) | 1 | 0=No;1=Yes
8845 | FRQV1:f> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8846 | FRQV1:f>> Enable | R(W) | 1 | 0=No;1=Yes
8847 | FRQV1:f>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8848 | FRQV1:f>>> Enable | R(W) | 1 | 0=No;1=Yes
8849 | FRQV1:f>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8850 | FRQV1:f>>>> Enable | R(W) | 1 | 0=No;1=Yes
8851 | FRQV1:f>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8852 | FRQV1:f< Enable | R(W) | 1 | 0=No;1=Yes
8853 | FRQV1:f< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8854 | FRQV1:f<< Enable | R(W) | 1 | 0=No;1=Yes
8855 | FRQV1:f<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8856 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8857 | FRQV1:f<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8858 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8859 | FRQV1:f<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8860 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8861 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8862 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8863 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8864 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8865 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8866 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8867 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8868 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8869 |  |  |  | HR8868 (Lo-16bits)
8870 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8871 |  |  |  | HR8870 (Lo-16bits)
8872 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8873 |  |  |  | HR8872 (Lo-16bits)
8874 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8875 |  |  |  | HR8874 (Lo-16bits)
8876 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8877 |  |  |  | HR8876 (Lo-16bits)
8878 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8879 |  |  |  | HR8878 (Lo-16bits)
8880 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8881 |  |  |  | HR8880 (Lo-16bits)
8882 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8883 |  |  |  | HR8882 (Lo-16bits)
8884 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8885 |  |  |  | HR8884 (Lo-16bits)
8886 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8887 |  |  |  | HR8886 (Lo-16bits)
8888 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8889 |  |  |  | HR8888 (Lo-16bits)
8890 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8891 |  |  |  | HR8890 (Lo-16bits)
8892 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8893 |  |  |  | HR8892 (Lo-16bits)
8894 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8895 |  |  |  | HR8894 (Lo-16bits)
8896 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8897 |  |  |  | HR8896 (Lo-16bits)
8898 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8899 |  |  |  | HR8898 (Lo-16bits)
8900 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8901 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8902 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8903 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8904 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8905 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8906 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8907 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8908 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8909 |  |  |  | HR8908 (Lo-16bits)
8910 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8911 |  |  |  | HR8910 (Lo-16bits)
8912 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8913 |  |  |  | HR8912 (Lo-16bits)
8914 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8915 |  |  |  | HR8914 (Lo-16bits)
8916 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8917 |  |  |  | HR8916 (Lo-16bits)
8918 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8919 |  |  |  | HR8918 (Lo-16bits)
8920 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8921 |  |  |  | HR8920 (Lo-16bits)
8922 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8923 |  |  |  | HR8922 (Lo-16bits)
8924 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8925 |  |  |  | HR8924 (Lo-16bits)
8926 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8927 |  |  |  | HR8926 (Lo-16bits)
8928 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8929 |  |  |  | HR8928 (Lo-16bits)
8930 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8931 |  |  |  | HR8930 (Lo-16bits)
8932 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8933 |  |  |  | HR8932 (Lo-16bits)
8934 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8935 |  |  |  | HR8934 (Lo-16bits)
8936 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8937 |  |  |  | HR8936 (Lo-16bits)
8938 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8939 |  |  |  | HR8938 (Lo-16bits)
8940 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8941 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8942 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8943 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8944 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8945 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8946 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8947 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8948 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8949 |  |  |  | HR8948 (Lo-16bits)
8950 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8951 |  |  |  | HR8950 (Lo-16bits)
8952 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8953 |  |  |  | HR8952 (Lo-16bits)
8954 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8955 |  |  |  | HR8954 (Lo-16bits)
8956 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8957 |  |  |  | HR8956 (Lo-16bits)
8958 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8959 |  |  |  | HR8958 (Lo-16bits)
8960 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8961 |  |  |  | HR8960 (Lo-16bits)
8962 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8963 |  |  |  | HR8962 (Lo-16bits)
8964 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8965 |  |  |  | HR8964 (Lo-16bits)
8966 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8967 |  |  |  | HR8966 (Lo-16bits)
8968 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8969 |  |  |  | HR8968 (Lo-16bits)
8970 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8971 |  |  |  | HR8970 (Lo-16bits)
8972 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8973 |  |  |  | HR8972 (Lo-16bits)
8974 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8975 |  |  |  | HR8974 (Lo-16bits)
8976 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8977 |  |  |  | HR8976 (Lo-16bits)
8978 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8979 |  |  |  | HR8978 (Lo-16bits)
8980 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8981 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8982 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8983 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8984 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8985 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8986 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8987 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8988 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8989 |  |  |  | HR8988 (Lo-16bits)
8990 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8991 |  |  |  | HR8990 (Lo-16bits)
8992 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8993 |  |  |  | HR8992 (Lo-16bits)
8994 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8995 |  |  |  | HR8994 (Lo-16bits)
8996 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8997 |  |  |  | HR8996 (Lo-16bits)
8998 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8999 |  |  |  | HR8998 (Lo-16bits)
9000 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9001 |  |  |  | HR9000 (Lo-16bits)
9002 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9003 |  |  |  | HR9002 (Lo-16bits)
9004 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9005 |  |  |  | HR9004 (Lo-16bits)
9006 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9007 |  |  |  | HR9006 (Lo-16bits)
9008 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9009 |  |  |  | HR9008 (Lo-16bits)
9010 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9011 |  |  |  | HR9010 (Lo-16bits)
9012 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9013 |  |  |  | HR9012 (Lo-16bits)
9014 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9015 |  |  |  | HR9014 (Lo-16bits)
9016 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9017 |  |  |  | HR9016 (Lo-16bits)
9018 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9019 |  |  |  | HR9018 (Lo-16bits)
9020 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9021 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9022 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9023 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9024 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9025 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9026 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9027 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9028 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9029 |  |  |  | HR9028 (Lo-16bits)
9030 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9031 |  |  |  | HR9030 (Lo-16bits)
9032 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9033 |  |  |  | HR9032 (Lo-16bits)
9034 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9035 |  |  |  | HR9034 (Lo-16bits)
9036 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9037 |  |  |  | HR9036 (Lo-16bits)
9038 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9039 |  |  |  | HR9038 (Lo-16bits)
9040 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9041 |  |  |  | HR9040 (Lo-16bits)
9042 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9043 |  |  |  | HR9042 (Lo-16bits)
9044 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9045 |  |  |  | HR9044 (Lo-16bits)
9046 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9047 |  |  |  | HR9046 (Lo-16bits)
9048 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9049 |  |  |  | HR9048 (Lo-16bits)
9050 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9051 |  |  |  | HR9050 (Lo-16bits)
9052 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9053 |  |  |  | HR9052 (Lo-16bits)
9054 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9055 |  |  |  | HR9054 (Lo-16bits)
9056 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9057 |  |  |  | HR9056 (Lo-16bits)
9058 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9059 |  |  |  | HR9058 (Lo-16bits)
9060 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9061 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9062 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9063 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9064 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9065 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9066 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9067 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9068 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9069 |  |  |  | HR9068 (Lo-16bits)
9070 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9071 |  |  |  | HR9070 (Lo-16bits)
9072 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9073 |  |  |  | HR9072 (Lo-16bits)
9074 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9075 |  |  |  | HR9074 (Lo-16bits)
9076 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9077 |  |  |  | HR9076 (Lo-16bits)
9078 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9079 |  |  |  | HR9078 (Lo-16bits)
9080 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9081 |  |  |  | HR9080 (Lo-16bits)
9082 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9083 |  |  |  | HR9082 (Lo-16bits)
9084 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9085 |  |  |  | HR9084 (Lo-16bits)
9086 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9087 |  |  |  | HR9086 (Lo-16bits)
9088 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9089 |  |  |  | HR9088 (Lo-16bits)
9090 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9091 |  |  |  | HR9090 (Lo-16bits)
9092 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9093 |  |  |  | HR9092 (Lo-16bits)
9094 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9095 |  |  |  | HR9094 (Lo-16bits)
9096 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9097 |  |  |  | HR9096 (Lo-16bits)
9098 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9099 |  |  |  | HR9098 (Lo-16bits)
9100 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9101 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9102 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9103 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9104 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9105 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9106 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9107 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9108 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9109 |  |  |  | HR9108 (Lo-16bits)
9110 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9111 |  |  |  | HR9110 (Lo-16bits)
9112 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9113 |  |  |  | HR9112 (Lo-16bits)
9114 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9115 |  |  |  | HR9114 (Lo-16bits)
9116 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9117 |  |  |  | HR9116 (Lo-16bits)
9118 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9119 |  |  |  | HR9118 (Lo-16bits)
9120 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9121 |  |  |  | HR9120 (Lo-16bits)
9122 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9123 |  |  |  | HR9122 (Lo-16bits)
9124 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9125 |  |  |  | HR9124 (Lo-16bits)
9126 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9127 |  |  |  | HR9126 (Lo-16bits)
9128 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9129 |  |  |  | HR9128 (Lo-16bits)
9130 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9131 |  |  |  | HR9130 (Lo-16bits)
9132 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9133 |  |  |  | HR9132 (Lo-16bits)
9134 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9135 |  |  |  | HR9134 (Lo-16bits)
9136 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9137 |  |  |  | HR9136 (Lo-16bits)
9138 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9139 |  |  |  | HR9138 (Lo-16bits)
9140 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9141 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9142 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9143 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9144 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9145 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9146 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9147 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9148 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9149 |  |  |  | HR9148 (Lo-16bits)
9150 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9151 |  |  |  | HR9150 (Lo-16bits)
9152 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9153 |  |  |  | HR9152 (Lo-16bits)
9154 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9155 |  |  |  | HR9154 (Lo-16bits)
9156 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9157 |  |  |  | HR9156 (Lo-16bits)
9158 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9159 |  |  |  | HR9158 (Lo-16bits)
9160 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9161 |  |  |  | HR9160 (Lo-16bits)
9162 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9163 |  |  |  | HR9162 (Lo-16bits)
9164 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9165 |  |  |  | HR9164 (Lo-16bits)
9166 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9167 |  |  |  | HR9166 (Lo-16bits)
9168 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9169 |  |  |  | HR9168 (Lo-16bits)
9170 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9171 |  |  |  | HR9170 (Lo-16bits)
9172 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9173 |  |  |  | HR9172 (Lo-16bits)
9174 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9175 |  |  |  | HR9174 (Lo-16bits)
9176 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9177 |  |  |  | HR9176 (Lo-16bits)
9178 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9179 |  |  |  | HR9178 (Lo-16bits)
9180 | DFT1:df/dt >/< (1) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9181 | DFT1:df/dt >/< (2) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9182 | DFT1:df/dt >/< (3) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9183 | DFT1:df/dt >/< (4) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9184 | DFT1:df/dt >/< (5) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9185 | DFT1:df/dt >/< (6) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9186 | DFT1:df/dt >/< (7) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9187 | DFT1:df/dt >/< (8) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9188 | RHC1:Counter is now | R | 1 | 0=Idle;1=Counting
9189 | RHC1:Running hours | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9190 |  |  |  | HR9189 (Lo-16bits)
9191 | RHC1:Start count | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9192 |  |  |  | HR9191 (Lo-16bits)
9193 | GST1:Generator is now | R | 1 | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
9194 | PWR1:PQS>/< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9195 | PWR2:PQS>>/<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9196 | PWR3:PQS>>>/<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9197 | PWR4:PQS>>>>/<<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9198 | OPW1:P> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9199 | UPW1:P< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9200 | RPW1:Prev> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9201 | SEF1:U03rd< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9202 | SEF1:U03rd< Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
9203 | UEX1:Q< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9204 | UIM1:Z< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9205 | UIM2:Z<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9206 | VOC1:Iv> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9207 | VOC1:Voltage measurement | R | 1 | 0=Invalid U1 not avail.;1=Ok
9208 | VHZ1:V/Hz(1) > condition | R | 1 | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
9209 | VHZ1:V/Hz(2) > condition | R | 1 | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
9210 | UPF1:PF< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
9211 | RTDIN:S1 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9212 |  |  |  | HR9211 (Lo-16bits)
9213 | RTDIN:S1 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9214 |  |  |  | HR9213 (Lo-16bits)
9215 | RTDIN:S1 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9216 | RTDIN:S1 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9217 |  |  |  | HR9216 (Lo-16bits)
9218 | RTDIN:S2 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9219 |  |  |  | HR9218 (Lo-16bits)
9220 | RTDIN:S2 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9221 |  |  |  | HR9220 (Lo-16bits)
9222 | RTDIN:S2 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9223 | RTDIN:S2 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9224 |  |  |  | HR9223 (Lo-16bits)
9225 | RTDIN:S3 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9226 |  |  |  | HR9225 (Lo-16bits)
9227 | RTDIN:S3 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9228 |  |  |  | HR9227 (Lo-16bits)
9229 | RTDIN:S3 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9230 | RTDIN:S3 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9231 |  |  |  | HR9230 (Lo-16bits)
9232 | RTDIN:S4 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9233 |  |  |  | HR9232 (Lo-16bits)
9234 | RTDIN:S4 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9235 |  |  |  | HR9234 (Lo-16bits)
9236 | RTDIN:S4 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9237 | RTDIN:S4 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9238 |  |  |  | HR9237 (Lo-16bits)
9239 | RTDIN:S5 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9240 |  |  |  | HR9239 (Lo-16bits)
9241 | RTDIN:S5 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9242 |  |  |  | HR9241 (Lo-16bits)
9243 | RTDIN:S5 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9244 | RTDIN:S5 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9245 |  |  |  | HR9244 (Lo-16bits)
9246 | RTDIN:S6 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9247 |  |  |  | HR9246 (Lo-16bits)
9248 | RTDIN:S6 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9249 |  |  |  | HR9248 (Lo-16bits)
9250 | RTDIN:S6 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9251 | RTDIN:S6 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9252 |  |  |  | HR9251 (Lo-16bits)
9253 | RTDIN:S7 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9254 |  |  |  | HR9253 (Lo-16bits)
9255 | RTDIN:S7 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9256 |  |  |  | HR9255 (Lo-16bits)
9257 | RTDIN:S7 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9258 |  |  |  | HR9257 (Lo-16bits)
9259 | RTDIN:S7 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9260 | RTDIN:S7 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9261 |  |  |  | HR9260 (Lo-16bits)
9262 | RTDIN:S8 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9263 |  |  |  | HR9262 (Lo-16bits)
9264 | RTDIN:S8 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9265 |  |  |  | HR9264 (Lo-16bits)
9266 | RTDIN:S8 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9267 |  |  |  | HR9266 (Lo-16bits)
9268 | RTDIN:S8 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9269 | RTDIN:S8 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9270 |  |  |  | HR9269 (Lo-16bits)
9271 | RTDIN:S9 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9272 |  |  |  | HR9271 (Lo-16bits)
9273 | RTDIN:S9 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9274 |  |  |  | HR9273 (Lo-16bits)
9275 | RTDIN:S9 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9276 | RTDIN:S9 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9277 |  |  |  | HR9276 (Lo-16bits)
9278 | RTDIN:S10 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9279 |  |  |  | HR9278 (Lo-16bits)
9280 | RTDIN:S10 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9281 |  |  |  | HR9280 (Lo-16bits)
9282 | RTDIN:S10 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9283 | RTDIN:S10 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9284 |  |  |  | HR9283 (Lo-16bits)
9285 | RTDIN:S11 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9286 |  |  |  | HR9285 (Lo-16bits)
9287 | RTDIN:S11 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9288 |  |  |  | HR9287 (Lo-16bits)
9289 | RTDIN:S11 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9290 | RTDIN:S11 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9291 |  |  |  | HR9290 (Lo-16bits)
9292 | RTDIN:S12 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9293 |  |  |  | HR9292 (Lo-16bits)
9294 | RTDIN:S12 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9295 |  |  |  | HR9294 (Lo-16bits)
9296 | RTDIN:S12 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9297 | RTDIN:S12 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9298 |  |  |  | HR9297 (Lo-16bits)
9299 | RTDIN:S13 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9300 |  |  |  | HR9299 (Lo-16bits)
9301 | RTDIN:S13 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9302 |  |  |  | HR9301 (Lo-16bits)
9303 | RTDIN:S13 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9304 | RTDIN:S13 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9305 |  |  |  | HR9304 (Lo-16bits)
9306 | RTDIN:S14 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9307 |  |  |  | HR9306 (Lo-16bits)
9308 | RTDIN:S14 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9309 |  |  |  | HR9308 (Lo-16bits)
9310 | RTDIN:S14 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9311 | RTDIN:S14 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9312 |  |  |  | HR9311 (Lo-16bits)
9313 | RTDIN:S15 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9314 |  |  |  | HR9313 (Lo-16bits)
9315 | RTDIN:S15 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9316 |  |  |  | HR9315 (Lo-16bits)
9317 | RTDIN:S15 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9318 |  |  |  | HR9317 (Lo-16bits)
9319 | RTDIN:S15 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9320 | RTDIN:S15 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9321 |  |  |  | HR9320 (Lo-16bits)
9322 | RTDIN:S16 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9323 |  |  |  | HR9322 (Lo-16bits)
9324 | RTDIN:S16 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9325 |  |  |  | HR9324 (Lo-16bits)
9326 | RTDIN:S16 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9327 |  |  |  | HR9326 (Lo-16bits)
9328 | RTDIN:S16 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9329 | RTDIN:S16 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9330 |  |  |  | HR9329 (Lo-16bits)
9331 | RTD1:S1 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9332 |  |  |  | HR9331 (Lo-16bits)
9333 | RTD1:S2 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9334 |  |  |  | HR9333 (Lo-16bits)
9335 | RTD1:S3 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9336 |  |  |  | HR9335 (Lo-16bits)
9337 | RTD1:S4 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9338 |  |  |  | HR9337 (Lo-16bits)
9339 | RTD1:S5 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9340 |  |  |  | HR9339 (Lo-16bits)
9341 | RTD1:S6 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9342 |  |  |  | HR9341 (Lo-16bits)
9343 | RTD1:S7 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9344 |  |  |  | HR9343 (Lo-16bits)
9345 | RTD1:S8 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9346 |  |  |  | HR9345 (Lo-16bits)
9347 | RTD1:S9 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9348 |  |  |  | HR9347 (Lo-16bits)
9349 | RTD1:S10 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9350 |  |  |  | HR9349 (Lo-16bits)
9351 | RTD1:S11 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9352 |  |  |  | HR9351 (Lo-16bits)
9353 | RTD1:S12 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9354 |  |  |  | HR9353 (Lo-16bits)
9355 | RTD1:S13 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9356 |  |  |  | HR9355 (Lo-16bits)
9357 | RTD1:S14 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9358 |  |  |  | HR9357 (Lo-16bits)
9359 | RTD1:S15 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9360 |  |  |  | HR9359 (Lo-16bits)
9361 | RTD1:S16 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9362 |  |  |  | HR9361 (Lo-16bits)
9363 | RTD1:S1 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9364 |  |  |  | HR9363 (Lo-16bits)
9365 | RTD1:S1 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9366 |  |  |  | HR9365 (Lo-16bits)
9367 | RTD1:S1 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9368 |  |  |  | HR9367 (Lo-16bits)
9369 | RTD1:S2 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9370 |  |  |  | HR9369 (Lo-16bits)
9371 | RTD1:S2 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9372 |  |  |  | HR9371 (Lo-16bits)
9373 | RTD1:S2 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9374 |  |  |  | HR9373 (Lo-16bits)
9375 | RTD1:S3 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9376 |  |  |  | HR9375 (Lo-16bits)
9377 | RTD1:S3 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9378 |  |  |  | HR9377 (Lo-16bits)
9379 | RTD1:S3 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9380 |  |  |  | HR9379 (Lo-16bits)
9381 | RTD1:S4 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9382 |  |  |  | HR9381 (Lo-16bits)
9383 | RTD1:S4 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9384 |  |  |  | HR9383 (Lo-16bits)
9385 | RTD1:S4 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9386 |  |  |  | HR9385 (Lo-16bits)
9387 | RTD1:S5 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9388 |  |  |  | HR9387 (Lo-16bits)
9389 | RTD1:S5 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9390 |  |  |  | HR9389 (Lo-16bits)
9391 | RTD1:S5 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9392 |  |  |  | HR9391 (Lo-16bits)
9393 | RTD1:S6 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9394 |  |  |  | HR9393 (Lo-16bits)
9395 | RTD1:S6 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9396 |  |  |  | HR9395 (Lo-16bits)
9397 | RTD1:S6 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9398 |  |  |  | HR9397 (Lo-16bits)
9399 | RTD1:S7 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9400 |  |  |  | HR9399 (Lo-16bits)
9401 | RTD1:S7 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9402 |  |  |  | HR9401 (Lo-16bits)
9403 | RTD1:S7 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9404 |  |  |  | HR9403 (Lo-16bits)
9405 | RTD1:S8 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9406 |  |  |  | HR9405 (Lo-16bits)
9407 | RTD1:S8 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9408 |  |  |  | HR9407 (Lo-16bits)
9409 | RTD1:S8 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9410 |  |  |  | HR9409 (Lo-16bits)
9411 | RTD1:S9 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9412 |  |  |  | HR9411 (Lo-16bits)
9413 | RTD1:S9 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9414 |  |  |  | HR9413 (Lo-16bits)
9415 | RTD1:S9 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9416 |  |  |  | HR9415 (Lo-16bits)
9417 | RTD1:S10 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9418 |  |  |  | HR9417 (Lo-16bits)
9419 | RTD1:S10 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9420 |  |  |  | HR9419 (Lo-16bits)
9421 | RTD1:S10 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9422 |  |  |  | HR9421 (Lo-16bits)
9423 | RTD1:S11 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9424 |  |  |  | HR9423 (Lo-16bits)
9425 | RTD1:S11 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9426 |  |  |  | HR9425 (Lo-16bits)
9427 | RTD1:S11 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9428 |  |  |  | HR9427 (Lo-16bits)
9429 | RTD1:S12 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9430 |  |  |  | HR9429 (Lo-16bits)
9431 | RTD1:S12 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9432 |  |  |  | HR9431 (Lo-16bits)
9433 | RTD1:S12 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9434 |  |  |  | HR9433 (Lo-16bits)
9435 | RTD1:S13 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9436 |  |  |  | HR9435 (Lo-16bits)
9437 | RTD1:S13 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9438 |  |  |  | HR9437 (Lo-16bits)
9439 | RTD1:S13 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9440 |  |  |  | HR9439 (Lo-16bits)
9441 | RTD1:S14 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9442 |  |  |  | HR9441 (Lo-16bits)
9443 | RTD1:S14 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9444 |  |  |  | HR9443 (Lo-16bits)
9445 | RTD1:S14 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9446 |  |  |  | HR9445 (Lo-16bits)
9447 | RTD1:S15 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9448 |  |  |  | HR9447 (Lo-16bits)
9449 | RTD1:S15 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9450 |  |  |  | HR9449 (Lo-16bits)
9451 | RTD1:S15 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9452 |  |  |  | HR9451 (Lo-16bits)
9453 | RTD1:S16 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9454 |  |  |  | HR9453 (Lo-16bits)
9455 | RTD1:S16 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9456 |  |  |  | HR9455 (Lo-16bits)
9457 | RTD1:S16 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9458 |  |  |  | HR9457 (Lo-16bits)
9459 | ARC1:I/I0 Arc> condition | R | 1 | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
9460 | ARC1:I/I0 Arc> S1 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9461 |  |  |  | HR9460 (Lo-16bits)
9462 | ARC1:I/I0 Arc> S2 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9463 |  |  |  | HR9462 (Lo-16bits)
9464 | ARC1:I/I0 Arc> S3 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9465 |  |  |  | HR9464 (Lo-16bits)
9466 | ARC1:I/I0 Arc> S4 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9467 |  |  |  | HR9466 (Lo-16bits)
9468 | ARC1:I/I0 Arc> IO unit fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9469 |  |  |  | HR9468 (Lo-16bits)
9470 | CTS1:CTS1 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9471 | CTS2:CTS2 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9472 | VTS1:VTS condition | R | 1 | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
9473 | VTS1:Bus voltages | R | 1 | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
9474 | FLX1:Fault locator condition | R | 1 | 0=Idle;1=Triggered;2=Calc ready
9475 | THD1:THD condition | R | 1 | 0=Normal;1=Start;2=Alarm;3=Blocked
9476 | CBW1:CBW condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On
9477 | NJK1:U0> RECL condition | R | 1 | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
9478 | SOF1:SOTF condition | R | 1 | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
9479 | PCS1:PCS1 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9480 |  |  |  | HR9479 (Lo-16bits)
9481 | PCS2:PCS2 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9482 |  |  |  | HR9481 (Lo-16bits)
9483 | PCS3:PCS3 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9484 |  |  |  | HR9483 (Lo-16bits)
9485 | PCS4:PCS4 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9486 |  |  |  | HR9485 (Lo-16bits)
9487 | PCS5:PCS5 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9488 |  |  |  | HR9487 (Lo-16bits)
9489 | SYN1:SYN1 Condition | R | 2 | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok (Hi-16bits)
9490 |  |  |  | HR9489 (Lo-16bits)
9491 | SYN1:SYN2 Condition | R | 2 | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok (Hi-16bits)
9492 |  |  |  | HR9491 (Lo-16bits)
9493 | SYN1:SYN3 Condition | R | 2 | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok (Hi-16bits)
9494 |  |  |  | HR9493 (Lo-16bits)
9495 | SYN1:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9496 |  |  |  | HR9495 (Lo-16bits)
9497 | SYN1:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9498 |  |  |  | HR9497 (Lo-16bits)
9499 | SYN1:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9500 |  |  |  | HR9499 (Lo-16bits)
9501 | SYN1:SYN2 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9502 |  |  |  | HR9501 (Lo-16bits)
9503 | SYN1:SYN2 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9504 |  |  |  | HR9503 (Lo-16bits)
9505 | SYN1:SYN2 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9506 |  |  |  | HR9505 (Lo-16bits)
9507 | SYN1:SYN3 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9508 |  |  |  | HR9507 (Lo-16bits)
9509 | SYN1:SYN3 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9510 |  |  |  | HR9509 (Lo-16bits)
9511 | SYN1:SYN3 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9512 |  |  |  | HR9511 (Lo-16bits)
9513 | VJP1:<DELTA><alpha> > condition | R | 1 | 0=Normal;1=Blocked;2=Trip;3=Alarm
9514 | VJP1:Voltage meas selected | R | 1 | 0=Selection Ok;1=Selection not available
9515 | OBJ1:Object1 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9516 | OBJ2:Object2 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9517 | OBJ3:Object3 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9518 | OBJ4:Object4 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9519 | OBJ5:Object5 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9520 | OBJ6:Object6 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9521 | OBJ7:Object7 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9522 | OBJ8:Object8 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9523 | OBJ9:Object9 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9524 | OBJ10:Object10 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9525 | CIN1:Ind.1 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9526 | CIN2:Ind.2 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9527 | CIN3:Ind.3 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9528 | CIN4:Ind.4 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9529 | CIN5:Ind.5 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9530 | AR1:Auto-recloser [79] Mode | RW | 1 | 0=Disabled;1=Activated
9531 | AR1:AR Status | R | 2 | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear (Hi-16bits)
9532 |  |  |  | HR9531 (Lo-16bits)
9533 | AR1:Timer active | R | 1 | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
9534 | VRG1:Vreg settings condition | R | 2 | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok (Hi-16bits)
9535 |  |  |  | HR9534 (Lo-16bits)
9536 | VRG1:Vreg condition | R | 2 | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on (Hi-16bits)
9537 |  |  |  | HR9536 (Lo-16bits)
9538 | VRG1:Vreg timer active | R | 1 | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
9539 | VRG1:Voltage now | R | 2 | FLOAT [0...140] (Hi-16bits)
9540 |  |  |  | HR9539 (Lo-16bits)
9541 | VRG1:Voltage difference to set target | R | 2 | FLOAT [-140...140] (Hi-16bits)
9542 |  |  |  | HR9541 (Lo-16bits)
9543 | VRG1:Voltage meas condition | R | 1 | 0=Not configured;1=System U12;2=System U23;3=System U31;4=VT4 meas U12;5=VT4 meas U23;6=VT4 meas U31;7=VT4 conf not ok
9544 | VRG1:Tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
9545 |  |  |  | HR9544 (Lo-16bits)
9546 | VRG1:Absolute tap location | R | 2 | FLOAT [0...50] (Hi-16bits)
9547 |  |  |  | HR9546 (Lo-16bits)
9548 | VRG1:Control mode | R | 1 | 0=Auto;1=Manual (loc&rem)
9549 | VRG1:Remote tap control input | RW | 1 | 0=Stop;1=Lower;2=Higher
9550 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9551 |  |  |  | HR9550 (Lo-16bits)
9552 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9553 |  |  |  | HR9552 (Lo-16bits)
9554 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9555 |  |  |  | HR9554 (Lo-16bits)
9556 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9557 |  |  |  | HR9556 (Lo-16bits)
9558 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9559 |  |  |  | HR9558 (Lo-16bits)
9560 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9561 |  |  |  | HR9560 (Lo-16bits)
9562 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9563 |  |  |  | HR9562 (Lo-16bits)
9564 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9565 |  |  |  | HR9564 (Lo-16bits)
9566 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9567 |  |  |  | HR9566 (Lo-16bits)
9568 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9569 |  |  |  | HR9568 (Lo-16bits)
9570 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9571 |  |  |  | HR9570 (Lo-16bits)
9572 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9573 |  |  |  | HR9572 (Lo-16bits)
9574 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9575 |  |  |  | HR9574 (Lo-16bits)
9576 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9577 |  |  |  | HR9576 (Lo-16bits)
9578 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9579 |  |  |  | HR9578 (Lo-16bits)
9580 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9581 |  |  |  | HR9580 (Lo-16bits)
9582 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9583 |  |  |  | HR9582 (Lo-16bits)
9584 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9585 |  |  |  | HR9584 (Lo-16bits)
9586 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9587 |  |  |  | HR9586 (Lo-16bits)
9588 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9589 |  |  |  | HR9588 (Lo-16bits)
9590 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9591 |  |  |  | HR9590 (Lo-16bits)
9592 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9593 |  |  |  | HR9592 (Lo-16bits)
9594 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9595 |  |  |  | HR9594 (Lo-16bits)
9596 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9597 |  |  |  | HR9596 (Lo-16bits)
9598 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9599 |  |  |  | HR9598 (Lo-16bits)
9600 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9601 |  |  |  | HR9600 (Lo-16bits)
9602 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9603 |  |  |  | HR9602 (Lo-16bits)
9604 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9605 |  |  |  | HR9604 (Lo-16bits)
9606 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9607 |  |  |  | HR9606 (Lo-16bits)
9608 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9609 |  |  |  | HR9608 (Lo-16bits)
9610 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9611 |  |  |  | HR9610 (Lo-16bits)
9612 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9613 |  |  |  | HR9612 (Lo-16bits)
9614 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9615 |  |  |  | HR9614 (Lo-16bits)
9616 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9617 |  |  |  | HR9616 (Lo-16bits)
9618 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9619 |  |  |  | HR9618 (Lo-16bits)
9620 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9621 |  |  |  | HR9620 (Lo-16bits)
9622 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9623 |  |  |  | HR9622 (Lo-16bits)
9624 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9625 |  |  |  | HR9624 (Lo-16bits)
9626 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9627 |  |  |  | HR9626 (Lo-16bits)
9628 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9629 |  |  |  | HR9628 (Lo-16bits)
9630 | EMON1:I> (50) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9631 | EMON1:I0> (50N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9632 | EMON1:Idir> (67) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9633 | EMON1:I0dir> (67N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9634 | EMON1:I0Int> (67NT) Monitor condition | R | 1 | 0=Normal;1=FLT FW;2=FLT REV
9635 | EMON1:U< (27) Monitor condition | R | 1 | 0=Normal;1=Undervoltage;2=No voltage
9636 | EMON1:U0> (59N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9637 | EMON1:FL (21FL) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9638 | ALARM:Alarms 1-32 | R | 2 | 0b=A1;1b=A2;2b=A3;3b=A4;4b=A5;5b=A6;6b=A7;7b=A8;8b=A9;9b=A10;10b=A11;11b=A12;12b=A13;13b=A14;14b=A15;15b=A16;16b=A17;17b=A18;18b=A19;19b=A20;20b=A21;21b=A22;22b=A23;23b=A24;24b=A25;25b=A26;26b=A27;27b=A28;28b=A29;29b=A30;30b=A31;31b=A32 (Hi-16bits)
9639 |  |  |  | HR9638 (Lo-16bits)
9640 | ALARM:Alarms 33-64 | R | 2 | 0b=A33;1b=A34;2b=A35;3b=A36;4b=A37;5b=A38;6b=A39;7b=A40;8b=A41;9b=A42;10b=A43;11b=A44;12b=A45;13b=A46;14b=A47;15b=A48;16b=A49;17b=A50;18b=A51;19b=A52;20b=A53;21b=A54;22b=A55;23b=A56;24b=A57;25b=A58;26b=A59;27b=A60;28b=A61;29b=A62;30b=A63;31b=A64 (Hi-16bits)
9641 |  |  |  | HR9640 (Lo-16bits)
9642 | GSYN:Synchronizer mode | RW | 1 | 0=Disabled;1=Activated
9643 | GSYN:Synchronizing by | RW | 1 | 0=Autosynchronizer;1=Manual commands
9644 | GSYN:Manual switching mode | RW | 1 | 0=Assisted synchroswitch;1=I know what I am doing
9645 | GSYN:Magnitude side A | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9646 |  |  |  | HR9645 (Lo-16bits)
9647 | GSYN:Magnitude side B | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9648 |  |  |  | HR9647 (Lo-16bits)
9649 | GSYN:Frequency side A | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9650 |  |  |  | HR9649 (Lo-16bits)
9651 | GSYN:Frequency side B | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9652 |  |  |  | HR9651 (Lo-16bits)
9653 | GSYN:Magnitude difference | R | 2 | FLOAT [-200...200] (Hi-16bits)
9654 |  |  |  | HR9653 (Lo-16bits)
9655 | GSYN:Frequency difference | R | 2 | FLOAT [-100...100] (Hi-16bits)
9656 |  |  |  | HR9655 (Lo-16bits)
9657 | GSYN:Angle difference | R | 2 | FLOAT [-360...360] (Hi-16bits)
9658 |  |  |  | HR9657 (Lo-16bits)
9659 | GSYN:Magnitude difference on closing BRK | R | 2 | FLOAT [-200...200] (Hi-16bits)
9660 |  |  |  | HR9659 (Lo-16bits)
9661 | GSYN:Frequency difference on closing BRK | R | 2 | FLOAT [-100...100] (Hi-16bits)
9662 |  |  |  | HR9661 (Lo-16bits)
9663 | GSYN:Angle difference on closing BRK | R | 2 | FLOAT [-360...360] (Hi-16bits)
9664 |  |  |  | HR9663 (Lo-16bits)
9665 | GSYN:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9666 |  |  |  | HR9665 (Lo-16bits)
9667 | GSYN:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9668 |  |  |  | HR9667 (Lo-16bits)
9669 | GSYN:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9670 |  |  |  | HR9669 (Lo-16bits)
9671 | GSYN:Synchronizing time left | R | 2 | FLOAT [0...1800] (Hi-16bits)
9672 |  |  |  | HR9671 (Lo-16bits)
9673 | GSYN:Magnitude difference fine tune | RW | 2 | FLOAT [-200...200] (Hi-16bits)
9674 |  |  |  | HR9673 (Lo-16bits)
9675 | GSYN:Frequency difference fine tune | RW | 2 | FLOAT [-100...100] (Hi-16bits)
9676 |  |  |  | HR9675 (Lo-16bits)
9677 | GSYN:Angle difference fine tune | RW | 2 | FLOAT [-360...360] (Hi-16bits)
9678 |  |  |  | HR9677 (Lo-16bits)
9679 | GSYN:Start Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9680 |  |  |  | HR9679 (Lo-16bits)
9681 | GSYN:Stop Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9682 |  |  |  | HR9681 (Lo-16bits)
9683 | GSYN:Block and Interrupt Synchronizing | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9684 |  |  |  | HR9683 (Lo-16bits)
9685 | GSYN:Breaker Closed | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9686 |  |  |  | HR9685 (Lo-16bits)
9687 | GSYN:Manual increase voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9688 |  |  |  | HR9687 (Lo-16bits)
9689 | GSYN:Manual decrease voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9690 |  |  |  | HR9689 (Lo-16bits)
9691 | GSYN:Manual increase frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9692 |  |  |  | HR9691 (Lo-16bits)
9693 | GSYN:Manual decrease frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9694 |  |  |  | HR9693 (Lo-16bits)
9695 | GSYN:Manual Close Breaker | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9696 |  |  |  | HR9695 (Lo-16bits)
9697 | GSYN:GSYN Voltage Mag.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9698 |  |  |  | HR9697 (Lo-16bits)
9699 | GSYN:GSYN Voltage Freq.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9700 |  |  |  | HR9699 (Lo-16bits)
9701 | GSYN:GSYN Voltage Ang.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9702 |  |  |  | HR9701 (Lo-16bits)
9703 | GSYN:GSYN Blocked | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9704 |  |  |  | HR9703 (Lo-16bits)
9705 | GSYN:GSYN Running | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9706 |  |  |  | HR9705 (Lo-16bits)
9707 | GSYN:GSYN Increase Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9708 |  |  |  | HR9707 (Lo-16bits)
9709 | GSYN:GSYN Decrease Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9710 |  |  |  | HR9709 (Lo-16bits)
9711 | GSYN:GSYN Increase Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9712 |  |  |  | HR9711 (Lo-16bits)
9713 | GSYN:GSYN Decrease Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9714 |  |  |  | HR9713 (Lo-16bits)
9715 | GSYN:GSYN Breaker Close Pulse | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9716 |  |  |  | HR9715 (Lo-16bits)
9717 | GSYN:GSYN Long Sync Time | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9718 |  |  |  | HR9717 (Lo-16bits)
9719 | GSYN:GSYN Nets Standstill | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9720 |  |  |  | HR9719 (Lo-16bits)
9721 | GSYN:GSYN Nets Departing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9722 |  |  |  | HR9721 (Lo-16bits)
9723 | GSYN:GSYN Nets Enclosing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9724 |  |  |  | HR9723 (Lo-16bits)
9725 | VREC:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9726 | VREC:Scale current values to primary | RW | 1 | 0=No;1=Yes
9727 | VREC:Record fault types (Overcurrrent & Voltage Over/Under) faults | RW | 1 | 0=No;1=Yes
9728 | VREC:Trigger register to memory | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9729 |  |  |  | HR9728 (Lo-16bits)
9730 | VREC:VREC Magnitude 1 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9731 |  |  |  | HR9730 (Lo-16bits)
9732 | VREC:VREC Magnitude 2 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9733 |  |  |  | HR9732 (Lo-16bits)
9734 | VREC:VREC Magnitude 3 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9735 |  |  |  | HR9734 (Lo-16bits)
9736 | VREC:VREC Magnitude 4 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9737 |  |  |  | HR9736 (Lo-16bits)
9738 | VREC:VREC Magnitude 5 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9739 |  |  |  | HR9738 (Lo-16bits)
9740 | VREC:VREC Magnitude 6 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9741 |  |  |  | HR9740 (Lo-16bits)
9742 | VREC:VREC Magnitude 7 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9743 |  |  |  | HR9742 (Lo-16bits)
9744 | VREC:VREC Magnitude 8 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9745 |  |  |  | HR9744 (Lo-16bits)
9746 | RTB:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9747 | RTB:Scale current values to primary | RW | 1 | 0=No;1=Yes
9748 | RTB:RTS to bus Magnitude 1 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9749 |  |  |  | HR9748 (Lo-16bits)
9750 | RTB:RTS to bus Magnitude 2 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9751 |  |  |  | HR9750 (Lo-16bits)
9752 | RTB:RTS to bus Magnitude 3 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9753 |  |  |  | HR9752 (Lo-16bits)
9754 | RTB:RTS to bus Magnitude 4 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9755 |  |  |  | HR9754 (Lo-16bits)
9756 | RTB:RTS to bus Magnitude 5 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9757 |  |  |  | HR9756 (Lo-16bits)
9758 | RTB:RTS to bus Magnitude 6 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9759 |  |  |  | HR9758 (Lo-16bits)
9760 | RTB:RTS to bus Magnitude 7 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9761 |  |  |  | HR9760 (Lo-16bits)
9762 | RTB:RTS to bus Magnitude 8 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9763 |  |  |  | HR9762 (Lo-16bits)
9764 | RTB:RTS to bus Magnitude 9 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9765 |  |  |  | HR9764 (Lo-16bits)
9766 | RTB:RTS to bus Magnitude 10 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9767 |  |  |  | HR9766 (Lo-16bits)
9768 | AOUT:mA In Channel 1 | R | 2 | FLOAT [0...24] (Hi-16bits)
9769 |  |  |  | HR9768 (Lo-16bits)
9770 | AOUT:mA In Channel 2 | R | 2 | FLOAT [0...24] (Hi-16bits)
9771 |  |  |  | HR9770 (Lo-16bits)
9772 | AOUT:mA Out Channel 1 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9773 |  |  |  | HR9772 (Lo-16bits)
9774 | AOUT:mA Out Channel 1 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9775 |  |  |  | HR9774 (Lo-16bits)
9776 | AOUT:mA Out Channel 2 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9777 |  |  |  | HR9776 (Lo-16bits)
9778 | AOUT:mA Out Channel 2 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9779 |  |  |  | HR9778 (Lo-16bits)
9780 | AOUT:mA Out Channel 3 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9781 |  |  |  | HR9780 (Lo-16bits)
9782 | AOUT:mA Out Channel 3 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9783 |  |  |  | HR9782 (Lo-16bits)
9784 | AOUT:mA Out Channel 4 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9785 |  |  |  | HR9784 (Lo-16bits)
9786 | AOUT:mA Out Channel 4 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9787 |  |  |  | HR9786 (Lo-16bits)
9788 | AOUT:mA Out Channel 5 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9789 |  |  |  | HR9788 (Lo-16bits)
9790 | AOUT:mA Out Channel 5 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9791 |  |  |  | HR9790 (Lo-16bits)
9792 | AOUT:mA Out Channel 6 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9793 |  |  |  | HR9792 (Lo-16bits)
9794 | AOUT:mA Out Channel 6 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9795 |  |  |  | HR9794 (Lo-16bits)
9796 | AOUT:mA Out Channel 7 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9797 |  |  |  | HR9796 (Lo-16bits)
9798 | AOUT:mA Out Channel 7 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9799 |  |  |  | HR9798 (Lo-16bits)
9800 | AOUT:mA Out Channel 8 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9801 |  |  |  | HR9800 (Lo-16bits)
9802 | AOUT:mA Out Channel 8 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9803 |  |  |  | HR9802 (Lo-16bits)
9906 | Object6 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9907 | Object7 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9908 | Object8 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9909 | Object9 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9910 | Object10 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020

## AQ-G215, v2.1.1.3-247
HR | Parameter | Access | Length | Info
1 | Modbus requests | R/W=0 | 1 | Diagnostic request counter
2 | Modbus quality | R | 1 | Diagnostic quality
3 | Modbus errors | R/W=0 | 1 | Diagnostic error counter
4 | Modbus Ctrl OK | R/W=0 | 1 | Diagnostic Control OK counter
5 | Modbus Ctrl Errors | R/W=0 | 1 | Diagnostic Control Error counter
6 | Object1 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
7 | Object2 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
8 | Object3 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9 | Object4 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
10 | Object5 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
11 | Previous Event register | R | 6 | Event code
12 | Previous Event register | R | 6 | Event timestamp (ms)
13 | Previous Event register | R | 6 | Event timestamp (sec Hi-16bits)
14 | Previous Event register | R | 6 | Event timestamp (sec Lo-16bits)
15 | Previous Event register | R | 6 | Event sequential index
16 | Previous Event register | R | 6 | RESERVED
17 | Event register | R | 6 | Event code
18 | Event register | R | 6 | Event timestamp (ms)
19 | Event register | R | 6 | Event timestamp (sec Hi-16bits)
20 | Event register | R | 6 | Event timestamp (sec Lo-16bits)
21 | Event register | R | 6 | Event sequential index
22 | Event register | R | 6 | RESERVED
23 | System time | RW | 3 | System time (ms)
24 | System time | RW | 3 | System time (sec Hi-16bits)
25 | System time | RW | 3 | System time (sec Lo-16bits)
26 | MEAS1:Pri.Pha.curr.IL1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
27 |  |  |  | HR26 (Lo-16bits)
28 | MEAS1:Pri.Pha.curr.IL2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
29 |  |  |  | HR28 (Lo-16bits)
30 | MEAS1:Pri.Pha.curr.IL3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
31 |  |  |  | HR30 (Lo-16bits)
32 | MEAS1:Pri.Res.curr.I01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
33 |  |  |  | HR32 (Lo-16bits)
34 | MEAS1:Pri.Res.curr.I02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
35 |  |  |  | HR34 (Lo-16bits)
36 | MEAS1:Pha.angle IL1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
37 |  |  |  | HR36 (Lo-16bits)
38 | MEAS1:Pha.angle IL2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
39 |  |  |  | HR38 (Lo-16bits)
40 | MEAS1:Pha.angle IL3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
41 |  |  |  | HR40 (Lo-16bits)
42 | MEAS1:Res.curr.angle I01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
43 |  |  |  | HR42 (Lo-16bits)
44 | MEAS1:Res.curr.angle I02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
45 |  |  |  | HR44 (Lo-16bits)
46 | MEAS1:Pri.calc.I0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
47 |  |  |  | HR46 (Lo-16bits)
48 | MEAS1:calc.I0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
49 |  |  |  | HR48 (Lo-16bits)
50 | MEAS1:Pha.curr.IL1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
51 |  |  |  | HR50 (Lo-16bits)
52 | MEAS1:Pha.curr.IL2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
53 |  |  |  | HR52 (Lo-16bits)
54 | MEAS1:Pha.curr.IL3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
55 |  |  |  | HR54 (Lo-16bits)
56 | MEAS1:Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
57 |  |  |  | HR56 (Lo-16bits)
58 | MEAS1:Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
59 |  |  |  | HR58 (Lo-16bits)
60 | MEAS1:Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
61 |  |  |  | HR60 (Lo-16bits)
62 | MEAS1:Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
63 |  |  |  | HR62 (Lo-16bits)
64 | MEAS1:Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
65 |  |  |  | HR64 (Lo-16bits)
66 | MEAS1:Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
67 |  |  |  | HR66 (Lo-16bits)
68 | MEAS1:Res.curr.I01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
69 |  |  |  | HR68 (Lo-16bits)
70 | MEAS1:Res.curr.I02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
71 |  |  |  | HR70 (Lo-16bits)
72 | MEAS1:Pha.L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
73 |  |  |  | HR72 (Lo-16bits)
74 | MEAS1:Pha.L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
75 |  |  |  | HR74 (Lo-16bits)
76 | MEAS1:Pha.L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
77 |  |  |  | HR76 (Lo-16bits)
78 | MEAS1:Pha.L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
79 |  |  |  | HR78 (Lo-16bits)
80 | MEAS1:Pha.L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
81 |  |  |  | HR80 (Lo-16bits)
82 | MEAS1:Pha.L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
83 |  |  |  | HR82 (Lo-16bits)
84 | MEAS1:Res.I01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
85 |  |  |  | HR84 (Lo-16bits)
86 | MEAS1:Res.I01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
87 |  |  |  | HR86 (Lo-16bits)
88 | MEAS1:Res.I02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
89 |  |  |  | HR88 (Lo-16bits)
90 | MEAS1:Res.I02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
91 |  |  |  | HR90 (Lo-16bits)
92 | MEAS1:P-P curr.IL1 | R | 2 | FLOAT [0...500] (Hi-16bits)
93 |  |  |  | HR92 (Lo-16bits)
94 | MEAS1:P-P curr.IL2 | R | 2 | FLOAT [0...500] (Hi-16bits)
95 |  |  |  | HR94 (Lo-16bits)
96 | MEAS1:P-P curr.IL3 | R | 2 | FLOAT [0...500] (Hi-16bits)
97 |  |  |  | HR96 (Lo-16bits)
98 | MEAS1:P-P curr.I01 | R | 2 | FLOAT [0...500] (Hi-16bits)
99 |  |  |  | HR98 (Lo-16bits)
100 | MEAS1:P-P curr.I02 | R | 2 | FLOAT [0...500] (Hi-16bits)
101 |  |  |  | HR100 (Lo-16bits)
102 | MEAS1:IL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
103 |  |  |  | HR102 (Lo-16bits)
104 | MEAS1:IL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
105 |  |  |  | HR104 (Lo-16bits)
106 | MEAS1:IL1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
107 |  |  |  | HR106 (Lo-16bits)
108 | MEAS1:IL1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
109 |  |  |  | HR108 (Lo-16bits)
110 | MEAS1:IL1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
111 |  |  |  | HR110 (Lo-16bits)
112 | MEAS1:IL1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
113 |  |  |  | HR112 (Lo-16bits)
114 | MEAS1:IL1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
115 |  |  |  | HR114 (Lo-16bits)
116 | MEAS1:IL1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
117 |  |  |  | HR116 (Lo-16bits)
118 | MEAS1:IL1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
119 |  |  |  | HR118 (Lo-16bits)
120 | MEAS1:IL1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
121 |  |  |  | HR120 (Lo-16bits)
122 | MEAS1:IL1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
123 |  |  |  | HR122 (Lo-16bits)
124 | MEAS1:IL1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
125 |  |  |  | HR124 (Lo-16bits)
126 | MEAS1:IL1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
127 |  |  |  | HR126 (Lo-16bits)
128 | MEAS1:IL1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
129 |  |  |  | HR128 (Lo-16bits)
130 | MEAS1:IL1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
131 |  |  |  | HR130 (Lo-16bits)
132 | MEAS1:IL1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
133 |  |  |  | HR132 (Lo-16bits)
134 | MEAS1:IL1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
135 |  |  |  | HR134 (Lo-16bits)
136 | MEAS1:IL1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
137 |  |  |  | HR136 (Lo-16bits)
138 | MEAS1:IL1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
139 |  |  |  | HR138 (Lo-16bits)
140 | MEAS1:IL1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
141 |  |  |  | HR140 (Lo-16bits)
142 | MEAS1:IL1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
143 |  |  |  | HR142 (Lo-16bits)
144 | MEAS1:IL1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
145 |  |  |  | HR144 (Lo-16bits)
146 | MEAS1:IL1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
147 |  |  |  | HR146 (Lo-16bits)
148 | MEAS1:IL1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
149 |  |  |  | HR148 (Lo-16bits)
150 | MEAS1:IL1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
151 |  |  |  | HR150 (Lo-16bits)
152 | MEAS1:IL1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
153 |  |  |  | HR152 (Lo-16bits)
154 | MEAS1:IL1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
155 |  |  |  | HR154 (Lo-16bits)
156 | MEAS1:IL1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
157 |  |  |  | HR156 (Lo-16bits)
158 | MEAS1:IL1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
159 |  |  |  | HR158 (Lo-16bits)
160 | MEAS1:IL1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
161 |  |  |  | HR160 (Lo-16bits)
162 | MEAS1:IL1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
163 |  |  |  | HR162 (Lo-16bits)
164 | MEAS1:IL1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
165 |  |  |  | HR164 (Lo-16bits)
166 | MEAS1:IL1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
167 |  |  |  | HR166 (Lo-16bits)
168 | MEAS1:IL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
169 |  |  |  | HR168 (Lo-16bits)
170 | MEAS1:IL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
171 |  |  |  | HR170 (Lo-16bits)
172 | MEAS1:IL2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
173 |  |  |  | HR172 (Lo-16bits)
174 | MEAS1:IL2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
175 |  |  |  | HR174 (Lo-16bits)
176 | MEAS1:IL2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
177 |  |  |  | HR176 (Lo-16bits)
178 | MEAS1:IL2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
179 |  |  |  | HR178 (Lo-16bits)
180 | MEAS1:IL2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
181 |  |  |  | HR180 (Lo-16bits)
182 | MEAS1:IL2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
183 |  |  |  | HR182 (Lo-16bits)
184 | MEAS1:IL2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
185 |  |  |  | HR184 (Lo-16bits)
186 | MEAS1:IL2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
187 |  |  |  | HR186 (Lo-16bits)
188 | MEAS1:IL2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
189 |  |  |  | HR188 (Lo-16bits)
190 | MEAS1:IL2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
191 |  |  |  | HR190 (Lo-16bits)
192 | MEAS1:IL2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
193 |  |  |  | HR192 (Lo-16bits)
194 | MEAS1:IL2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
195 |  |  |  | HR194 (Lo-16bits)
196 | MEAS1:IL2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
197 |  |  |  | HR196 (Lo-16bits)
198 | MEAS1:IL2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
199 |  |  |  | HR198 (Lo-16bits)
200 | MEAS1:IL2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
201 |  |  |  | HR200 (Lo-16bits)
202 | MEAS1:IL2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
203 |  |  |  | HR202 (Lo-16bits)
204 | MEAS1:IL2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
205 |  |  |  | HR204 (Lo-16bits)
206 | MEAS1:IL2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
207 |  |  |  | HR206 (Lo-16bits)
208 | MEAS1:IL2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
209 |  |  |  | HR208 (Lo-16bits)
210 | MEAS1:IL2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
211 |  |  |  | HR210 (Lo-16bits)
212 | MEAS1:IL2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
213 |  |  |  | HR212 (Lo-16bits)
214 | MEAS1:IL2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
215 |  |  |  | HR214 (Lo-16bits)
216 | MEAS1:IL2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
217 |  |  |  | HR216 (Lo-16bits)
218 | MEAS1:IL2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
219 |  |  |  | HR218 (Lo-16bits)
220 | MEAS1:IL2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
221 |  |  |  | HR220 (Lo-16bits)
222 | MEAS1:IL2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
223 |  |  |  | HR222 (Lo-16bits)
224 | MEAS1:IL2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
225 |  |  |  | HR224 (Lo-16bits)
226 | MEAS1:IL2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
227 |  |  |  | HR226 (Lo-16bits)
228 | MEAS1:IL2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
229 |  |  |  | HR228 (Lo-16bits)
230 | MEAS1:IL2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
231 |  |  |  | HR230 (Lo-16bits)
232 | MEAS1:IL2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
233 |  |  |  | HR232 (Lo-16bits)
234 | MEAS1:IL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
235 |  |  |  | HR234 (Lo-16bits)
236 | MEAS1:IL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
237 |  |  |  | HR236 (Lo-16bits)
238 | MEAS1:IL3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
239 |  |  |  | HR238 (Lo-16bits)
240 | MEAS1:IL3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
241 |  |  |  | HR240 (Lo-16bits)
242 | MEAS1:IL3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
243 |  |  |  | HR242 (Lo-16bits)
244 | MEAS1:IL3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
245 |  |  |  | HR244 (Lo-16bits)
246 | MEAS1:IL3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
247 |  |  |  | HR246 (Lo-16bits)
248 | MEAS1:IL3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
249 |  |  |  | HR248 (Lo-16bits)
250 | MEAS1:IL3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
251 |  |  |  | HR250 (Lo-16bits)
252 | MEAS1:IL3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
253 |  |  |  | HR252 (Lo-16bits)
254 | MEAS1:IL3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
255 |  |  |  | HR254 (Lo-16bits)
256 | MEAS1:IL3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
257 |  |  |  | HR256 (Lo-16bits)
258 | MEAS1:IL3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
259 |  |  |  | HR258 (Lo-16bits)
260 | MEAS1:IL3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
261 |  |  |  | HR260 (Lo-16bits)
262 | MEAS1:IL3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
263 |  |  |  | HR262 (Lo-16bits)
264 | MEAS1:IL3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
265 |  |  |  | HR264 (Lo-16bits)
266 | MEAS1:IL3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
267 |  |  |  | HR266 (Lo-16bits)
268 | MEAS1:IL3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
269 |  |  |  | HR268 (Lo-16bits)
270 | MEAS1:IL3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
271 |  |  |  | HR270 (Lo-16bits)
272 | MEAS1:IL3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
273 |  |  |  | HR272 (Lo-16bits)
274 | MEAS1:IL3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
275 |  |  |  | HR274 (Lo-16bits)
276 | MEAS1:IL3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
277 |  |  |  | HR276 (Lo-16bits)
278 | MEAS1:IL3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
279 |  |  |  | HR278 (Lo-16bits)
280 | MEAS1:IL3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
281 |  |  |  | HR280 (Lo-16bits)
282 | MEAS1:IL3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
283 |  |  |  | HR282 (Lo-16bits)
284 | MEAS1:IL3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
285 |  |  |  | HR284 (Lo-16bits)
286 | MEAS1:IL3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
287 |  |  |  | HR286 (Lo-16bits)
288 | MEAS1:IL3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
289 |  |  |  | HR288 (Lo-16bits)
290 | MEAS1:IL3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
291 |  |  |  | HR290 (Lo-16bits)
292 | MEAS1:IL3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
293 |  |  |  | HR292 (Lo-16bits)
294 | MEAS1:IL3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
295 |  |  |  | HR294 (Lo-16bits)
296 | MEAS1:IL3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
297 |  |  |  | HR296 (Lo-16bits)
298 | MEAS1:IL3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
299 |  |  |  | HR298 (Lo-16bits)
300 | MEAS1:I01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
301 |  |  |  | HR300 (Lo-16bits)
302 | MEAS1:I01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
303 |  |  |  | HR302 (Lo-16bits)
304 | MEAS1:I01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
305 |  |  |  | HR304 (Lo-16bits)
306 | MEAS1:I01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
307 |  |  |  | HR306 (Lo-16bits)
308 | MEAS1:I01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
309 |  |  |  | HR308 (Lo-16bits)
310 | MEAS1:I01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
311 |  |  |  | HR310 (Lo-16bits)
312 | MEAS1:I01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
313 |  |  |  | HR312 (Lo-16bits)
314 | MEAS1:I01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
315 |  |  |  | HR314 (Lo-16bits)
316 | MEAS1:I01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
317 |  |  |  | HR316 (Lo-16bits)
318 | MEAS1:I01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
319 |  |  |  | HR318 (Lo-16bits)
320 | MEAS1:I01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
321 |  |  |  | HR320 (Lo-16bits)
322 | MEAS1:I01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
323 |  |  |  | HR322 (Lo-16bits)
324 | MEAS1:I01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
325 |  |  |  | HR324 (Lo-16bits)
326 | MEAS1:I01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
327 |  |  |  | HR326 (Lo-16bits)
328 | MEAS1:I01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
329 |  |  |  | HR328 (Lo-16bits)
330 | MEAS1:I01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
331 |  |  |  | HR330 (Lo-16bits)
332 | MEAS1:I01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
333 |  |  |  | HR332 (Lo-16bits)
334 | MEAS1:I01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
335 |  |  |  | HR334 (Lo-16bits)
336 | MEAS1:I01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
337 |  |  |  | HR336 (Lo-16bits)
338 | MEAS1:I01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
339 |  |  |  | HR338 (Lo-16bits)
340 | MEAS1:I01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
341 |  |  |  | HR340 (Lo-16bits)
342 | MEAS1:I01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
343 |  |  |  | HR342 (Lo-16bits)
344 | MEAS1:I01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
345 |  |  |  | HR344 (Lo-16bits)
346 | MEAS1:I01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
347 |  |  |  | HR346 (Lo-16bits)
348 | MEAS1:I01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
349 |  |  |  | HR348 (Lo-16bits)
350 | MEAS1:I01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
351 |  |  |  | HR350 (Lo-16bits)
352 | MEAS1:I01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
353 |  |  |  | HR352 (Lo-16bits)
354 | MEAS1:I01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
355 |  |  |  | HR354 (Lo-16bits)
356 | MEAS1:I01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
357 |  |  |  | HR356 (Lo-16bits)
358 | MEAS1:I01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
359 |  |  |  | HR358 (Lo-16bits)
360 | MEAS1:I01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
361 |  |  |  | HR360 (Lo-16bits)
362 | MEAS1:I01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
363 |  |  |  | HR362 (Lo-16bits)
364 | MEAS1:I01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
365 |  |  |  | HR364 (Lo-16bits)
366 | MEAS1:I02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
367 |  |  |  | HR366 (Lo-16bits)
368 | MEAS1:I02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
369 |  |  |  | HR368 (Lo-16bits)
370 | MEAS1:I02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
371 |  |  |  | HR370 (Lo-16bits)
372 | MEAS1:I02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
373 |  |  |  | HR372 (Lo-16bits)
374 | MEAS1:I02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
375 |  |  |  | HR374 (Lo-16bits)
376 | MEAS1:I02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
377 |  |  |  | HR376 (Lo-16bits)
378 | MEAS1:I02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
379 |  |  |  | HR378 (Lo-16bits)
380 | MEAS1:I02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
381 |  |  |  | HR380 (Lo-16bits)
382 | MEAS1:I02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
383 |  |  |  | HR382 (Lo-16bits)
384 | MEAS1:I02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
385 |  |  |  | HR384 (Lo-16bits)
386 | MEAS1:I02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
387 |  |  |  | HR386 (Lo-16bits)
388 | MEAS1:I02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
389 |  |  |  | HR388 (Lo-16bits)
390 | MEAS1:I02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
391 |  |  |  | HR390 (Lo-16bits)
392 | MEAS1:I02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
393 |  |  |  | HR392 (Lo-16bits)
394 | MEAS1:I02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
395 |  |  |  | HR394 (Lo-16bits)
396 | MEAS1:I02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
397 |  |  |  | HR396 (Lo-16bits)
398 | MEAS1:I02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
399 |  |  |  | HR398 (Lo-16bits)
400 | MEAS1:I02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
401 |  |  |  | HR400 (Lo-16bits)
402 | MEAS1:I02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
403 |  |  |  | HR402 (Lo-16bits)
404 | MEAS1:I02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
405 |  |  |  | HR404 (Lo-16bits)
406 | MEAS1:I02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
407 |  |  |  | HR406 (Lo-16bits)
408 | MEAS1:I02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
409 |  |  |  | HR408 (Lo-16bits)
410 | MEAS1:I02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
411 |  |  |  | HR410 (Lo-16bits)
412 | MEAS1:I02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
413 |  |  |  | HR412 (Lo-16bits)
414 | MEAS1:I02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
415 |  |  |  | HR414 (Lo-16bits)
416 | MEAS1:I02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
417 |  |  |  | HR416 (Lo-16bits)
418 | MEAS1:I02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
419 |  |  |  | HR418 (Lo-16bits)
420 | MEAS1:I02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
421 |  |  |  | HR420 (Lo-16bits)
422 | MEAS1:I02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
423 |  |  |  | HR422 (Lo-16bits)
424 | MEAS1:I02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
425 |  |  |  | HR424 (Lo-16bits)
426 | MEAS1:I02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
427 |  |  |  | HR426 (Lo-16bits)
428 | MEAS1:I02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
429 |  |  |  | HR428 (Lo-16bits)
430 | MEAS1:I02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
431 |  |  |  | HR430 (Lo-16bits)
432 | MEAS1:Meas1 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
433 |  |  |  | HR432 (Lo-16bits)
434 | MEAS2:Pri.Pha.curr.I''L1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
435 |  |  |  | HR434 (Lo-16bits)
436 | MEAS2:Pri.Pha.curr.I''L2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
437 |  |  |  | HR436 (Lo-16bits)
438 | MEAS2:Pri.Pha.curr.I''L3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
439 |  |  |  | HR438 (Lo-16bits)
440 | MEAS2:Pha.angle I''L1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
441 |  |  |  | HR440 (Lo-16bits)
442 | MEAS2:Pha.angle I''L2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
443 |  |  |  | HR442 (Lo-16bits)
444 | MEAS2:Pha.angle I''L3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
445 |  |  |  | HR444 (Lo-16bits)
446 | MEAS2:Pri.Res.curr.I''01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
447 |  |  |  | HR446 (Lo-16bits)
448 | MEAS2:Res.curr.angle I''01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
449 |  |  |  | HR448 (Lo-16bits)
450 | MEAS2:Pri.Res.curr.I''02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
451 |  |  |  | HR450 (Lo-16bits)
452 | MEAS2:Res.curr.angle I''02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
453 |  |  |  | HR452 (Lo-16bits)
454 | MEAS2:Pri.calc.I''0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
455 |  |  |  | HR454 (Lo-16bits)
456 | MEAS2:calc.I''0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
457 |  |  |  | HR456 (Lo-16bits)
458 | MEAS2:Pha.curr.I''L1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
459 |  |  |  | HR458 (Lo-16bits)
460 | MEAS2:Pha.curr.I''L2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
461 |  |  |  | HR460 (Lo-16bits)
462 | MEAS2:Pha.curr.I''L3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
463 |  |  |  | HR462 (Lo-16bits)
464 | MEAS2:I'' Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
465 |  |  |  | HR464 (Lo-16bits)
466 | MEAS2:I'' Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
467 |  |  |  | HR466 (Lo-16bits)
468 | MEAS2:I'' Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
469 |  |  |  | HR468 (Lo-16bits)
470 | MEAS2:I'' Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
471 |  |  |  | HR470 (Lo-16bits)
472 | MEAS2:I'' Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
473 |  |  |  | HR472 (Lo-16bits)
474 | MEAS2:I'' Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
475 |  |  |  | HR474 (Lo-16bits)
476 | MEAS2:Res.curr.I''01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
477 |  |  |  | HR476 (Lo-16bits)
478 | MEAS2:Res.curr.I''02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
479 |  |  |  | HR478 (Lo-16bits)
480 | MEAS2:Pha.I''L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
481 |  |  |  | HR480 (Lo-16bits)
482 | MEAS2:Pha.I''L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
483 |  |  |  | HR482 (Lo-16bits)
484 | MEAS2:Pha.I''L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
485 |  |  |  | HR484 (Lo-16bits)
486 | MEAS2:Pha.I''L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
487 |  |  |  | HR486 (Lo-16bits)
488 | MEAS2:Pha.I''L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
489 |  |  |  | HR488 (Lo-16bits)
490 | MEAS2:Pha.I''L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
491 |  |  |  | HR490 (Lo-16bits)
492 | MEAS2:Res.I''01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
493 |  |  |  | HR492 (Lo-16bits)
494 | MEAS2:Res.I''01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
495 |  |  |  | HR494 (Lo-16bits)
496 | MEAS2:Res.I''02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
497 |  |  |  | HR496 (Lo-16bits)
498 | MEAS2:Res.I''02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
499 |  |  |  | HR498 (Lo-16bits)
500 | MEAS2:P-P curr.I''L1 | R | 2 | FLOAT [0...500] (Hi-16bits)
501 |  |  |  | HR500 (Lo-16bits)
502 | MEAS2:P-P curr.I''L2 | R | 2 | FLOAT [0...500] (Hi-16bits)
503 |  |  |  | HR502 (Lo-16bits)
504 | MEAS2:P-P curr.I''L3 | R | 2 | FLOAT [0...500] (Hi-16bits)
505 |  |  |  | HR504 (Lo-16bits)
506 | MEAS2:P-P curr.I''01 | R | 2 | FLOAT [0...500] (Hi-16bits)
507 |  |  |  | HR506 (Lo-16bits)
508 | MEAS2:P-P curr.I''02 | R | 2 | FLOAT [0...500] (Hi-16bits)
509 |  |  |  | HR508 (Lo-16bits)
510 | MEAS2:I''L1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
511 |  |  |  | HR510 (Lo-16bits)
512 | MEAS2:I''L1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
513 |  |  |  | HR512 (Lo-16bits)
514 | MEAS2:I''L1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
515 |  |  |  | HR514 (Lo-16bits)
516 | MEAS2:I''L1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
517 |  |  |  | HR516 (Lo-16bits)
518 | MEAS2:I''L1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
519 |  |  |  | HR518 (Lo-16bits)
520 | MEAS2:I''L1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
521 |  |  |  | HR520 (Lo-16bits)
522 | MEAS2:I''L1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
523 |  |  |  | HR522 (Lo-16bits)
524 | MEAS2:I''L1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
525 |  |  |  | HR524 (Lo-16bits)
526 | MEAS2:I''L1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
527 |  |  |  | HR526 (Lo-16bits)
528 | MEAS2:I''L1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
529 |  |  |  | HR528 (Lo-16bits)
530 | MEAS2:I''L1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
531 |  |  |  | HR530 (Lo-16bits)
532 | MEAS2:I''L1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
533 |  |  |  | HR532 (Lo-16bits)
534 | MEAS2:I''L1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
535 |  |  |  | HR534 (Lo-16bits)
536 | MEAS2:I''L1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
537 |  |  |  | HR536 (Lo-16bits)
538 | MEAS2:I''L1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
539 |  |  |  | HR538 (Lo-16bits)
540 | MEAS2:I''L1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
541 |  |  |  | HR540 (Lo-16bits)
542 | MEAS2:I''L1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
543 |  |  |  | HR542 (Lo-16bits)
544 | MEAS2:I''L1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
545 |  |  |  | HR544 (Lo-16bits)
546 | MEAS2:I''L1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
547 |  |  |  | HR546 (Lo-16bits)
548 | MEAS2:I''L1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
549 |  |  |  | HR548 (Lo-16bits)
550 | MEAS2:I''L1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
551 |  |  |  | HR550 (Lo-16bits)
552 | MEAS2:I''L1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
553 |  |  |  | HR552 (Lo-16bits)
554 | MEAS2:I''L1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
555 |  |  |  | HR554 (Lo-16bits)
556 | MEAS2:I''L1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
557 |  |  |  | HR556 (Lo-16bits)
558 | MEAS2:I''L1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
559 |  |  |  | HR558 (Lo-16bits)
560 | MEAS2:I''L1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
561 |  |  |  | HR560 (Lo-16bits)
562 | MEAS2:I''L1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
563 |  |  |  | HR562 (Lo-16bits)
564 | MEAS2:I''L1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
565 |  |  |  | HR564 (Lo-16bits)
566 | MEAS2:I''L1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
567 |  |  |  | HR566 (Lo-16bits)
568 | MEAS2:I''L1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
569 |  |  |  | HR568 (Lo-16bits)
570 | MEAS2:I''L1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
571 |  |  |  | HR570 (Lo-16bits)
572 | MEAS2:I''L1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
573 |  |  |  | HR572 (Lo-16bits)
574 | MEAS2:I''L1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
575 |  |  |  | HR574 (Lo-16bits)
576 | MEAS2:I''L2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
577 |  |  |  | HR576 (Lo-16bits)
578 | MEAS2:I''L2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
579 |  |  |  | HR578 (Lo-16bits)
580 | MEAS2:I''L2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
581 |  |  |  | HR580 (Lo-16bits)
582 | MEAS2:I''L2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
583 |  |  |  | HR582 (Lo-16bits)
584 | MEAS2:I''L2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
585 |  |  |  | HR584 (Lo-16bits)
586 | MEAS2:I''L2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
587 |  |  |  | HR586 (Lo-16bits)
588 | MEAS2:I''L2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
589 |  |  |  | HR588 (Lo-16bits)
590 | MEAS2:I''L2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
591 |  |  |  | HR590 (Lo-16bits)
592 | MEAS2:I''L2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
593 |  |  |  | HR592 (Lo-16bits)
594 | MEAS2:I''L2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
595 |  |  |  | HR594 (Lo-16bits)
596 | MEAS2:I''L2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
597 |  |  |  | HR596 (Lo-16bits)
598 | MEAS2:I''L2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
599 |  |  |  | HR598 (Lo-16bits)
600 | MEAS2:I''L2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
601 |  |  |  | HR600 (Lo-16bits)
602 | MEAS2:I''L2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
603 |  |  |  | HR602 (Lo-16bits)
604 | MEAS2:I''L2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
605 |  |  |  | HR604 (Lo-16bits)
606 | MEAS2:I''L2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
607 |  |  |  | HR606 (Lo-16bits)
608 | MEAS2:I''L2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
609 |  |  |  | HR608 (Lo-16bits)
610 | MEAS2:I''L2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
611 |  |  |  | HR610 (Lo-16bits)
612 | MEAS2:I''L2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
613 |  |  |  | HR612 (Lo-16bits)
614 | MEAS2:I''L2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
615 |  |  |  | HR614 (Lo-16bits)
616 | MEAS2:I''L2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
617 |  |  |  | HR616 (Lo-16bits)
618 | MEAS2:I''L2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
619 |  |  |  | HR618 (Lo-16bits)
620 | MEAS2:I''L2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
621 |  |  |  | HR620 (Lo-16bits)
622 | MEAS2:I''L2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
623 |  |  |  | HR622 (Lo-16bits)
624 | MEAS2:I''L2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
625 |  |  |  | HR624 (Lo-16bits)
626 | MEAS2:I''L2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
627 |  |  |  | HR626 (Lo-16bits)
628 | MEAS2:I''L2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
629 |  |  |  | HR628 (Lo-16bits)
630 | MEAS2:I''L2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
631 |  |  |  | HR630 (Lo-16bits)
632 | MEAS2:I''L2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
633 |  |  |  | HR632 (Lo-16bits)
634 | MEAS2:I''L2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
635 |  |  |  | HR634 (Lo-16bits)
636 | MEAS2:I''L2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
637 |  |  |  | HR636 (Lo-16bits)
638 | MEAS2:I''L2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
639 |  |  |  | HR638 (Lo-16bits)
640 | MEAS2:I''L2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
641 |  |  |  | HR640 (Lo-16bits)
642 | MEAS2:I''L3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
643 |  |  |  | HR642 (Lo-16bits)
644 | MEAS2:I''L3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
645 |  |  |  | HR644 (Lo-16bits)
646 | MEAS2:I''L3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
647 |  |  |  | HR646 (Lo-16bits)
648 | MEAS2:I''L3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
649 |  |  |  | HR648 (Lo-16bits)
650 | MEAS2:I''L3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
651 |  |  |  | HR650 (Lo-16bits)
652 | MEAS2:I''L3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
653 |  |  |  | HR652 (Lo-16bits)
654 | MEAS2:I''L3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
655 |  |  |  | HR654 (Lo-16bits)
656 | MEAS2:I''L3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
657 |  |  |  | HR656 (Lo-16bits)
658 | MEAS2:I''L3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
659 |  |  |  | HR658 (Lo-16bits)
660 | MEAS2:I''L3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
661 |  |  |  | HR660 (Lo-16bits)
662 | MEAS2:I''L3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
663 |  |  |  | HR662 (Lo-16bits)
664 | MEAS2:I''L3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
665 |  |  |  | HR664 (Lo-16bits)
666 | MEAS2:I''L3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
667 |  |  |  | HR666 (Lo-16bits)
668 | MEAS2:I''L3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
669 |  |  |  | HR668 (Lo-16bits)
670 | MEAS2:I''L3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
671 |  |  |  | HR670 (Lo-16bits)
672 | MEAS2:I''L3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
673 |  |  |  | HR672 (Lo-16bits)
674 | MEAS2:I''L3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
675 |  |  |  | HR674 (Lo-16bits)
676 | MEAS2:I''L3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
677 |  |  |  | HR676 (Lo-16bits)
678 | MEAS2:I''L3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
679 |  |  |  | HR678 (Lo-16bits)
680 | MEAS2:I''L3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
681 |  |  |  | HR680 (Lo-16bits)
682 | MEAS2:I''L3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
683 |  |  |  | HR682 (Lo-16bits)
684 | MEAS2:I''L3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
685 |  |  |  | HR684 (Lo-16bits)
686 | MEAS2:I''L3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
687 |  |  |  | HR686 (Lo-16bits)
688 | MEAS2:I''L3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
689 |  |  |  | HR688 (Lo-16bits)
690 | MEAS2:I''L3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
691 |  |  |  | HR690 (Lo-16bits)
692 | MEAS2:I''L3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
693 |  |  |  | HR692 (Lo-16bits)
694 | MEAS2:I''L3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
695 |  |  |  | HR694 (Lo-16bits)
696 | MEAS2:I''L3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
697 |  |  |  | HR696 (Lo-16bits)
698 | MEAS2:I''L3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
699 |  |  |  | HR698 (Lo-16bits)
700 | MEAS2:I''L3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
701 |  |  |  | HR700 (Lo-16bits)
702 | MEAS2:I''L3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
703 |  |  |  | HR702 (Lo-16bits)
704 | MEAS2:I''L3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
705 |  |  |  | HR704 (Lo-16bits)
706 | MEAS2:I''L3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
707 |  |  |  | HR706 (Lo-16bits)
708 | MEAS2:I''01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
709 |  |  |  | HR708 (Lo-16bits)
710 | MEAS2:I''01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
711 |  |  |  | HR710 (Lo-16bits)
712 | MEAS2:I''01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
713 |  |  |  | HR712 (Lo-16bits)
714 | MEAS2:I''01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
715 |  |  |  | HR714 (Lo-16bits)
716 | MEAS2:I''01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
717 |  |  |  | HR716 (Lo-16bits)
718 | MEAS2:I''01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
719 |  |  |  | HR718 (Lo-16bits)
720 | MEAS2:I''01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
721 |  |  |  | HR720 (Lo-16bits)
722 | MEAS2:I''01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
723 |  |  |  | HR722 (Lo-16bits)
724 | MEAS2:I''01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
725 |  |  |  | HR724 (Lo-16bits)
726 | MEAS2:I''01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
727 |  |  |  | HR726 (Lo-16bits)
728 | MEAS2:I''01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
729 |  |  |  | HR728 (Lo-16bits)
730 | MEAS2:I''01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
731 |  |  |  | HR730 (Lo-16bits)
732 | MEAS2:I''01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
733 |  |  |  | HR732 (Lo-16bits)
734 | MEAS2:I''01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
735 |  |  |  | HR734 (Lo-16bits)
736 | MEAS2:I''01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
737 |  |  |  | HR736 (Lo-16bits)
738 | MEAS2:I''01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
739 |  |  |  | HR738 (Lo-16bits)
740 | MEAS2:I''01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
741 |  |  |  | HR740 (Lo-16bits)
742 | MEAS2:I''01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
743 |  |  |  | HR742 (Lo-16bits)
744 | MEAS2:I''01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
745 |  |  |  | HR744 (Lo-16bits)
746 | MEAS2:I''01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
747 |  |  |  | HR746 (Lo-16bits)
748 | MEAS2:I''01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
749 |  |  |  | HR748 (Lo-16bits)
750 | MEAS2:I''01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
751 |  |  |  | HR750 (Lo-16bits)
752 | MEAS2:I''01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
753 |  |  |  | HR752 (Lo-16bits)
754 | MEAS2:I''01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
755 |  |  |  | HR754 (Lo-16bits)
756 | MEAS2:I''01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
757 |  |  |  | HR756 (Lo-16bits)
758 | MEAS2:I''01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
759 |  |  |  | HR758 (Lo-16bits)
760 | MEAS2:I''01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
761 |  |  |  | HR760 (Lo-16bits)
762 | MEAS2:I''01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
763 |  |  |  | HR762 (Lo-16bits)
764 | MEAS2:I''01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
765 |  |  |  | HR764 (Lo-16bits)
766 | MEAS2:I''01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
767 |  |  |  | HR766 (Lo-16bits)
768 | MEAS2:I''01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
769 |  |  |  | HR768 (Lo-16bits)
770 | MEAS2:I''01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
771 |  |  |  | HR770 (Lo-16bits)
772 | MEAS2:I''01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
773 |  |  |  | HR772 (Lo-16bits)
774 | MEAS2:I''02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
775 |  |  |  | HR774 (Lo-16bits)
776 | MEAS2:I''02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
777 |  |  |  | HR776 (Lo-16bits)
778 | MEAS2:I''02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
779 |  |  |  | HR778 (Lo-16bits)
780 | MEAS2:I''02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
781 |  |  |  | HR780 (Lo-16bits)
782 | MEAS2:I''02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
783 |  |  |  | HR782 (Lo-16bits)
784 | MEAS2:I''02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
785 |  |  |  | HR784 (Lo-16bits)
786 | MEAS2:I''02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
787 |  |  |  | HR786 (Lo-16bits)
788 | MEAS2:I''02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
789 |  |  |  | HR788 (Lo-16bits)
790 | MEAS2:I''02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
791 |  |  |  | HR790 (Lo-16bits)
792 | MEAS2:I''02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
793 |  |  |  | HR792 (Lo-16bits)
794 | MEAS2:I''02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
795 |  |  |  | HR794 (Lo-16bits)
796 | MEAS2:I''02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
797 |  |  |  | HR796 (Lo-16bits)
798 | MEAS2:I''02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
799 |  |  |  | HR798 (Lo-16bits)
800 | MEAS2:I''02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
801 |  |  |  | HR800 (Lo-16bits)
802 | MEAS2:I''02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
803 |  |  |  | HR802 (Lo-16bits)
804 | MEAS2:I''02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
805 |  |  |  | HR804 (Lo-16bits)
806 | MEAS2:I''02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
807 |  |  |  | HR806 (Lo-16bits)
808 | MEAS2:I''02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
809 |  |  |  | HR808 (Lo-16bits)
810 | MEAS2:I''02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
811 |  |  |  | HR810 (Lo-16bits)
812 | MEAS2:I''02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
813 |  |  |  | HR812 (Lo-16bits)
814 | MEAS2:I''02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
815 |  |  |  | HR814 (Lo-16bits)
816 | MEAS2:I''02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
817 |  |  |  | HR816 (Lo-16bits)
818 | MEAS2:I''02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
819 |  |  |  | HR818 (Lo-16bits)
820 | MEAS2:I''02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
821 |  |  |  | HR820 (Lo-16bits)
822 | MEAS2:I''02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
823 |  |  |  | HR822 (Lo-16bits)
824 | MEAS2:I''02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
825 |  |  |  | HR824 (Lo-16bits)
826 | MEAS2:I''02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
827 |  |  |  | HR826 (Lo-16bits)
828 | MEAS2:I''02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
829 |  |  |  | HR828 (Lo-16bits)
830 | MEAS2:I''02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
831 |  |  |  | HR830 (Lo-16bits)
832 | MEAS2:I''02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
833 |  |  |  | HR832 (Lo-16bits)
834 | MEAS2:I''02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
835 |  |  |  | HR834 (Lo-16bits)
836 | MEAS2:I''02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
837 |  |  |  | HR836 (Lo-16bits)
838 | MEAS2:I''02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
839 |  |  |  | HR838 (Lo-16bits)
840 | MEAS2:MEAS2 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
841 |  |  |  | HR840 (Lo-16bits)
842 | MEAS3:U1Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
843 |  |  |  | HR842 (Lo-16bits)
844 | MEAS3:U1Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
845 |  |  |  | HR844 (Lo-16bits)
846 | MEAS3:U2Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
847 |  |  |  | HR846 (Lo-16bits)
848 | MEAS3:U2Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
849 |  |  |  | HR848 (Lo-16bits)
850 | MEAS3:U3Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
851 |  |  |  | HR850 (Lo-16bits)
852 | MEAS3:U3Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
853 |  |  |  | HR852 (Lo-16bits)
854 | MEAS3:U4Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
855 |  |  |  | HR854 (Lo-16bits)
856 | MEAS3:U4Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
857 |  |  |  | HR856 (Lo-16bits)
858 | MEAS3:U1Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
859 |  |  |  | HR858 (Lo-16bits)
860 | MEAS3:U1Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
861 |  |  |  | HR860 (Lo-16bits)
862 | MEAS3:U2Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
863 |  |  |  | HR862 (Lo-16bits)
864 | MEAS3:U2Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
865 |  |  |  | HR864 (Lo-16bits)
866 | MEAS3:U3Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
867 |  |  |  | HR866 (Lo-16bits)
868 | MEAS3:U3Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
869 |  |  |  | HR868 (Lo-16bits)
870 | MEAS3:U4Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
871 |  |  |  | HR870 (Lo-16bits)
872 | MEAS3:U4Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
873 |  |  |  | HR872 (Lo-16bits)
874 | MEAS3:Pos.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
875 |  |  |  | HR874 (Lo-16bits)
876 | MEAS3:Pos.seq.Volt.sec | R | 2 | FLOAT [0...480] (Hi-16bits)
877 |  |  |  | HR876 (Lo-16bits)
878 | MEAS3:Neg.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
879 |  |  |  | HR878 (Lo-16bits)
880 | MEAS3:Neg.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
881 |  |  |  | HR880 (Lo-16bits)
882 | MEAS3:Zero.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
883 |  |  |  | HR882 (Lo-16bits)
884 | MEAS3:Zero.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
885 |  |  |  | HR884 (Lo-16bits)
886 | MEAS3:U0 Calc. pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
887 |  |  |  | HR886 (Lo-16bits)
888 | MEAS3:U0 Calc.Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
889 |  |  |  | HR888 (Lo-16bits)
890 | MEAS3:U1 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
891 |  |  |  | HR890 (Lo-16bits)
892 | MEAS3:U2 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
893 |  |  |  | HR892 (Lo-16bits)
894 | MEAS3:U3 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
895 |  |  |  | HR894 (Lo-16bits)
896 | MEAS3:U4 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
897 |  |  |  | HR896 (Lo-16bits)
898 | MEAS3:Pos.Seq volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
899 |  |  |  | HR898 (Lo-16bits)
900 | MEAS3:Neg.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
901 |  |  |  | HR900 (Lo-16bits)
902 | MEAS3:Zero.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
903 |  |  |  | HR902 (Lo-16bits)
904 | MEAS3:System volt UL12 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
905 |  |  |  | HR904 (Lo-16bits)
906 | MEAS3:System volt UL12 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
907 |  |  |  | HR906 (Lo-16bits)
908 | MEAS3:System volt UL12 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
909 |  |  |  | HR908 (Lo-16bits)
910 | MEAS3:System volt UL23 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
911 |  |  |  | HR910 (Lo-16bits)
912 | MEAS3:System volt UL23 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
913 |  |  |  | HR912 (Lo-16bits)
914 | MEAS3:System volt UL23 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
915 |  |  |  | HR914 (Lo-16bits)
916 | MEAS3:System volt UL31 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
917 |  |  |  | HR916 (Lo-16bits)
918 | MEAS3:System volt UL31 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
919 |  |  |  | HR918 (Lo-16bits)
920 | MEAS3:System volt UL31 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
921 |  |  |  | HR920 (Lo-16bits)
922 | MEAS3:System volt UL1 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
923 |  |  |  | HR922 (Lo-16bits)
924 | MEAS3:System volt UL1 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
925 |  |  |  | HR924 (Lo-16bits)
926 | MEAS3:System volt UL1 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
927 |  |  |  | HR926 (Lo-16bits)
928 | MEAS3:System volt UL2 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
929 |  |  |  | HR928 (Lo-16bits)
930 | MEAS3:System volt UL2 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
931 |  |  |  | HR930 (Lo-16bits)
932 | MEAS3:System volt UL2 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
933 |  |  |  | HR932 (Lo-16bits)
934 | MEAS3:System volt UL3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
935 |  |  |  | HR934 (Lo-16bits)
936 | MEAS3:System volt UL3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
937 |  |  |  | HR936 (Lo-16bits)
938 | MEAS3:System volt UL3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
939 |  |  |  | HR938 (Lo-16bits)
940 | MEAS3:System volt U0 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
941 |  |  |  | HR940 (Lo-16bits)
942 | MEAS3:System volt U0 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
943 |  |  |  | HR942 (Lo-16bits)
944 | MEAS3:System volt U0 mag(%) | R | 2 | FLOAT [0...120] (Hi-16bits)
945 |  |  |  | HR944 (Lo-16bits)
946 | MEAS3:System volt U0 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
947 |  |  |  | HR946 (Lo-16bits)
948 | MEAS3:System volt U3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
949 |  |  |  | HR948 (Lo-16bits)
950 | MEAS3:System volt U3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
951 |  |  |  | HR950 (Lo-16bits)
952 | MEAS3:System volt U3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
953 |  |  |  | HR952 (Lo-16bits)
954 | MEAS3:System volt U4 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
955 |  |  |  | HR954 (Lo-16bits)
956 | MEAS3:System volt U4 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
957 |  |  |  | HR956 (Lo-16bits)
958 | MEAS3:System volt U4 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
959 |  |  |  | HR958 (Lo-16bits)
960 | MEAS3:System volt UL1 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
961 |  |  |  | HR960 (Lo-16bits)
962 | MEAS3:System volt UL2 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
963 |  |  |  | HR962 (Lo-16bits)
964 | MEAS3:System volt UL3 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
965 |  |  |  | HR964 (Lo-16bits)
966 | MEAS3:UL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
967 |  |  |  | HR966 (Lo-16bits)
968 | MEAS3:UL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
969 |  |  |  | HR968 (Lo-16bits)
970 | MEAS3:UL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
971 |  |  |  | HR970 (Lo-16bits)
972 | MEAS3:UL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
973 |  |  |  | HR972 (Lo-16bits)
974 | MEAS3:UL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
975 |  |  |  | HR974 (Lo-16bits)
976 | MEAS3:UL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
977 |  |  |  | HR976 (Lo-16bits)
978 | MEAS3:U1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
979 |  |  |  | HR978 (Lo-16bits)
980 | MEAS3:U1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
981 |  |  |  | HR980 (Lo-16bits)
982 | MEAS3:U1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
983 |  |  |  | HR982 (Lo-16bits)
984 | MEAS3:U1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
985 |  |  |  | HR984 (Lo-16bits)
986 | MEAS3:U1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
987 |  |  |  | HR986 (Lo-16bits)
988 | MEAS3:U1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
989 |  |  |  | HR988 (Lo-16bits)
990 | MEAS3:U1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
991 |  |  |  | HR990 (Lo-16bits)
992 | MEAS3:U1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
993 |  |  |  | HR992 (Lo-16bits)
994 | MEAS3:U1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
995 |  |  |  | HR994 (Lo-16bits)
996 | MEAS3:U1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
997 |  |  |  | HR996 (Lo-16bits)
998 | MEAS3:U1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
999 |  |  |  | HR998 (Lo-16bits)
1000 | MEAS3:U1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1001 |  |  |  | HR1000 (Lo-16bits)
1002 | MEAS3:U1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1003 |  |  |  | HR1002 (Lo-16bits)
1004 | MEAS3:U1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1005 |  |  |  | HR1004 (Lo-16bits)
1006 | MEAS3:U1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1007 |  |  |  | HR1006 (Lo-16bits)
1008 | MEAS3:U1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1009 |  |  |  | HR1008 (Lo-16bits)
1010 | MEAS3:U1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1011 |  |  |  | HR1010 (Lo-16bits)
1012 | MEAS3:U1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1013 |  |  |  | HR1012 (Lo-16bits)
1014 | MEAS3:U1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1015 |  |  |  | HR1014 (Lo-16bits)
1016 | MEAS3:U1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1017 |  |  |  | HR1016 (Lo-16bits)
1018 | MEAS3:U1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1019 |  |  |  | HR1018 (Lo-16bits)
1020 | MEAS3:U1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1021 |  |  |  | HR1020 (Lo-16bits)
1022 | MEAS3:U1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1023 |  |  |  | HR1022 (Lo-16bits)
1024 | MEAS3:U1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1025 |  |  |  | HR1024 (Lo-16bits)
1026 | MEAS3:U1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1027 |  |  |  | HR1026 (Lo-16bits)
1028 | MEAS3:U1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1029 |  |  |  | HR1028 (Lo-16bits)
1030 | MEAS3:U1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1031 |  |  |  | HR1030 (Lo-16bits)
1032 | MEAS3:U1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1033 |  |  |  | HR1032 (Lo-16bits)
1034 | MEAS3:U1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1035 |  |  |  | HR1034 (Lo-16bits)
1036 | MEAS3:U1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1037 |  |  |  | HR1036 (Lo-16bits)
1038 | MEAS3:U1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1039 |  |  |  | HR1038 (Lo-16bits)
1040 | MEAS3:U2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1041 |  |  |  | HR1040 (Lo-16bits)
1042 | MEAS3:U2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1043 |  |  |  | HR1042 (Lo-16bits)
1044 | MEAS3:U2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1045 |  |  |  | HR1044 (Lo-16bits)
1046 | MEAS3:U2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1047 |  |  |  | HR1046 (Lo-16bits)
1048 | MEAS3:U2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1049 |  |  |  | HR1048 (Lo-16bits)
1050 | MEAS3:U2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1051 |  |  |  | HR1050 (Lo-16bits)
1052 | MEAS3:U2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1053 |  |  |  | HR1052 (Lo-16bits)
1054 | MEAS3:U2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1055 |  |  |  | HR1054 (Lo-16bits)
1056 | MEAS3:U2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1057 |  |  |  | HR1056 (Lo-16bits)
1058 | MEAS3:U2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1059 |  |  |  | HR1058 (Lo-16bits)
1060 | MEAS3:U2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1061 |  |  |  | HR1060 (Lo-16bits)
1062 | MEAS3:U2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1063 |  |  |  | HR1062 (Lo-16bits)
1064 | MEAS3:U2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1065 |  |  |  | HR1064 (Lo-16bits)
1066 | MEAS3:U2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1067 |  |  |  | HR1066 (Lo-16bits)
1068 | MEAS3:U2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1069 |  |  |  | HR1068 (Lo-16bits)
1070 | MEAS3:U2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1071 |  |  |  | HR1070 (Lo-16bits)
1072 | MEAS3:U2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1073 |  |  |  | HR1072 (Lo-16bits)
1074 | MEAS3:U2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1075 |  |  |  | HR1074 (Lo-16bits)
1076 | MEAS3:U2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1077 |  |  |  | HR1076 (Lo-16bits)
1078 | MEAS3:U2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1079 |  |  |  | HR1078 (Lo-16bits)
1080 | MEAS3:U2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1081 |  |  |  | HR1080 (Lo-16bits)
1082 | MEAS3:U2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1083 |  |  |  | HR1082 (Lo-16bits)
1084 | MEAS3:U2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1085 |  |  |  | HR1084 (Lo-16bits)
1086 | MEAS3:U2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1087 |  |  |  | HR1086 (Lo-16bits)
1088 | MEAS3:U2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1089 |  |  |  | HR1088 (Lo-16bits)
1090 | MEAS3:U2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1091 |  |  |  | HR1090 (Lo-16bits)
1092 | MEAS3:U2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1093 |  |  |  | HR1092 (Lo-16bits)
1094 | MEAS3:U2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1095 |  |  |  | HR1094 (Lo-16bits)
1096 | MEAS3:U2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1097 |  |  |  | HR1096 (Lo-16bits)
1098 | MEAS3:U2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1099 |  |  |  | HR1098 (Lo-16bits)
1100 | MEAS3:U2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1101 |  |  |  | HR1100 (Lo-16bits)
1102 | MEAS3:U3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1103 |  |  |  | HR1102 (Lo-16bits)
1104 | MEAS3:U3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1105 |  |  |  | HR1104 (Lo-16bits)
1106 | MEAS3:U3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1107 |  |  |  | HR1106 (Lo-16bits)
1108 | MEAS3:U3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1109 |  |  |  | HR1108 (Lo-16bits)
1110 | MEAS3:U3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1111 |  |  |  | HR1110 (Lo-16bits)
1112 | MEAS3:U3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1113 |  |  |  | HR1112 (Lo-16bits)
1114 | MEAS3:U3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1115 |  |  |  | HR1114 (Lo-16bits)
1116 | MEAS3:U3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1117 |  |  |  | HR1116 (Lo-16bits)
1118 | MEAS3:U3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1119 |  |  |  | HR1118 (Lo-16bits)
1120 | MEAS3:U3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1121 |  |  |  | HR1120 (Lo-16bits)
1122 | MEAS3:U3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1123 |  |  |  | HR1122 (Lo-16bits)
1124 | MEAS3:U3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1125 |  |  |  | HR1124 (Lo-16bits)
1126 | MEAS3:U3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1127 |  |  |  | HR1126 (Lo-16bits)
1128 | MEAS3:U3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1129 |  |  |  | HR1128 (Lo-16bits)
1130 | MEAS3:U3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1131 |  |  |  | HR1130 (Lo-16bits)
1132 | MEAS3:U3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1133 |  |  |  | HR1132 (Lo-16bits)
1134 | MEAS3:U3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1135 |  |  |  | HR1134 (Lo-16bits)
1136 | MEAS3:U3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1137 |  |  |  | HR1136 (Lo-16bits)
1138 | MEAS3:U3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1139 |  |  |  | HR1138 (Lo-16bits)
1140 | MEAS3:U3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1141 |  |  |  | HR1140 (Lo-16bits)
1142 | MEAS3:U3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1143 |  |  |  | HR1142 (Lo-16bits)
1144 | MEAS3:U3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1145 |  |  |  | HR1144 (Lo-16bits)
1146 | MEAS3:U3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1147 |  |  |  | HR1146 (Lo-16bits)
1148 | MEAS3:U3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1149 |  |  |  | HR1148 (Lo-16bits)
1150 | MEAS3:U3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1151 |  |  |  | HR1150 (Lo-16bits)
1152 | MEAS3:U3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1153 |  |  |  | HR1152 (Lo-16bits)
1154 | MEAS3:U3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1155 |  |  |  | HR1154 (Lo-16bits)
1156 | MEAS3:U3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1157 |  |  |  | HR1156 (Lo-16bits)
1158 | MEAS3:U3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1159 |  |  |  | HR1158 (Lo-16bits)
1160 | MEAS3:U3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1161 |  |  |  | HR1160 (Lo-16bits)
1162 | MEAS3:U3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1163 |  |  |  | HR1162 (Lo-16bits)
1164 | MEAS3:U4 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1165 |  |  |  | HR1164 (Lo-16bits)
1166 | MEAS3:U4 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1167 |  |  |  | HR1166 (Lo-16bits)
1168 | MEAS3:U4 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1169 |  |  |  | HR1168 (Lo-16bits)
1170 | MEAS3:U4 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1171 |  |  |  | HR1170 (Lo-16bits)
1172 | MEAS3:U4 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1173 |  |  |  | HR1172 (Lo-16bits)
1174 | MEAS3:U4 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1175 |  |  |  | HR1174 (Lo-16bits)
1176 | MEAS3:U4 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1177 |  |  |  | HR1176 (Lo-16bits)
1178 | MEAS3:U4 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1179 |  |  |  | HR1178 (Lo-16bits)
1180 | MEAS3:U4 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1181 |  |  |  | HR1180 (Lo-16bits)
1182 | MEAS3:U4 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1183 |  |  |  | HR1182 (Lo-16bits)
1184 | MEAS3:U4 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1185 |  |  |  | HR1184 (Lo-16bits)
1186 | MEAS3:U4 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1187 |  |  |  | HR1186 (Lo-16bits)
1188 | MEAS3:U4 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1189 |  |  |  | HR1188 (Lo-16bits)
1190 | MEAS3:U4 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1191 |  |  |  | HR1190 (Lo-16bits)
1192 | MEAS3:U4 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1193 |  |  |  | HR1192 (Lo-16bits)
1194 | MEAS3:U4 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1195 |  |  |  | HR1194 (Lo-16bits)
1196 | MEAS3:U4 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1197 |  |  |  | HR1196 (Lo-16bits)
1198 | MEAS3:U4 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1199 |  |  |  | HR1198 (Lo-16bits)
1200 | MEAS3:U4 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1201 |  |  |  | HR1200 (Lo-16bits)
1202 | MEAS3:U4 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1203 |  |  |  | HR1202 (Lo-16bits)
1204 | MEAS3:U4 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1205 |  |  |  | HR1204 (Lo-16bits)
1206 | MEAS3:U4 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1207 |  |  |  | HR1206 (Lo-16bits)
1208 | MEAS3:U4 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1209 |  |  |  | HR1208 (Lo-16bits)
1210 | MEAS3:U4 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1211 |  |  |  | HR1210 (Lo-16bits)
1212 | MEAS3:U4 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1213 |  |  |  | HR1212 (Lo-16bits)
1214 | MEAS3:U4 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1215 |  |  |  | HR1214 (Lo-16bits)
1216 | MEAS3:U4 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1217 |  |  |  | HR1216 (Lo-16bits)
1218 | MEAS3:U4 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1219 |  |  |  | HR1218 (Lo-16bits)
1220 | MEAS3:U4 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1221 |  |  |  | HR1220 (Lo-16bits)
1222 | MEAS3:U4 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1223 |  |  |  | HR1222 (Lo-16bits)
1224 | MEAS3:U4 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1225 |  |  |  | HR1224 (Lo-16bits)
1226 | IMERX:IL1 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1227 |  |  |  | HR1226 (Lo-16bits)
1228 | IMERX:IL1 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1229 |  |  |  | HR1228 (Lo-16bits)
1230 | IMERX:IL2 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1231 |  |  |  | HR1230 (Lo-16bits)
1232 | IMERX:IL2 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1233 |  |  |  | HR1232 (Lo-16bits)
1234 | IMERX:IL3 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1235 |  |  |  | HR1234 (Lo-16bits)
1236 | IMERX:IL3 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1237 |  |  |  | HR1236 (Lo-16bits)
1238 | IMERX:Pos.seq. Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1239 |  |  |  | HR1238 (Lo-16bits)
1240 | IMERX:Pos.Seq. Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1241 |  |  |  | HR1240 (Lo-16bits)
1242 | IMERX:I01 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1243 |  |  |  | HR1242 (Lo-16bits)
1244 | IMERX:I01 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1245 |  |  |  | HR1244 (Lo-16bits)
1246 | IMERX:I02 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1247 |  |  |  | HR1246 (Lo-16bits)
1248 | IMERX:I02 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1249 |  |  |  | HR1248 (Lo-16bits)
1250 | IMERX:I01 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1251 |  |  |  | HR1250 (Lo-16bits)
1252 | IMERX:I01 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1253 |  |  |  | HR1252 (Lo-16bits)
1254 | IMERX:I02 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1255 |  |  |  | HR1254 (Lo-16bits)
1256 | IMERX:I02 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1257 |  |  |  | HR1256 (Lo-16bits)
1258 | POW1:Export Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1259 |  |  |  | HR1258 (Lo-16bits)
1260 | POW1:Export Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1261 |  |  |  | HR1260 (Lo-16bits)
1262 | POW1:Import Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1263 |  |  |  | HR1262 (Lo-16bits)
1264 | POW1:Import Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1265 |  |  |  | HR1264 (Lo-16bits)
1266 | POW1:Active Energy (P) Export/Import balance MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1267 |  |  |  | HR1266 (Lo-16bits)
1268 | POW1:Active Energy (P) Export/Import balance kWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1269 |  |  |  | HR1268 (Lo-16bits)
1270 | POW1:Exported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1271 |  |  |  | HR1270 (Lo-16bits)
1272 | POW1:Exported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1273 |  |  |  | HR1272 (Lo-16bits)
1274 | POW1:Imported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1275 |  |  |  | HR1274 (Lo-16bits)
1276 | POW1:Imported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1277 |  |  |  | HR1276 (Lo-16bits)
1278 | POW1:Reactive Energy (Q) balance while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1279 |  |  |  | HR1278 (Lo-16bits)
1280 | POW1:Reactive Energy (Q) balance while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1281 |  |  |  | HR1280 (Lo-16bits)
1282 | POW1:Exported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1283 |  |  |  | HR1282 (Lo-16bits)
1284 | POW1:Exported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1285 |  |  |  | HR1284 (Lo-16bits)
1286 | POW1:Imported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1287 |  |  |  | HR1286 (Lo-16bits)
1288 | POW1:Imported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1289 |  |  |  | HR1288 (Lo-16bits)
1290 | POW1:Reactive Energy (Q) balance while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1291 |  |  |  | HR1290 (Lo-16bits)
1292 | POW1:Reactive Energy (Q) balance while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1293 |  |  |  | HR1292 (Lo-16bits)
1294 | POW1:Apparent Energy (S) while Export (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1295 |  |  |  | HR1294 (Lo-16bits)
1296 | POW1:Apparent Energy (S) while Export (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1297 |  |  |  | HR1296 (Lo-16bits)
1298 | POW1:Apparent Energy (S) while Import (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1299 |  |  |  | HR1298 (Lo-16bits)
1300 | POW1:Apparent Energy (S) while Import (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1301 |  |  |  | HR1300 (Lo-16bits)
1302 | POW1:Apparent Energy (S) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1303 |  |  |  | HR1302 (Lo-16bits)
1304 | POW1:Real Energy (P) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1305 |  |  |  | HR1304 (Lo-16bits)
1306 | POW1:Reactive Energy (Q) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1307 |  |  |  | HR1306 (Lo-16bits)
1308 | POW1:Real Energy (P) Supply (Default supply direction towards busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1309 |  |  |  | HR1308 (Lo-16bits)
1310 | POW1:Reactive Energy (Q) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1311 |  |  |  | HR1310 (Lo-16bits)
1312 | POW1:Real Energy (P) Demand (Default demand direction from busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1313 |  |  |  | HR1312 (Lo-16bits)
1314 | POW1:Reactive Energy (Q) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1315 |  |  |  | HR1314 (Lo-16bits)
1316 | POW1:Reset 3ph Energies | RW | 1 | 0=-;1=Reset
1317 | POW1:POW1 3PH Apparent power (S) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1318 |  |  |  | HR1317 (Lo-16bits)
1319 | POW1:POW1 3PH Apparent power (S MVA) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1320 |  |  |  | HR1319 (Lo-16bits)
1321 | POW1:POW1 3PH Active power (P) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1322 |  |  |  | HR1321 (Lo-16bits)
1323 | POW1:POW1 3PH Active power (P MW) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1324 |  |  |  | HR1323 (Lo-16bits)
1325 | POW1:POW1 3PH Reactive power (Q) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1326 |  |  |  | HR1325 (Lo-16bits)
1327 | POW1:POW1 3PH Reactive power (QMVar) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1328 |  |  |  | HR1327 (Lo-16bits)
1329 | POW1:POW1 3PH Tan(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1330 |  |  |  | HR1329 (Lo-16bits)
1331 | POW1:POW1 3PH Cos(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1332 |  |  |  | HR1331 (Lo-16bits)
1333 | POW1:3PH PF | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1334 |  |  |  | HR1333 (Lo-16bits)
1335 | ASC1:Curve1 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1336 |  |  |  | HR1335 (Lo-16bits)
1337 | ASC1:Curve1 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1338 |  |  |  | HR1337 (Lo-16bits)
1339 | ASC1:Curve2 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1340 |  |  |  | HR1339 (Lo-16bits)
1341 | ASC1:Curve2 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1342 |  |  |  | HR1341 (Lo-16bits)
1343 | ASC1:Curve3 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1344 |  |  |  | HR1343 (Lo-16bits)
1345 | ASC1:Curve3 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1346 |  |  |  | HR1345 (Lo-16bits)
1347 | ASC1:Curve4 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1348 |  |  |  | HR1347 (Lo-16bits)
1349 | ASC1:Curve4 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1350 |  |  |  | HR1349 (Lo-16bits)
1351 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1352 |  |  |  | HR1351 (Lo-16bits)
1353 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1354 |  |  |  | HR1353 (Lo-16bits)
1355 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1356 |  |  |  | HR1355 (Lo-16bits)
1357 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1358 |  |  |  | HR1357 (Lo-16bits)
1359 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1360 |  |  |  | HR1359 (Lo-16bits)
1361 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1362 |  |  |  | HR1361 (Lo-16bits)
1363 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1364 |  |  |  | HR1363 (Lo-16bits)
1365 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1366 |  |  |  | HR1365 (Lo-16bits)
1367 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1368 |  |  |  | HR1367 (Lo-16bits)
1369 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1370 |  |  |  | HR1369 (Lo-16bits)
1371 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1372 |  |  |  | HR1371 (Lo-16bits)
1373 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1374 |  |  |  | HR1373 (Lo-16bits)
1375 | M1CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1376 |  |  |  | HR1375 (Lo-16bits)
1377 | M1CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1378 |  |  |  | HR1377 (Lo-16bits)
1379 | M1CT2:I01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1380 |  |  |  | HR1379 (Lo-16bits)
1381 | M1CT2:I01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1382 |  |  |  | HR1381 (Lo-16bits)
1383 | M1CT3:I02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1384 |  |  |  | HR1383 (Lo-16bits)
1385 | M1CT3:I02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1386 |  |  |  | HR1385 (Lo-16bits)
1387 | M2CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1388 |  |  |  | HR1387 (Lo-16bits)
1389 | M2CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1390 |  |  |  | HR1389 (Lo-16bits)
1391 | M2CT2:I''01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1392 |  |  |  | HR1391 (Lo-16bits)
1393 | M2CT2:I''01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1394 |  |  |  | HR1393 (Lo-16bits)
1395 | M2CT3:I''02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1396 |  |  |  | HR1395 (Lo-16bits)
1397 | M2CT3:I''02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1398 |  |  |  | HR1397 (Lo-16bits)
1399 | M1VT1:VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1400 |  |  |  | HR1399 (Lo-16bits)
1401 | M1VT1:VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1402 |  |  |  | HR1401 (Lo-16bits)
1403 | M1VT1:U3 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1404 |  |  |  | HR1403 (Lo-16bits)
1405 | M1VT1:U3 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1406 |  |  |  | HR1405 (Lo-16bits)
1407 | M1VT1:U4 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1408 |  |  |  | HR1407 (Lo-16bits)
1409 | M1VT1:U4 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1410 |  |  |  | HR1409 (Lo-16bits)
1411 | FREQS:f atm. Protections (when not measurable returns to nominal) | R | 2 | FLOAT [0...75] (Hi-16bits)
1412 |  |  |  | HR1411 (Lo-16bits)
1413 | FREQS:f atm. Display (when not measurable is 0Hz) | R | 2 | FLOAT [0...75] (Hi-16bits)
1414 |  |  |  | HR1413 (Lo-16bits)
1415 | FREQS:SS1.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1416 |  |  |  | HR1415 (Lo-16bits)
1417 | FREQS:SS2.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1418 |  |  |  | HR1417 (Lo-16bits)
1419 | DIGI:DIs (cpu) | R | 2 | 0b=DI1;1b=DI2;2b=DI3; (Hi-16bits)
1420 |  |  |  | HR1419 (Lo-16bits)
1421 | DIGI:DIs (input option 1) | R | 2 | 0b=DI4;1b=DI5;2b=DI6;3b=DI7;4b=DI8;5b=DI9;6b=DI10;7b=DI11 (Hi-16bits)
1422 |  |  |  | HR1421 (Lo-16bits)
1423 | DIGI:DIs (input option 2) | R | 2 | 0b=DI12;1b=DI13;2b=DI14;3b=DI15;4b=DI16;5b=DI17;6b=DI18;7b=DI19 (Hi-16bits)
1424 |  |  |  | HR1423 (Lo-16bits)
1425 | DIGI:DIs (input option 3) | R | 2 | 0b=DI20;1b=DI21;2b=DI22;3b=DI23;4b=DI24;5b=DI25;6b=DI26;7b=DI27 (Hi-16bits)
1426 |  |  |  | HR1425 (Lo-16bits)
1427 | DIGI:DIs (input option 4) | R | 2 | 0b=D28;1b=DI29;2b=DI30;3b=DI31;4b=DI32;5b=DI33;6b=DI34;7b=DI35 (Hi-16bits)
1428 |  |  |  | HR1427 (Lo-16bits)
1429 | DIGI:DIs (input option 5) | R | 2 | 0b=DI36;1b=DI37;2b=DI38;3b=DI39;4b=DI40;5b=DI41;6b=DI42;7b=DI43 (Hi-16bits)
1430 |  |  |  | HR1429 (Lo-16bits)
1431 | DIGI:DIs (input option 6) | R | 2 | 0b=DI44;1b=DI45;2b=DI46;3b=DI47;4b=DI48;5b=DI49;6b=DI50;7b=DI51 (Hi-16bits)
1432 |  |  |  | HR1431 (Lo-16bits)
1433 | DIGI:Dis 1-32 | R | 2 | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32 (Hi-16bits)
1434 |  |  |  | HR1433 (Lo-16bits)
1435 | DIGI:Dis 33-64 | R | 2 | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51 (Hi-16bits)
1436 |  |  |  | HR1435 (Lo-16bits)
1437 | DIGI:DI1 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1438 |  |  |  | HR1437 (Lo-16bits)
1439 | DIGI:DI1 Counter Clear | RW | 1 | 0=-;1=Clear
1440 | DIGI:DI2 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1441 |  |  |  | HR1440 (Lo-16bits)
1442 | DIGI:DI2 Counter Clear | RW | 1 | 0=-;1=Clear
1443 | DIGI:DI3 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1444 |  |  |  | HR1443 (Lo-16bits)
1445 | DIGI:DI3 Counter Clear | RW | 1 | 0=-;1=Clear
1446 | DIGI:DI4 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1447 |  |  |  | HR1446 (Lo-16bits)
1448 | DIGI:DI4 Counter Clear | RW | 1 | 0=-;1=Clear
1449 | DIGI:DI5 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1450 |  |  |  | HR1449 (Lo-16bits)
1451 | DIGI:DI5 Counter Clear | RW | 1 | 0=-;1=Clear
1452 | DIGI:DI6 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1453 |  |  |  | HR1452 (Lo-16bits)
1454 | DIGI:DI6 Counter Clear | RW | 1 | 0=-;1=Clear
1455 | DIGI:DI7 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1456 |  |  |  | HR1455 (Lo-16bits)
1457 | DIGI:DI7 Counter Clear | RW | 1 | 0=-;1=Clear
1458 | DIGI:DI8 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1459 |  |  |  | HR1458 (Lo-16bits)
1460 | DIGI:DI8 Counter Clear | RW | 1 | 0=-;1=Clear
1461 | DIGI:DI9 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1462 |  |  |  | HR1461 (Lo-16bits)
1463 | DIGI:DI9 Counter Clear | RW | 1 | 0=-;1=Clear
1464 | DIGI:DI10 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1465 |  |  |  | HR1464 (Lo-16bits)
1466 | DIGI:DI10 Counter Clear | RW | 1 | 0=-;1=Clear
1467 | DIGI:DI11 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1468 |  |  |  | HR1467 (Lo-16bits)
1469 | DIGI:DI11 Counter Clear | RW | 1 | 0=-;1=Clear
1470 | DIGI:DI12 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1471 |  |  |  | HR1470 (Lo-16bits)
1472 | DIGI:DI12 Counter Clear | RW | 1 | 0=-;1=Clear
1473 | DIGI:DI13 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1474 |  |  |  | HR1473 (Lo-16bits)
1475 | DIGI:DI13 Counter Clear | RW | 1 | 0=-;1=Clear
1476 | DIGI:DI14 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1477 |  |  |  | HR1476 (Lo-16bits)
1478 | DIGI:DI14 Counter Clear | RW | 1 | 0=-;1=Clear
1479 | DIGI:DI15 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1480 |  |  |  | HR1479 (Lo-16bits)
1481 | DIGI:DI15 Counter Clear | RW | 1 | 0=-;1=Clear
1482 | DIGI:DI16 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1483 |  |  |  | HR1482 (Lo-16bits)
1484 | DIGI:DI16 Counter Clear | RW | 1 | 0=-;1=Clear
1485 | DIGI:DI17 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1486 |  |  |  | HR1485 (Lo-16bits)
1487 | DIGI:DI17 Counter Clear | RW | 1 | 0=-;1=Clear
1488 | DIGI:DI18 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1489 |  |  |  | HR1488 (Lo-16bits)
1490 | DIGI:DI18 Counter Clear | RW | 1 | 0=-;1=Clear
1491 | DIGI:DI19 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1492 |  |  |  | HR1491 (Lo-16bits)
1493 | DIGI:DI19 Counter Clear | RW | 1 | 0=-;1=Clear
1494 | DIGI:DI20 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1495 |  |  |  | HR1494 (Lo-16bits)
1496 | DIGI:DI20 Counter Clear | RW | 1 | 0=-;1=Clear
1497 | DIGI:DI21 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1498 |  |  |  | HR1497 (Lo-16bits)
1499 | DIGI:DI21 Counter Clear | RW | 1 | 0=-;1=Clear
1500 | DIGI:DI22 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1501 |  |  |  | HR1500 (Lo-16bits)
1502 | DIGI:DI22 Counter Clear | RW | 1 | 0=-;1=Clear
1503 | DIGI:DI23 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1504 |  |  |  | HR1503 (Lo-16bits)
1505 | DIGI:DI23 Counter Clear | RW | 1 | 0=-;1=Clear
1506 | DIGI:DI24 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1507 |  |  |  | HR1506 (Lo-16bits)
1508 | DIGI:DI24 Counter Clear | RW | 1 | 0=-;1=Clear
1509 | DIGI:DI25 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1510 |  |  |  | HR1509 (Lo-16bits)
1511 | DIGI:DI25 Counter Clear | RW | 1 | 0=-;1=Clear
1512 | DIGI:DI26 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1513 |  |  |  | HR1512 (Lo-16bits)
1514 | DIGI:DI26 Counter Clear | RW | 1 | 0=-;1=Clear
1515 | DIGI:DI27 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1516 |  |  |  | HR1515 (Lo-16bits)
1517 | DIGI:DI27 Counter Clear | RW | 1 | 0=-;1=Clear
1518 | DIGI:DI28 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1519 |  |  |  | HR1518 (Lo-16bits)
1520 | DIGI:DI28 Counter Clear | RW | 1 | 0=-;1=Clear
1521 | DIGI:DI29 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1522 |  |  |  | HR1521 (Lo-16bits)
1523 | DIGI:DI29 Counter Clear | RW | 1 | 0=-;1=Clear
1524 | DIGI:DI30 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1525 |  |  |  | HR1524 (Lo-16bits)
1526 | DIGI:DI30 Counter Clear | RW | 1 | 0=-;1=Clear
1527 | DIGI:DI31 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1528 |  |  |  | HR1527 (Lo-16bits)
1529 | DIGI:DI31 Counter Clear | RW | 1 | 0=-;1=Clear
1530 | DIGI:DI32 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1531 |  |  |  | HR1530 (Lo-16bits)
1532 | DIGI:DI32 Counter Clear | RW | 1 | 0=-;1=Clear
1533 | DIGI:DI33 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1534 |  |  |  | HR1533 (Lo-16bits)
1535 | DIGI:DI33 Counter Clear | RW | 1 | 0=-;1=Clear
1536 | DIGI:DI34 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1537 |  |  |  | HR1536 (Lo-16bits)
1538 | DIGI:DI34 Counter Clear | RW | 1 | 0=-;1=Clear
1539 | DIGI:DI35 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1540 |  |  |  | HR1539 (Lo-16bits)
1541 | DIGI:DI35 Counter Clear | RW | 1 | 0=-;1=Clear
1542 | DIGI:DI36 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1543 |  |  |  | HR1542 (Lo-16bits)
1544 | DIGI:DI36 Counter Clear | RW | 1 | 0=-;1=Clear
1545 | DIGI:DI37 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1546 |  |  |  | HR1545 (Lo-16bits)
1547 | DIGI:DI37 Counter Clear | RW | 1 | 0=-;1=Clear
1548 | DIGI:DI38 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1549 |  |  |  | HR1548 (Lo-16bits)
1550 | DIGI:DI38 Counter Clear | RW | 1 | 0=-;1=Clear
1551 | DIGI:DI39 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1552 |  |  |  | HR1551 (Lo-16bits)
1553 | DIGI:DI39 Counter Clear | RW | 1 | 0=-;1=Clear
1554 | DIGI:DI40 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1555 |  |  |  | HR1554 (Lo-16bits)
1556 | DIGI:DI40 Counter Clear | RW | 1 | 0=-;1=Clear
1557 | DIGI:DI41 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1558 |  |  |  | HR1557 (Lo-16bits)
1559 | DIGI:DI41 Counter Clear | RW | 1 | 0=-;1=Clear
1560 | DIGI:DI42 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1561 |  |  |  | HR1560 (Lo-16bits)
1562 | DIGI:DI42 Counter Clear | RW | 1 | 0=-;1=Clear
1563 | DIGI:DI43 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1564 |  |  |  | HR1563 (Lo-16bits)
1565 | DIGI:DI43 Counter Clear | RW | 1 | 0=-;1=Clear
1566 | DIGI:DI44 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1567 |  |  |  | HR1566 (Lo-16bits)
1568 | DIGI:DI44 Counter Clear | RW | 1 | 0=-;1=Clear
1569 | DIGI:DI45 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1570 |  |  |  | HR1569 (Lo-16bits)
1571 | DIGI:DI45 Counter Clear | RW | 1 | 0=-;1=Clear
1572 | DIGI:DI46 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1573 |  |  |  | HR1572 (Lo-16bits)
1574 | DIGI:DI46 Counter Clear | RW | 1 | 0=-;1=Clear
1575 | DIGI:DI47 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1576 |  |  |  | HR1575 (Lo-16bits)
1577 | DIGI:DI47 Counter Clear | RW | 1 | 0=-;1=Clear
1578 | DIGI:DI48 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1579 |  |  |  | HR1578 (Lo-16bits)
1580 | DIGI:DI48 Counter Clear | RW | 1 | 0=-;1=Clear
1581 | DIGI:DI49 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1582 |  |  |  | HR1581 (Lo-16bits)
1583 | DIGI:DI49 Counter Clear | RW | 1 | 0=-;1=Clear
1584 | DIGI:DI50 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1585 |  |  |  | HR1584 (Lo-16bits)
1586 | DIGI:DI50 Counter Clear | RW | 1 | 0=-;1=Clear
1587 | DIGI:DI51 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1588 |  |  |  | HR1587 (Lo-16bits)
1589 | DIGI:DI51 Counter Clear | RW | 1 | 0=-;1=Clear
1590 | RELE:Outputs status | R | 2 | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15 (Hi-16bits)
1591 |  |  |  | HR1590 (Lo-16bits)
1592 | SGS:Active setting group | R | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
1593 | SGS:Force SG | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1594 | SGS:Force SG change | RW | 1 | 0=Disabled;1=Enabled
1595 | SGS:Used setting groups | RW | 1 | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
1596 | SGS:Remote SG change | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1597 | CTRL:Local/Remote status | R | 1 | 0=Remote;1=Local
1598 | DEV:Serial number | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1599 |  |  |  | HR1598 (Lo-16bits)
1600 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1601 |  |  |  | HR1600 (Lo-16bits)
1602 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1603 |  |  |  | HR1602 (Lo-16bits)
1604 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1605 |  |  |  | HR1604 (Lo-16bits)
1606 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1607 |  |  |  | HR1606 (Lo-16bits)
1608 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1609 |  |  |  | HR1608 (Lo-16bits)
1610 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1611 |  |  |  | HR1610 (Lo-16bits)
1612 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1613 |  |  |  | HR1612 (Lo-16bits)
1614 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1615 |  |  |  | HR1614 (Lo-16bits)
1616 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1617 |  |  |  | HR1616 (Lo-16bits)
1618 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1619 |  |  |  | HR1618 (Lo-16bits)
1620 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1621 |  |  |  | HR1620 (Lo-16bits)
1622 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1623 |  |  |  | HR1622 (Lo-16bits)
1624 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1625 |  |  |  | HR1624 (Lo-16bits)
1626 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1627 |  |  |  | HR1626 (Lo-16bits)
1628 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1629 |  |  |  | HR1628 (Lo-16bits)
1630 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1631 |  |  |  | HR1630 (Lo-16bits)
1632 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1633 |  |  |  | HR1632 (Lo-16bits)
1634 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1635 |  |  |  | HR1634 (Lo-16bits)
1636 | DIAG:Configuration changed | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1637 |  |  |  | HR1636 (Lo-16bits)
1638 | MBTCP:Enable mapped setting value modification through Modbus | RW | 1 | 0=Disabled;1=Enabled
1639 | MBIO:MBIO ModA Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1640 |  |  |  | HR1639 (Lo-16bits)
1641 | MBIO:MBIO ModA Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1642 |  |  |  | HR1641 (Lo-16bits)
1643 | MBIO:MBIO ModA Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1644 |  |  |  | HR1643 (Lo-16bits)
1645 | MBIO:MBIO ModA Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1646 |  |  |  | HR1645 (Lo-16bits)
1647 | MBIO:MBIO ModA Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1648 |  |  |  | HR1647 (Lo-16bits)
1649 | MBIO:MBIO ModA Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1650 |  |  |  | HR1649 (Lo-16bits)
1651 | MBIO:MBIO ModA Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1652 |  |  |  | HR1651 (Lo-16bits)
1653 | MBIO:MBIO ModA Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1654 |  |  |  | HR1653 (Lo-16bits)
1655 | MBIO:MBIO ModB Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1656 |  |  |  | HR1655 (Lo-16bits)
1657 | MBIO:MBIO ModB Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1658 |  |  |  | HR1657 (Lo-16bits)
1659 | MBIO:MBIO ModB Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1660 |  |  |  | HR1659 (Lo-16bits)
1661 | MBIO:MBIO ModB Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1662 |  |  |  | HR1661 (Lo-16bits)
1663 | MBIO:MBIO ModB Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1664 |  |  |  | HR1663 (Lo-16bits)
1665 | MBIO:MBIO ModB Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1666 |  |  |  | HR1665 (Lo-16bits)
1667 | MBIO:MBIO ModB Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1668 |  |  |  | HR1667 (Lo-16bits)
1669 | MBIO:MBIO ModB Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1670 |  |  |  | HR1669 (Lo-16bits)
1671 | MBIO:MBIO ModC Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1672 |  |  |  | HR1671 (Lo-16bits)
1673 | MBIO:MBIO ModC Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1674 |  |  |  | HR1673 (Lo-16bits)
1675 | MBIO:MBIO ModC Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1676 |  |  |  | HR1675 (Lo-16bits)
1677 | MBIO:MBIO ModC Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1678 |  |  |  | HR1677 (Lo-16bits)
1679 | MBIO:MBIO ModC Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1680 |  |  |  | HR1679 (Lo-16bits)
1681 | MBIO:MBIO ModC Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1682 |  |  |  | HR1681 (Lo-16bits)
1683 | MBIO:MBIO ModC Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1684 |  |  |  | HR1683 (Lo-16bits)
1685 | MBIO:MBIO ModC Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1686 |  |  |  | HR1685 (Lo-16bits)
1687 | LOGIC:Reset Latches | RW | 1 | 0=-;1=Reset
1688 | LOGIC1:Logic out 1-32 | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
1689 |  |  |  | HR1688 (Lo-16bits)
1690 | NOC1:I> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1691 | NOC1:I> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1692 | NOC1:I> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1693 | NOC1:I> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1694 | NOC1:I> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1695 | NOC1:I> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1696 |  |  |  | HR1695 (Lo-16bits)
1697 | NOC1:I> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1698 |  |  |  | HR1697 (Lo-16bits)
1699 | NOC1:I> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1700 |  |  |  | HR1699 (Lo-16bits)
1701 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1702 |  |  |  | HR1701 (Lo-16bits)
1703 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1704 |  |  |  | HR1703 (Lo-16bits)
1705 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1706 |  |  |  | HR1705 (Lo-16bits)
1707 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1708 |  |  |  | HR1707 (Lo-16bits)
1709 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1710 |  |  |  | HR1709 (Lo-16bits)
1711 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1712 |  |  |  | HR1711 (Lo-16bits)
1713 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1714 |  |  |  | HR1713 (Lo-16bits)
1715 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1716 |  |  |  | HR1715 (Lo-16bits)
1717 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1718 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1719 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1720 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1721 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1722 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1723 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1724 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1725 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1726 |  |  |  | HR1725 (Lo-16bits)
1727 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1728 |  |  |  | HR1727 (Lo-16bits)
1729 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1730 |  |  |  | HR1729 (Lo-16bits)
1731 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1732 |  |  |  | HR1731 (Lo-16bits)
1733 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1734 |  |  |  | HR1733 (Lo-16bits)
1735 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1736 |  |  |  | HR1735 (Lo-16bits)
1737 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1738 |  |  |  | HR1737 (Lo-16bits)
1739 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1740 |  |  |  | HR1739 (Lo-16bits)
1741 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1742 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1743 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1744 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1745 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1746 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1747 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1748 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1749 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1750 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1751 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1752 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1753 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1754 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1755 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1756 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1757 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1758 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1759 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1760 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1761 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1762 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1763 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1764 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1765 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1766 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1767 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1768 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1769 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1770 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1771 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1772 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1773 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1774 |  |  |  | HR1773 (Lo-16bits)
1775 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1776 |  |  |  | HR1775 (Lo-16bits)
1777 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1778 |  |  |  | HR1777 (Lo-16bits)
1779 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1780 |  |  |  | HR1779 (Lo-16bits)
1781 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1782 |  |  |  | HR1781 (Lo-16bits)
1783 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1784 |  |  |  | HR1783 (Lo-16bits)
1785 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1786 |  |  |  | HR1785 (Lo-16bits)
1787 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1788 |  |  |  | HR1787 (Lo-16bits)
1789 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1790 |  |  |  | HR1789 (Lo-16bits)
1791 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1792 |  |  |  | HR1791 (Lo-16bits)
1793 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1794 |  |  |  | HR1793 (Lo-16bits)
1795 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1796 |  |  |  | HR1795 (Lo-16bits)
1797 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1798 |  |  |  | HR1797 (Lo-16bits)
1799 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1800 |  |  |  | HR1799 (Lo-16bits)
1801 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1802 |  |  |  | HR1801 (Lo-16bits)
1803 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1804 |  |  |  | HR1803 (Lo-16bits)
1805 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1806 |  |  |  | HR1805 (Lo-16bits)
1807 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1808 |  |  |  | HR1807 (Lo-16bits)
1809 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1810 |  |  |  | HR1809 (Lo-16bits)
1811 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1812 |  |  |  | HR1811 (Lo-16bits)
1813 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1814 |  |  |  | HR1813 (Lo-16bits)
1815 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1816 |  |  |  | HR1815 (Lo-16bits)
1817 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1818 |  |  |  | HR1817 (Lo-16bits)
1819 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1820 |  |  |  | HR1819 (Lo-16bits)
1821 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1822 |  |  |  | HR1821 (Lo-16bits)
1823 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1824 |  |  |  | HR1823 (Lo-16bits)
1825 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1826 |  |  |  | HR1825 (Lo-16bits)
1827 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1828 |  |  |  | HR1827 (Lo-16bits)
1829 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1830 |  |  |  | HR1829 (Lo-16bits)
1831 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1832 |  |  |  | HR1831 (Lo-16bits)
1833 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1834 |  |  |  | HR1833 (Lo-16bits)
1835 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1836 |  |  |  | HR1835 (Lo-16bits)
1837 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1838 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1839 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1840 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1841 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1842 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1843 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1844 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1845 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1846 |  |  |  | HR1845 (Lo-16bits)
1847 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1848 |  |  |  | HR1847 (Lo-16bits)
1849 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1850 |  |  |  | HR1849 (Lo-16bits)
1851 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1852 |  |  |  | HR1851 (Lo-16bits)
1853 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1854 |  |  |  | HR1853 (Lo-16bits)
1855 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1856 |  |  |  | HR1855 (Lo-16bits)
1857 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1858 |  |  |  | HR1857 (Lo-16bits)
1859 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1860 |  |  |  | HR1859 (Lo-16bits)
1861 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1862 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1863 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1864 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1865 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1866 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1867 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1868 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1869 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1870 |  |  |  | HR1869 (Lo-16bits)
1871 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1872 |  |  |  | HR1871 (Lo-16bits)
1873 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1874 |  |  |  | HR1873 (Lo-16bits)
1875 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1876 |  |  |  | HR1875 (Lo-16bits)
1877 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1878 |  |  |  | HR1877 (Lo-16bits)
1879 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1880 |  |  |  | HR1879 (Lo-16bits)
1881 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1882 |  |  |  | HR1881 (Lo-16bits)
1883 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1884 |  |  |  | HR1883 (Lo-16bits)
1885 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1886 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1887 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1888 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1889 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1890 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1891 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1892 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1893 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1894 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1895 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1896 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1897 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1898 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1899 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1900 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1901 | NOC1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
1902 |  |  |  | HR1901 (Lo-16bits)
1903 | NOC1:Delay type | RW | 1 | 0=DT;1=IDMT
1904 | NOC1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
1905 |  |  |  | HR1904 (Lo-16bits)
1906 | NOC1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
1907 | NOC1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1908 | NOC1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1909 | NOC1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
1910 | NOC1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
1911 |  |  |  | HR1910 (Lo-16bits)
1912 | NOC1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
1913 |  |  |  | HR1912 (Lo-16bits)
1914 | NOC1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
1915 |  |  |  | HR1914 (Lo-16bits)
1916 | NOC1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
1917 |  |  |  | HR1916 (Lo-16bits)
1918 | NOC1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
1919 | NOC1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
1920 | NOC2:I>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1921 | NOC2:I>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1922 | NOC2:I>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1923 | NOC2:I>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1924 | NOC2:I>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1925 | NOC2:I>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1926 |  |  |  | HR1925 (Lo-16bits)
1927 | NOC2:I>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1928 |  |  |  | HR1927 (Lo-16bits)
1929 | NOC2:I>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1930 |  |  |  | HR1929 (Lo-16bits)
1931 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1932 |  |  |  | HR1931 (Lo-16bits)
1933 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1934 |  |  |  | HR1933 (Lo-16bits)
1935 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1936 |  |  |  | HR1935 (Lo-16bits)
1937 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1938 |  |  |  | HR1937 (Lo-16bits)
1939 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1940 |  |  |  | HR1939 (Lo-16bits)
1941 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1942 |  |  |  | HR1941 (Lo-16bits)
1943 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1944 |  |  |  | HR1943 (Lo-16bits)
1945 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1946 |  |  |  | HR1945 (Lo-16bits)
1947 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1948 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1949 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1950 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1951 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1952 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1953 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1954 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1955 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1956 |  |  |  | HR1955 (Lo-16bits)
1957 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1958 |  |  |  | HR1957 (Lo-16bits)
1959 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1960 |  |  |  | HR1959 (Lo-16bits)
1961 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1962 |  |  |  | HR1961 (Lo-16bits)
1963 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1964 |  |  |  | HR1963 (Lo-16bits)
1965 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1966 |  |  |  | HR1965 (Lo-16bits)
1967 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1968 |  |  |  | HR1967 (Lo-16bits)
1969 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1970 |  |  |  | HR1969 (Lo-16bits)
1971 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1972 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1973 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1974 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1975 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1976 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1977 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1978 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1979 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1980 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1981 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1982 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1983 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1984 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1985 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1986 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1987 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1988 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1989 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1990 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1991 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1992 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1993 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1994 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1995 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1996 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1997 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1998 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1999 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2000 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2001 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2002 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2003 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2004 |  |  |  | HR2003 (Lo-16bits)
2005 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2006 |  |  |  | HR2005 (Lo-16bits)
2007 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2008 |  |  |  | HR2007 (Lo-16bits)
2009 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2010 |  |  |  | HR2009 (Lo-16bits)
2011 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2012 |  |  |  | HR2011 (Lo-16bits)
2013 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2014 |  |  |  | HR2013 (Lo-16bits)
2015 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2016 |  |  |  | HR2015 (Lo-16bits)
2017 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2018 |  |  |  | HR2017 (Lo-16bits)
2019 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2020 |  |  |  | HR2019 (Lo-16bits)
2021 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2022 |  |  |  | HR2021 (Lo-16bits)
2023 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2024 |  |  |  | HR2023 (Lo-16bits)
2025 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2026 |  |  |  | HR2025 (Lo-16bits)
2027 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2028 |  |  |  | HR2027 (Lo-16bits)
2029 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2030 |  |  |  | HR2029 (Lo-16bits)
2031 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2032 |  |  |  | HR2031 (Lo-16bits)
2033 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2034 |  |  |  | HR2033 (Lo-16bits)
2035 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2036 |  |  |  | HR2035 (Lo-16bits)
2037 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2038 |  |  |  | HR2037 (Lo-16bits)
2039 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2040 |  |  |  | HR2039 (Lo-16bits)
2041 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2042 |  |  |  | HR2041 (Lo-16bits)
2043 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2044 |  |  |  | HR2043 (Lo-16bits)
2045 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2046 |  |  |  | HR2045 (Lo-16bits)
2047 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2048 |  |  |  | HR2047 (Lo-16bits)
2049 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2050 |  |  |  | HR2049 (Lo-16bits)
2051 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2052 |  |  |  | HR2051 (Lo-16bits)
2053 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2054 |  |  |  | HR2053 (Lo-16bits)
2055 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2056 |  |  |  | HR2055 (Lo-16bits)
2057 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2058 |  |  |  | HR2057 (Lo-16bits)
2059 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2060 |  |  |  | HR2059 (Lo-16bits)
2061 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2062 |  |  |  | HR2061 (Lo-16bits)
2063 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2064 |  |  |  | HR2063 (Lo-16bits)
2065 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2066 |  |  |  | HR2065 (Lo-16bits)
2067 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2068 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2069 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2070 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2071 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2072 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2073 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2074 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2075 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2076 |  |  |  | HR2075 (Lo-16bits)
2077 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2078 |  |  |  | HR2077 (Lo-16bits)
2079 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2080 |  |  |  | HR2079 (Lo-16bits)
2081 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2082 |  |  |  | HR2081 (Lo-16bits)
2083 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2084 |  |  |  | HR2083 (Lo-16bits)
2085 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2086 |  |  |  | HR2085 (Lo-16bits)
2087 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2088 |  |  |  | HR2087 (Lo-16bits)
2089 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2090 |  |  |  | HR2089 (Lo-16bits)
2091 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2092 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2093 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2094 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2095 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2096 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2097 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2098 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2099 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2100 |  |  |  | HR2099 (Lo-16bits)
2101 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2102 |  |  |  | HR2101 (Lo-16bits)
2103 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2104 |  |  |  | HR2103 (Lo-16bits)
2105 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2106 |  |  |  | HR2105 (Lo-16bits)
2107 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2108 |  |  |  | HR2107 (Lo-16bits)
2109 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2110 |  |  |  | HR2109 (Lo-16bits)
2111 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2112 |  |  |  | HR2111 (Lo-16bits)
2113 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2114 |  |  |  | HR2113 (Lo-16bits)
2115 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2116 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2117 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2118 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2119 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2120 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2121 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2122 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2123 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2124 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2125 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2126 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2127 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2128 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2129 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2130 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2131 | NOC2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2132 |  |  |  | HR2131 (Lo-16bits)
2133 | NOC2:Delay type | RW | 1 | 0=DT;1=IDMT
2134 | NOC2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2135 |  |  |  | HR2134 (Lo-16bits)
2136 | NOC2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2137 | NOC2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2138 | NOC2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2139 | NOC2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2140 | NOC2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2141 |  |  |  | HR2140 (Lo-16bits)
2142 | NOC2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2143 |  |  |  | HR2142 (Lo-16bits)
2144 | NOC2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2145 |  |  |  | HR2144 (Lo-16bits)
2146 | NOC2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2147 |  |  |  | HR2146 (Lo-16bits)
2148 | NOC2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2149 | NOC2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2150 | NOC3:I>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2151 | NOC3:I>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2152 | NOC3:I>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2153 | NOC3:I>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2154 | NOC3:I>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2155 | NOC3:I>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2156 |  |  |  | HR2155 (Lo-16bits)
2157 | NOC3:I>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2158 |  |  |  | HR2157 (Lo-16bits)
2159 | NOC3:I>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2160 |  |  |  | HR2159 (Lo-16bits)
2161 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2162 |  |  |  | HR2161 (Lo-16bits)
2163 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2164 |  |  |  | HR2163 (Lo-16bits)
2165 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2166 |  |  |  | HR2165 (Lo-16bits)
2167 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2168 |  |  |  | HR2167 (Lo-16bits)
2169 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2170 |  |  |  | HR2169 (Lo-16bits)
2171 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2172 |  |  |  | HR2171 (Lo-16bits)
2173 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2174 |  |  |  | HR2173 (Lo-16bits)
2175 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2176 |  |  |  | HR2175 (Lo-16bits)
2177 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2178 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2179 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2180 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2181 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2182 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2183 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2184 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2185 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2186 |  |  |  | HR2185 (Lo-16bits)
2187 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2188 |  |  |  | HR2187 (Lo-16bits)
2189 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2190 |  |  |  | HR2189 (Lo-16bits)
2191 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2192 |  |  |  | HR2191 (Lo-16bits)
2193 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2194 |  |  |  | HR2193 (Lo-16bits)
2195 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2196 |  |  |  | HR2195 (Lo-16bits)
2197 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2198 |  |  |  | HR2197 (Lo-16bits)
2199 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2200 |  |  |  | HR2199 (Lo-16bits)
2201 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2202 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2203 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2204 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2205 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2206 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2207 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2208 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2209 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2210 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2211 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2212 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2213 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2214 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2215 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2216 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2217 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2218 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2219 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2220 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2221 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2222 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2223 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2224 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2225 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2226 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2227 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2228 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2229 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2230 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2231 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2232 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2233 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2234 |  |  |  | HR2233 (Lo-16bits)
2235 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2236 |  |  |  | HR2235 (Lo-16bits)
2237 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2238 |  |  |  | HR2237 (Lo-16bits)
2239 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2240 |  |  |  | HR2239 (Lo-16bits)
2241 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2242 |  |  |  | HR2241 (Lo-16bits)
2243 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2244 |  |  |  | HR2243 (Lo-16bits)
2245 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2246 |  |  |  | HR2245 (Lo-16bits)
2247 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2248 |  |  |  | HR2247 (Lo-16bits)
2249 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2250 |  |  |  | HR2249 (Lo-16bits)
2251 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2252 |  |  |  | HR2251 (Lo-16bits)
2253 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2254 |  |  |  | HR2253 (Lo-16bits)
2255 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2256 |  |  |  | HR2255 (Lo-16bits)
2257 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2258 |  |  |  | HR2257 (Lo-16bits)
2259 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2260 |  |  |  | HR2259 (Lo-16bits)
2261 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2262 |  |  |  | HR2261 (Lo-16bits)
2263 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2264 |  |  |  | HR2263 (Lo-16bits)
2265 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2266 |  |  |  | HR2265 (Lo-16bits)
2267 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2268 |  |  |  | HR2267 (Lo-16bits)
2269 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2270 |  |  |  | HR2269 (Lo-16bits)
2271 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2272 |  |  |  | HR2271 (Lo-16bits)
2273 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2274 |  |  |  | HR2273 (Lo-16bits)
2275 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2276 |  |  |  | HR2275 (Lo-16bits)
2277 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2278 |  |  |  | HR2277 (Lo-16bits)
2279 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2280 |  |  |  | HR2279 (Lo-16bits)
2281 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2282 |  |  |  | HR2281 (Lo-16bits)
2283 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2284 |  |  |  | HR2283 (Lo-16bits)
2285 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2286 |  |  |  | HR2285 (Lo-16bits)
2287 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2288 |  |  |  | HR2287 (Lo-16bits)
2289 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2290 |  |  |  | HR2289 (Lo-16bits)
2291 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2292 |  |  |  | HR2291 (Lo-16bits)
2293 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2294 |  |  |  | HR2293 (Lo-16bits)
2295 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2296 |  |  |  | HR2295 (Lo-16bits)
2297 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2298 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2299 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2300 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2301 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2302 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2303 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2304 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2305 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2306 |  |  |  | HR2305 (Lo-16bits)
2307 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2308 |  |  |  | HR2307 (Lo-16bits)
2309 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2310 |  |  |  | HR2309 (Lo-16bits)
2311 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2312 |  |  |  | HR2311 (Lo-16bits)
2313 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2314 |  |  |  | HR2313 (Lo-16bits)
2315 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2316 |  |  |  | HR2315 (Lo-16bits)
2317 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2318 |  |  |  | HR2317 (Lo-16bits)
2319 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2320 |  |  |  | HR2319 (Lo-16bits)
2321 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2322 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2323 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2324 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2325 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2326 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2327 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2328 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2329 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2330 |  |  |  | HR2329 (Lo-16bits)
2331 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2332 |  |  |  | HR2331 (Lo-16bits)
2333 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2334 |  |  |  | HR2333 (Lo-16bits)
2335 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2336 |  |  |  | HR2335 (Lo-16bits)
2337 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2338 |  |  |  | HR2337 (Lo-16bits)
2339 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2340 |  |  |  | HR2339 (Lo-16bits)
2341 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2342 |  |  |  | HR2341 (Lo-16bits)
2343 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2344 |  |  |  | HR2343 (Lo-16bits)
2345 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2346 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2347 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2348 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2349 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2350 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2351 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2352 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2353 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2354 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2355 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2356 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2357 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2358 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2359 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2360 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2361 | NOC3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2362 |  |  |  | HR2361 (Lo-16bits)
2363 | NOC3:Delay type | RW | 1 | 0=DT;1=IDMT
2364 | NOC3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2365 |  |  |  | HR2364 (Lo-16bits)
2366 | NOC3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2367 | NOC3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2368 | NOC3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2369 | NOC3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2370 | NOC3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2371 |  |  |  | HR2370 (Lo-16bits)
2372 | NOC3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2373 |  |  |  | HR2372 (Lo-16bits)
2374 | NOC3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2375 |  |  |  | HR2374 (Lo-16bits)
2376 | NOC3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2377 |  |  |  | HR2376 (Lo-16bits)
2378 | NOC3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2379 | NOC3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2380 | NOC4:I>>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2381 | NOC4:I>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2382 | NOC4:I>>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2383 | NOC4:I>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2384 | NOC4:I>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2385 | NOC4:I>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2386 |  |  |  | HR2385 (Lo-16bits)
2387 | NOC4:I>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2388 |  |  |  | HR2387 (Lo-16bits)
2389 | NOC4:I>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2390 |  |  |  | HR2389 (Lo-16bits)
2391 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2392 |  |  |  | HR2391 (Lo-16bits)
2393 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2394 |  |  |  | HR2393 (Lo-16bits)
2395 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2396 |  |  |  | HR2395 (Lo-16bits)
2397 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2398 |  |  |  | HR2397 (Lo-16bits)
2399 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2400 |  |  |  | HR2399 (Lo-16bits)
2401 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2402 |  |  |  | HR2401 (Lo-16bits)
2403 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2404 |  |  |  | HR2403 (Lo-16bits)
2405 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2406 |  |  |  | HR2405 (Lo-16bits)
2407 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2408 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2409 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2410 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2411 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2412 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2413 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2414 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2415 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2416 |  |  |  | HR2415 (Lo-16bits)
2417 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2418 |  |  |  | HR2417 (Lo-16bits)
2419 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2420 |  |  |  | HR2419 (Lo-16bits)
2421 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2422 |  |  |  | HR2421 (Lo-16bits)
2423 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2424 |  |  |  | HR2423 (Lo-16bits)
2425 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2426 |  |  |  | HR2425 (Lo-16bits)
2427 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2428 |  |  |  | HR2427 (Lo-16bits)
2429 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2430 |  |  |  | HR2429 (Lo-16bits)
2431 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2432 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2433 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2434 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2435 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2436 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2437 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2438 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2439 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2440 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2441 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2442 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2443 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2444 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2445 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2446 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2447 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2448 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2449 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2450 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2451 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2452 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2453 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2454 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2455 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2456 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2457 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2458 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2459 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2460 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2461 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2462 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2463 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2464 |  |  |  | HR2463 (Lo-16bits)
2465 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2466 |  |  |  | HR2465 (Lo-16bits)
2467 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2468 |  |  |  | HR2467 (Lo-16bits)
2469 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2470 |  |  |  | HR2469 (Lo-16bits)
2471 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2472 |  |  |  | HR2471 (Lo-16bits)
2473 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2474 |  |  |  | HR2473 (Lo-16bits)
2475 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2476 |  |  |  | HR2475 (Lo-16bits)
2477 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2478 |  |  |  | HR2477 (Lo-16bits)
2479 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2480 |  |  |  | HR2479 (Lo-16bits)
2481 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2482 |  |  |  | HR2481 (Lo-16bits)
2483 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2484 |  |  |  | HR2483 (Lo-16bits)
2485 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2486 |  |  |  | HR2485 (Lo-16bits)
2487 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2488 |  |  |  | HR2487 (Lo-16bits)
2489 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2490 |  |  |  | HR2489 (Lo-16bits)
2491 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2492 |  |  |  | HR2491 (Lo-16bits)
2493 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2494 |  |  |  | HR2493 (Lo-16bits)
2495 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2496 |  |  |  | HR2495 (Lo-16bits)
2497 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2498 |  |  |  | HR2497 (Lo-16bits)
2499 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2500 |  |  |  | HR2499 (Lo-16bits)
2501 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2502 |  |  |  | HR2501 (Lo-16bits)
2503 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2504 |  |  |  | HR2503 (Lo-16bits)
2505 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2506 |  |  |  | HR2505 (Lo-16bits)
2507 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2508 |  |  |  | HR2507 (Lo-16bits)
2509 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2510 |  |  |  | HR2509 (Lo-16bits)
2511 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2512 |  |  |  | HR2511 (Lo-16bits)
2513 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2514 |  |  |  | HR2513 (Lo-16bits)
2515 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2516 |  |  |  | HR2515 (Lo-16bits)
2517 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2518 |  |  |  | HR2517 (Lo-16bits)
2519 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2520 |  |  |  | HR2519 (Lo-16bits)
2521 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2522 |  |  |  | HR2521 (Lo-16bits)
2523 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2524 |  |  |  | HR2523 (Lo-16bits)
2525 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2526 |  |  |  | HR2525 (Lo-16bits)
2527 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2528 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2529 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2530 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2531 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2532 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2533 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2534 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2535 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2536 |  |  |  | HR2535 (Lo-16bits)
2537 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2538 |  |  |  | HR2537 (Lo-16bits)
2539 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2540 |  |  |  | HR2539 (Lo-16bits)
2541 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2542 |  |  |  | HR2541 (Lo-16bits)
2543 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2544 |  |  |  | HR2543 (Lo-16bits)
2545 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2546 |  |  |  | HR2545 (Lo-16bits)
2547 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2548 |  |  |  | HR2547 (Lo-16bits)
2549 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2550 |  |  |  | HR2549 (Lo-16bits)
2551 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2552 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2553 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2554 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2555 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2556 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2557 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2558 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2559 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2560 |  |  |  | HR2559 (Lo-16bits)
2561 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2562 |  |  |  | HR2561 (Lo-16bits)
2563 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2564 |  |  |  | HR2563 (Lo-16bits)
2565 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2566 |  |  |  | HR2565 (Lo-16bits)
2567 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2568 |  |  |  | HR2567 (Lo-16bits)
2569 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2570 |  |  |  | HR2569 (Lo-16bits)
2571 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2572 |  |  |  | HR2571 (Lo-16bits)
2573 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2574 |  |  |  | HR2573 (Lo-16bits)
2575 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2576 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2577 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2578 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2579 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2580 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2581 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2582 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2583 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2584 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2585 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2586 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2587 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2588 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2589 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2590 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2591 | NOC4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2592 |  |  |  | HR2591 (Lo-16bits)
2593 | NOC4:Delay type | RW | 1 | 0=DT;1=IDMT
2594 | NOC4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2595 |  |  |  | HR2594 (Lo-16bits)
2596 | NOC4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2597 | NOC4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2598 | NOC4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2599 | NOC4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2600 | NOC4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2601 |  |  |  | HR2600 (Lo-16bits)
2602 | NOC4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2603 |  |  |  | HR2602 (Lo-16bits)
2604 | NOC4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2605 |  |  |  | HR2604 (Lo-16bits)
2606 | NOC4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2607 |  |  |  | HR2606 (Lo-16bits)
2608 | NOC4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2609 | NOC4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2610 | ROC1:Idrw> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2611 | ROC1:Idrw> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2612 | ROC2:Idrw>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2613 | ROC2:Idrw>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2614 | ROC3:Idrw>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2615 | ROC3:Idrw>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2616 | ROC4:Idrw>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2617 | ROC4:Idrw>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2618 | ROC5:Idrw>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2619 | ROC5:Idrw>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2620 | ROC6:Idrw>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2621 | ROC6:Idrw>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2622 | ROC7:Idrw>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2623 | ROC7:Idrw>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2624 | ROC8:Idrw>>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2625 | ROC8:Idrw>>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2626 | ROV1:Urw>/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2627 | ROV2:Urw>>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2628 | ROV3:Urw>>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2629 | ROV4:Urw>>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2630 | COL1:ICOL> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2631 | COL2:ICOL>> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2632 | CNU1:CNU> (50UB) mode | R(W) | 1 | 0=Disabled;1=Activated
2633 | UCP1:IUC> condition | R | 1 | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
2634 | DOC1:Idir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2635 | DOC1:Idir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2636 | DOC1:Idir> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2637 | DOC1:Idir> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2638 |  |  |  | HR2637 (Lo-16bits)
2639 | DOC1:Idir> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2640 |  |  |  | HR2639 (Lo-16bits)
2641 | DOC1:Idir> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2642 |  |  |  | HR2641 (Lo-16bits)
2643 | DOC1:Idir> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2644 |  |  |  | HR2643 (Lo-16bits)
2645 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2646 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2647 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2648 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2649 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2650 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2651 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2652 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2653 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2654 |  |  |  | HR2653 (Lo-16bits)
2655 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2656 |  |  |  | HR2655 (Lo-16bits)
2657 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2658 |  |  |  | HR2657 (Lo-16bits)
2659 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2660 |  |  |  | HR2659 (Lo-16bits)
2661 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2662 |  |  |  | HR2661 (Lo-16bits)
2663 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2664 |  |  |  | HR2663 (Lo-16bits)
2665 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2666 |  |  |  | HR2665 (Lo-16bits)
2667 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2668 |  |  |  | HR2667 (Lo-16bits)
2669 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2670 |  |  |  | HR2669 (Lo-16bits)
2671 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2672 |  |  |  | HR2671 (Lo-16bits)
2673 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2674 |  |  |  | HR2673 (Lo-16bits)
2675 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2676 |  |  |  | HR2675 (Lo-16bits)
2677 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2678 |  |  |  | HR2677 (Lo-16bits)
2679 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2680 |  |  |  | HR2679 (Lo-16bits)
2681 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2682 |  |  |  | HR2681 (Lo-16bits)
2683 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2684 |  |  |  | HR2683 (Lo-16bits)
2685 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2686 |  |  |  | HR2685 (Lo-16bits)
2687 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2688 |  |  |  | HR2687 (Lo-16bits)
2689 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2690 |  |  |  | HR2689 (Lo-16bits)
2691 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2692 |  |  |  | HR2691 (Lo-16bits)
2693 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2694 |  |  |  | HR2693 (Lo-16bits)
2695 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2696 |  |  |  | HR2695 (Lo-16bits)
2697 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2698 |  |  |  | HR2697 (Lo-16bits)
2699 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2700 |  |  |  | HR2699 (Lo-16bits)
2701 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2702 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2703 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2704 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2705 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2706 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2707 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2708 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2709 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2710 |  |  |  | HR2709 (Lo-16bits)
2711 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2712 |  |  |  | HR2711 (Lo-16bits)
2713 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2714 |  |  |  | HR2713 (Lo-16bits)
2715 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2716 |  |  |  | HR2715 (Lo-16bits)
2717 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2718 |  |  |  | HR2717 (Lo-16bits)
2719 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2720 |  |  |  | HR2719 (Lo-16bits)
2721 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2722 |  |  |  | HR2721 (Lo-16bits)
2723 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2724 |  |  |  | HR2723 (Lo-16bits)
2725 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2726 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2727 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2728 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2729 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2730 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2731 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2732 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2733 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2734 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2735 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2736 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2737 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2738 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2739 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2740 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2741 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2742 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2743 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2744 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2745 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2746 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2747 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2748 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2749 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2750 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2751 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2752 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2753 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2754 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2755 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2756 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2757 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2758 |  |  |  | HR2757 (Lo-16bits)
2759 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2760 |  |  |  | HR2759 (Lo-16bits)
2761 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2762 |  |  |  | HR2761 (Lo-16bits)
2763 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2764 |  |  |  | HR2763 (Lo-16bits)
2765 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2766 |  |  |  | HR2765 (Lo-16bits)
2767 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2768 |  |  |  | HR2767 (Lo-16bits)
2769 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2770 |  |  |  | HR2769 (Lo-16bits)
2771 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2772 |  |  |  | HR2771 (Lo-16bits)
2773 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2774 |  |  |  | HR2773 (Lo-16bits)
2775 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2776 |  |  |  | HR2775 (Lo-16bits)
2777 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2778 |  |  |  | HR2777 (Lo-16bits)
2779 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2780 |  |  |  | HR2779 (Lo-16bits)
2781 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2782 |  |  |  | HR2781 (Lo-16bits)
2783 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2784 |  |  |  | HR2783 (Lo-16bits)
2785 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2786 |  |  |  | HR2785 (Lo-16bits)
2787 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2788 |  |  |  | HR2787 (Lo-16bits)
2789 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2790 |  |  |  | HR2789 (Lo-16bits)
2791 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2792 |  |  |  | HR2791 (Lo-16bits)
2793 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2794 |  |  |  | HR2793 (Lo-16bits)
2795 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2796 |  |  |  | HR2795 (Lo-16bits)
2797 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2798 |  |  |  | HR2797 (Lo-16bits)
2799 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2800 |  |  |  | HR2799 (Lo-16bits)
2801 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2802 |  |  |  | HR2801 (Lo-16bits)
2803 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2804 |  |  |  | HR2803 (Lo-16bits)
2805 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2806 |  |  |  | HR2805 (Lo-16bits)
2807 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2808 |  |  |  | HR2807 (Lo-16bits)
2809 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2810 |  |  |  | HR2809 (Lo-16bits)
2811 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2812 |  |  |  | HR2811 (Lo-16bits)
2813 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2814 |  |  |  | HR2813 (Lo-16bits)
2815 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2816 |  |  |  | HR2815 (Lo-16bits)
2817 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2818 |  |  |  | HR2817 (Lo-16bits)
2819 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2820 |  |  |  | HR2819 (Lo-16bits)
2821 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2822 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2823 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2824 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2825 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2826 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2827 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2828 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2829 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2830 |  |  |  | HR2829 (Lo-16bits)
2831 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2832 |  |  |  | HR2831 (Lo-16bits)
2833 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2834 |  |  |  | HR2833 (Lo-16bits)
2835 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2836 |  |  |  | HR2835 (Lo-16bits)
2837 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2838 |  |  |  | HR2837 (Lo-16bits)
2839 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2840 |  |  |  | HR2839 (Lo-16bits)
2841 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2842 |  |  |  | HR2841 (Lo-16bits)
2843 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2844 |  |  |  | HR2843 (Lo-16bits)
2845 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2846 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2847 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2848 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2849 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2850 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2851 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2852 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2853 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2854 |  |  |  | HR2853 (Lo-16bits)
2855 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2856 |  |  |  | HR2855 (Lo-16bits)
2857 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2858 |  |  |  | HR2857 (Lo-16bits)
2859 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2860 |  |  |  | HR2859 (Lo-16bits)
2861 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2862 |  |  |  | HR2861 (Lo-16bits)
2863 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2864 |  |  |  | HR2863 (Lo-16bits)
2865 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2866 |  |  |  | HR2865 (Lo-16bits)
2867 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2868 |  |  |  | HR2867 (Lo-16bits)
2869 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2870 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2871 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2872 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2873 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2874 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2875 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2876 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2877 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2878 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2879 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2880 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2881 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2882 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2883 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2884 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2885 | DOC2:Idir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2886 | DOC2:Idir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2887 | DOC2:Idir>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2888 | DOC2:Idir>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2889 |  |  |  | HR2888 (Lo-16bits)
2890 | DOC2:Idir>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2891 |  |  |  | HR2890 (Lo-16bits)
2892 | DOC2:Idir>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2893 |  |  |  | HR2892 (Lo-16bits)
2894 | DOC2:Idir>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2895 |  |  |  | HR2894 (Lo-16bits)
2896 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2897 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2898 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2899 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2900 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2901 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2902 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2903 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2904 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2905 |  |  |  | HR2904 (Lo-16bits)
2906 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2907 |  |  |  | HR2906 (Lo-16bits)
2908 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2909 |  |  |  | HR2908 (Lo-16bits)
2910 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2911 |  |  |  | HR2910 (Lo-16bits)
2912 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2913 |  |  |  | HR2912 (Lo-16bits)
2914 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2915 |  |  |  | HR2914 (Lo-16bits)
2916 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2917 |  |  |  | HR2916 (Lo-16bits)
2918 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2919 |  |  |  | HR2918 (Lo-16bits)
2920 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2921 |  |  |  | HR2920 (Lo-16bits)
2922 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2923 |  |  |  | HR2922 (Lo-16bits)
2924 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2925 |  |  |  | HR2924 (Lo-16bits)
2926 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2927 |  |  |  | HR2926 (Lo-16bits)
2928 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2929 |  |  |  | HR2928 (Lo-16bits)
2930 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2931 |  |  |  | HR2930 (Lo-16bits)
2932 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2933 |  |  |  | HR2932 (Lo-16bits)
2934 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2935 |  |  |  | HR2934 (Lo-16bits)
2936 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2937 |  |  |  | HR2936 (Lo-16bits)
2938 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2939 |  |  |  | HR2938 (Lo-16bits)
2940 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2941 |  |  |  | HR2940 (Lo-16bits)
2942 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2943 |  |  |  | HR2942 (Lo-16bits)
2944 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2945 |  |  |  | HR2944 (Lo-16bits)
2946 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2947 |  |  |  | HR2946 (Lo-16bits)
2948 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2949 |  |  |  | HR2948 (Lo-16bits)
2950 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2951 |  |  |  | HR2950 (Lo-16bits)
2952 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2953 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2954 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2955 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2956 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2957 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2958 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2959 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2960 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2961 |  |  |  | HR2960 (Lo-16bits)
2962 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2963 |  |  |  | HR2962 (Lo-16bits)
2964 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2965 |  |  |  | HR2964 (Lo-16bits)
2966 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2967 |  |  |  | HR2966 (Lo-16bits)
2968 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2969 |  |  |  | HR2968 (Lo-16bits)
2970 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2971 |  |  |  | HR2970 (Lo-16bits)
2972 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2973 |  |  |  | HR2972 (Lo-16bits)
2974 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2975 |  |  |  | HR2974 (Lo-16bits)
2976 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2977 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2978 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2979 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2980 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2981 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2982 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2983 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2984 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2985 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2986 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2987 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2988 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2989 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2990 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2991 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2992 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2993 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2994 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2995 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2996 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2997 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2998 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2999 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3000 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3001 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3002 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3003 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3004 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3005 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3006 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3007 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3008 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3009 |  |  |  | HR3008 (Lo-16bits)
3010 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3011 |  |  |  | HR3010 (Lo-16bits)
3012 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3013 |  |  |  | HR3012 (Lo-16bits)
3014 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3015 |  |  |  | HR3014 (Lo-16bits)
3016 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3017 |  |  |  | HR3016 (Lo-16bits)
3018 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3019 |  |  |  | HR3018 (Lo-16bits)
3020 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3021 |  |  |  | HR3020 (Lo-16bits)
3022 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3023 |  |  |  | HR3022 (Lo-16bits)
3024 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3025 |  |  |  | HR3024 (Lo-16bits)
3026 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3027 |  |  |  | HR3026 (Lo-16bits)
3028 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3029 |  |  |  | HR3028 (Lo-16bits)
3030 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3031 |  |  |  | HR3030 (Lo-16bits)
3032 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3033 |  |  |  | HR3032 (Lo-16bits)
3034 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3035 |  |  |  | HR3034 (Lo-16bits)
3036 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3037 |  |  |  | HR3036 (Lo-16bits)
3038 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3039 |  |  |  | HR3038 (Lo-16bits)
3040 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3041 |  |  |  | HR3040 (Lo-16bits)
3042 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3043 |  |  |  | HR3042 (Lo-16bits)
3044 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3045 |  |  |  | HR3044 (Lo-16bits)
3046 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3047 |  |  |  | HR3046 (Lo-16bits)
3048 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3049 |  |  |  | HR3048 (Lo-16bits)
3050 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3051 |  |  |  | HR3050 (Lo-16bits)
3052 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3053 |  |  |  | HR3052 (Lo-16bits)
3054 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3055 |  |  |  | HR3054 (Lo-16bits)
3056 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3057 |  |  |  | HR3056 (Lo-16bits)
3058 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3059 |  |  |  | HR3058 (Lo-16bits)
3060 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3061 |  |  |  | HR3060 (Lo-16bits)
3062 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3063 |  |  |  | HR3062 (Lo-16bits)
3064 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3065 |  |  |  | HR3064 (Lo-16bits)
3066 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3067 |  |  |  | HR3066 (Lo-16bits)
3068 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3069 |  |  |  | HR3068 (Lo-16bits)
3070 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3071 |  |  |  | HR3070 (Lo-16bits)
3072 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3073 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3074 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3075 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3076 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3077 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3078 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3079 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3080 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3081 |  |  |  | HR3080 (Lo-16bits)
3082 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3083 |  |  |  | HR3082 (Lo-16bits)
3084 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3085 |  |  |  | HR3084 (Lo-16bits)
3086 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3087 |  |  |  | HR3086 (Lo-16bits)
3088 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3089 |  |  |  | HR3088 (Lo-16bits)
3090 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3091 |  |  |  | HR3090 (Lo-16bits)
3092 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3093 |  |  |  | HR3092 (Lo-16bits)
3094 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3095 |  |  |  | HR3094 (Lo-16bits)
3096 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3097 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3098 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3099 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3100 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3101 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3102 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3103 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3104 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3105 |  |  |  | HR3104 (Lo-16bits)
3106 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3107 |  |  |  | HR3106 (Lo-16bits)
3108 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3109 |  |  |  | HR3108 (Lo-16bits)
3110 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3111 |  |  |  | HR3110 (Lo-16bits)
3112 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3113 |  |  |  | HR3112 (Lo-16bits)
3114 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3115 |  |  |  | HR3114 (Lo-16bits)
3116 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3117 |  |  |  | HR3116 (Lo-16bits)
3118 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3119 |  |  |  | HR3118 (Lo-16bits)
3120 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3121 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3122 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3123 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3124 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3125 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3126 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3127 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3128 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3129 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3130 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3131 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3132 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3133 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3134 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3135 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3136 | DOC3:Idir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3137 | DOC3:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3138 | DOC3:Idir>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3139 | DOC3:Idir>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3140 |  |  |  | HR3139 (Lo-16bits)
3141 | DOC3:Idir>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3142 |  |  |  | HR3141 (Lo-16bits)
3143 | DOC3:Idir>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3144 |  |  |  | HR3143 (Lo-16bits)
3145 | DOC3:Idir>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3146 |  |  |  | HR3145 (Lo-16bits)
3147 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3148 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3149 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3150 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3151 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3152 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3153 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3154 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3155 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3156 |  |  |  | HR3155 (Lo-16bits)
3157 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3158 |  |  |  | HR3157 (Lo-16bits)
3159 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3160 |  |  |  | HR3159 (Lo-16bits)
3161 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3162 |  |  |  | HR3161 (Lo-16bits)
3163 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3164 |  |  |  | HR3163 (Lo-16bits)
3165 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3166 |  |  |  | HR3165 (Lo-16bits)
3167 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3168 |  |  |  | HR3167 (Lo-16bits)
3169 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3170 |  |  |  | HR3169 (Lo-16bits)
3171 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3172 |  |  |  | HR3171 (Lo-16bits)
3173 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3174 |  |  |  | HR3173 (Lo-16bits)
3175 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3176 |  |  |  | HR3175 (Lo-16bits)
3177 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3178 |  |  |  | HR3177 (Lo-16bits)
3179 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3180 |  |  |  | HR3179 (Lo-16bits)
3181 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3182 |  |  |  | HR3181 (Lo-16bits)
3183 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3184 |  |  |  | HR3183 (Lo-16bits)
3185 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3186 |  |  |  | HR3185 (Lo-16bits)
3187 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3188 |  |  |  | HR3187 (Lo-16bits)
3189 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3190 |  |  |  | HR3189 (Lo-16bits)
3191 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3192 |  |  |  | HR3191 (Lo-16bits)
3193 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3194 |  |  |  | HR3193 (Lo-16bits)
3195 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3196 |  |  |  | HR3195 (Lo-16bits)
3197 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3198 |  |  |  | HR3197 (Lo-16bits)
3199 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3200 |  |  |  | HR3199 (Lo-16bits)
3201 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3202 |  |  |  | HR3201 (Lo-16bits)
3203 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3204 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3205 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3206 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3207 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3208 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3209 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3210 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3211 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3212 |  |  |  | HR3211 (Lo-16bits)
3213 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3214 |  |  |  | HR3213 (Lo-16bits)
3215 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3216 |  |  |  | HR3215 (Lo-16bits)
3217 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3218 |  |  |  | HR3217 (Lo-16bits)
3219 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3220 |  |  |  | HR3219 (Lo-16bits)
3221 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3222 |  |  |  | HR3221 (Lo-16bits)
3223 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3224 |  |  |  | HR3223 (Lo-16bits)
3225 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3226 |  |  |  | HR3225 (Lo-16bits)
3227 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3228 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3229 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3230 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3231 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3232 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3233 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3234 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3235 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3236 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3237 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3238 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3239 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3240 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3241 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3242 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3243 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3244 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3245 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3246 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3247 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3248 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3249 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3250 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3251 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3252 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3253 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3254 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3255 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3256 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3257 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3258 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3259 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3260 |  |  |  | HR3259 (Lo-16bits)
3261 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3262 |  |  |  | HR3261 (Lo-16bits)
3263 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3264 |  |  |  | HR3263 (Lo-16bits)
3265 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3266 |  |  |  | HR3265 (Lo-16bits)
3267 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3268 |  |  |  | HR3267 (Lo-16bits)
3269 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3270 |  |  |  | HR3269 (Lo-16bits)
3271 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3272 |  |  |  | HR3271 (Lo-16bits)
3273 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3274 |  |  |  | HR3273 (Lo-16bits)
3275 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3276 |  |  |  | HR3275 (Lo-16bits)
3277 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3278 |  |  |  | HR3277 (Lo-16bits)
3279 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3280 |  |  |  | HR3279 (Lo-16bits)
3281 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3282 |  |  |  | HR3281 (Lo-16bits)
3283 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3284 |  |  |  | HR3283 (Lo-16bits)
3285 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3286 |  |  |  | HR3285 (Lo-16bits)
3287 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3288 |  |  |  | HR3287 (Lo-16bits)
3289 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3290 |  |  |  | HR3289 (Lo-16bits)
3291 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3292 |  |  |  | HR3291 (Lo-16bits)
3293 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3294 |  |  |  | HR3293 (Lo-16bits)
3295 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3296 |  |  |  | HR3295 (Lo-16bits)
3297 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3298 |  |  |  | HR3297 (Lo-16bits)
3299 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3300 |  |  |  | HR3299 (Lo-16bits)
3301 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3302 |  |  |  | HR3301 (Lo-16bits)
3303 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3304 |  |  |  | HR3303 (Lo-16bits)
3305 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3306 |  |  |  | HR3305 (Lo-16bits)
3307 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3308 |  |  |  | HR3307 (Lo-16bits)
3309 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3310 |  |  |  | HR3309 (Lo-16bits)
3311 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3312 |  |  |  | HR3311 (Lo-16bits)
3313 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3314 |  |  |  | HR3313 (Lo-16bits)
3315 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3316 |  |  |  | HR3315 (Lo-16bits)
3317 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3318 |  |  |  | HR3317 (Lo-16bits)
3319 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3320 |  |  |  | HR3319 (Lo-16bits)
3321 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3322 |  |  |  | HR3321 (Lo-16bits)
3323 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3324 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3325 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3326 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3327 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3328 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3329 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3330 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3331 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3332 |  |  |  | HR3331 (Lo-16bits)
3333 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3334 |  |  |  | HR3333 (Lo-16bits)
3335 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3336 |  |  |  | HR3335 (Lo-16bits)
3337 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3338 |  |  |  | HR3337 (Lo-16bits)
3339 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3340 |  |  |  | HR3339 (Lo-16bits)
3341 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3342 |  |  |  | HR3341 (Lo-16bits)
3343 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3344 |  |  |  | HR3343 (Lo-16bits)
3345 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3346 |  |  |  | HR3345 (Lo-16bits)
3347 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3348 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3349 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3350 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3351 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3352 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3353 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3354 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3355 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3356 |  |  |  | HR3355 (Lo-16bits)
3357 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3358 |  |  |  | HR3357 (Lo-16bits)
3359 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3360 |  |  |  | HR3359 (Lo-16bits)
3361 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3362 |  |  |  | HR3361 (Lo-16bits)
3363 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3364 |  |  |  | HR3363 (Lo-16bits)
3365 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3366 |  |  |  | HR3365 (Lo-16bits)
3367 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3368 |  |  |  | HR3367 (Lo-16bits)
3369 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3370 |  |  |  | HR3369 (Lo-16bits)
3371 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3372 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3373 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3374 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3375 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3376 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3377 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3378 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3379 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3380 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3381 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3382 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3383 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3384 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3385 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3386 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3387 | DOC4:Idir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3388 | DOC4:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3389 | DOC4:Idir>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3390 | DOC4:Idir>>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3391 |  |  |  | HR3390 (Lo-16bits)
3392 | DOC4:Idir>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3393 |  |  |  | HR3392 (Lo-16bits)
3394 | DOC4:Idir>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3395 |  |  |  | HR3394 (Lo-16bits)
3396 | DOC4:Idir>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3397 |  |  |  | HR3396 (Lo-16bits)
3398 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3399 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3400 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3401 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3402 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3403 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3404 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3405 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3406 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3407 |  |  |  | HR3406 (Lo-16bits)
3408 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3409 |  |  |  | HR3408 (Lo-16bits)
3410 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3411 |  |  |  | HR3410 (Lo-16bits)
3412 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3413 |  |  |  | HR3412 (Lo-16bits)
3414 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3415 |  |  |  | HR3414 (Lo-16bits)
3416 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3417 |  |  |  | HR3416 (Lo-16bits)
3418 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3419 |  |  |  | HR3418 (Lo-16bits)
3420 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3421 |  |  |  | HR3420 (Lo-16bits)
3422 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3423 |  |  |  | HR3422 (Lo-16bits)
3424 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3425 |  |  |  | HR3424 (Lo-16bits)
3426 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3427 |  |  |  | HR3426 (Lo-16bits)
3428 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3429 |  |  |  | HR3428 (Lo-16bits)
3430 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3431 |  |  |  | HR3430 (Lo-16bits)
3432 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3433 |  |  |  | HR3432 (Lo-16bits)
3434 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3435 |  |  |  | HR3434 (Lo-16bits)
3436 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3437 |  |  |  | HR3436 (Lo-16bits)
3438 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3439 |  |  |  | HR3438 (Lo-16bits)
3440 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3441 |  |  |  | HR3440 (Lo-16bits)
3442 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3443 |  |  |  | HR3442 (Lo-16bits)
3444 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3445 |  |  |  | HR3444 (Lo-16bits)
3446 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3447 |  |  |  | HR3446 (Lo-16bits)
3448 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3449 |  |  |  | HR3448 (Lo-16bits)
3450 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3451 |  |  |  | HR3450 (Lo-16bits)
3452 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3453 |  |  |  | HR3452 (Lo-16bits)
3454 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3455 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3456 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3457 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3458 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3459 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3460 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3461 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3462 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3463 |  |  |  | HR3462 (Lo-16bits)
3464 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3465 |  |  |  | HR3464 (Lo-16bits)
3466 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3467 |  |  |  | HR3466 (Lo-16bits)
3468 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3469 |  |  |  | HR3468 (Lo-16bits)
3470 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3471 |  |  |  | HR3470 (Lo-16bits)
3472 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3473 |  |  |  | HR3472 (Lo-16bits)
3474 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3475 |  |  |  | HR3474 (Lo-16bits)
3476 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3477 |  |  |  | HR3476 (Lo-16bits)
3478 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3479 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3480 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3481 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3482 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3483 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3484 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3485 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3486 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3487 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3488 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3489 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3490 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3491 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3492 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3493 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3494 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3495 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3496 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3497 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3498 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3499 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3500 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3501 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3502 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3503 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3504 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3505 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3506 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3507 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3508 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3509 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3510 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3511 |  |  |  | HR3510 (Lo-16bits)
3512 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3513 |  |  |  | HR3512 (Lo-16bits)
3514 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3515 |  |  |  | HR3514 (Lo-16bits)
3516 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3517 |  |  |  | HR3516 (Lo-16bits)
3518 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3519 |  |  |  | HR3518 (Lo-16bits)
3520 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3521 |  |  |  | HR3520 (Lo-16bits)
3522 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3523 |  |  |  | HR3522 (Lo-16bits)
3524 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3525 |  |  |  | HR3524 (Lo-16bits)
3526 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3527 |  |  |  | HR3526 (Lo-16bits)
3528 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3529 |  |  |  | HR3528 (Lo-16bits)
3530 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3531 |  |  |  | HR3530 (Lo-16bits)
3532 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3533 |  |  |  | HR3532 (Lo-16bits)
3534 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3535 |  |  |  | HR3534 (Lo-16bits)
3536 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3537 |  |  |  | HR3536 (Lo-16bits)
3538 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3539 |  |  |  | HR3538 (Lo-16bits)
3540 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3541 |  |  |  | HR3540 (Lo-16bits)
3542 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3543 |  |  |  | HR3542 (Lo-16bits)
3544 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3545 |  |  |  | HR3544 (Lo-16bits)
3546 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3547 |  |  |  | HR3546 (Lo-16bits)
3548 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3549 |  |  |  | HR3548 (Lo-16bits)
3550 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3551 |  |  |  | HR3550 (Lo-16bits)
3552 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3553 |  |  |  | HR3552 (Lo-16bits)
3554 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3555 |  |  |  | HR3554 (Lo-16bits)
3556 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3557 |  |  |  | HR3556 (Lo-16bits)
3558 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3559 |  |  |  | HR3558 (Lo-16bits)
3560 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3561 |  |  |  | HR3560 (Lo-16bits)
3562 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3563 |  |  |  | HR3562 (Lo-16bits)
3564 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3565 |  |  |  | HR3564 (Lo-16bits)
3566 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3567 |  |  |  | HR3566 (Lo-16bits)
3568 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3569 |  |  |  | HR3568 (Lo-16bits)
3570 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3571 |  |  |  | HR3570 (Lo-16bits)
3572 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3573 |  |  |  | HR3572 (Lo-16bits)
3574 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3575 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3576 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3577 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3578 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3579 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3580 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3581 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3582 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3583 |  |  |  | HR3582 (Lo-16bits)
3584 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3585 |  |  |  | HR3584 (Lo-16bits)
3586 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3587 |  |  |  | HR3586 (Lo-16bits)
3588 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3589 |  |  |  | HR3588 (Lo-16bits)
3590 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3591 |  |  |  | HR3590 (Lo-16bits)
3592 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3593 |  |  |  | HR3592 (Lo-16bits)
3594 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3595 |  |  |  | HR3594 (Lo-16bits)
3596 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3597 |  |  |  | HR3596 (Lo-16bits)
3598 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3599 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3600 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3601 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3602 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3603 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3604 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3605 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3606 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3607 |  |  |  | HR3606 (Lo-16bits)
3608 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3609 |  |  |  | HR3608 (Lo-16bits)
3610 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3611 |  |  |  | HR3610 (Lo-16bits)
3612 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3613 |  |  |  | HR3612 (Lo-16bits)
3614 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3615 |  |  |  | HR3614 (Lo-16bits)
3616 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3617 |  |  |  | HR3616 (Lo-16bits)
3618 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3619 |  |  |  | HR3618 (Lo-16bits)
3620 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3621 |  |  |  | HR3620 (Lo-16bits)
3622 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3623 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3624 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3625 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3626 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3627 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3628 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3629 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3630 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3631 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3632 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3633 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3634 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3635 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3636 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3637 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3638 | NEF1:I0> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3639 | NEF1:I0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3640 | NEF1:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3641 | NEF1:I0> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3642 | NEF1:I0> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3643 |  |  |  | HR3642 (Lo-16bits)
3644 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3645 |  |  |  | HR3644 (Lo-16bits)
3646 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3647 |  |  |  | HR3646 (Lo-16bits)
3648 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3649 |  |  |  | HR3648 (Lo-16bits)
3650 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3651 |  |  |  | HR3650 (Lo-16bits)
3652 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3653 |  |  |  | HR3652 (Lo-16bits)
3654 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3655 |  |  |  | HR3654 (Lo-16bits)
3656 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3657 |  |  |  | HR3656 (Lo-16bits)
3658 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3659 |  |  |  | HR3658 (Lo-16bits)
3660 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3661 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3662 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3663 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3664 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3665 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3666 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3667 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3668 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3669 |  |  |  | HR3668 (Lo-16bits)
3670 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3671 |  |  |  | HR3670 (Lo-16bits)
3672 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3673 |  |  |  | HR3672 (Lo-16bits)
3674 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3675 |  |  |  | HR3674 (Lo-16bits)
3676 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3677 |  |  |  | HR3676 (Lo-16bits)
3678 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3679 |  |  |  | HR3678 (Lo-16bits)
3680 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3681 |  |  |  | HR3680 (Lo-16bits)
3682 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3683 |  |  |  | HR3682 (Lo-16bits)
3684 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3685 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3686 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3687 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3688 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3689 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3690 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3691 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3692 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3693 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3694 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3695 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3696 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3697 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3698 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3699 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3700 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3701 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3702 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3703 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3704 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3705 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3706 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3707 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3708 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3709 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3710 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3711 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3712 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3713 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3714 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3715 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3716 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3717 |  |  |  | HR3716 (Lo-16bits)
3718 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3719 |  |  |  | HR3718 (Lo-16bits)
3720 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3721 |  |  |  | HR3720 (Lo-16bits)
3722 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3723 |  |  |  | HR3722 (Lo-16bits)
3724 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3725 |  |  |  | HR3724 (Lo-16bits)
3726 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3727 |  |  |  | HR3726 (Lo-16bits)
3728 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3729 |  |  |  | HR3728 (Lo-16bits)
3730 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3731 |  |  |  | HR3730 (Lo-16bits)
3732 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3733 |  |  |  | HR3732 (Lo-16bits)
3734 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3735 |  |  |  | HR3734 (Lo-16bits)
3736 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3737 |  |  |  | HR3736 (Lo-16bits)
3738 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3739 |  |  |  | HR3738 (Lo-16bits)
3740 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3741 |  |  |  | HR3740 (Lo-16bits)
3742 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3743 |  |  |  | HR3742 (Lo-16bits)
3744 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3745 |  |  |  | HR3744 (Lo-16bits)
3746 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3747 |  |  |  | HR3746 (Lo-16bits)
3748 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3749 |  |  |  | HR3748 (Lo-16bits)
3750 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3751 |  |  |  | HR3750 (Lo-16bits)
3752 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3753 |  |  |  | HR3752 (Lo-16bits)
3754 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3755 |  |  |  | HR3754 (Lo-16bits)
3756 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3757 |  |  |  | HR3756 (Lo-16bits)
3758 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3759 |  |  |  | HR3758 (Lo-16bits)
3760 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3761 |  |  |  | HR3760 (Lo-16bits)
3762 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3763 |  |  |  | HR3762 (Lo-16bits)
3764 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3765 |  |  |  | HR3764 (Lo-16bits)
3766 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3767 |  |  |  | HR3766 (Lo-16bits)
3768 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3769 |  |  |  | HR3768 (Lo-16bits)
3770 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3771 |  |  |  | HR3770 (Lo-16bits)
3772 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3773 |  |  |  | HR3772 (Lo-16bits)
3774 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3775 |  |  |  | HR3774 (Lo-16bits)
3776 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3777 |  |  |  | HR3776 (Lo-16bits)
3778 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3779 |  |  |  | HR3778 (Lo-16bits)
3780 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3781 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3782 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3783 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3784 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3785 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3786 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3787 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3788 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3789 |  |  |  | HR3788 (Lo-16bits)
3790 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3791 |  |  |  | HR3790 (Lo-16bits)
3792 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3793 |  |  |  | HR3792 (Lo-16bits)
3794 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3795 |  |  |  | HR3794 (Lo-16bits)
3796 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3797 |  |  |  | HR3796 (Lo-16bits)
3798 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3799 |  |  |  | HR3798 (Lo-16bits)
3800 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3801 |  |  |  | HR3800 (Lo-16bits)
3802 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3803 |  |  |  | HR3802 (Lo-16bits)
3804 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3805 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3806 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3807 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3808 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3809 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3810 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3811 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3812 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3813 |  |  |  | HR3812 (Lo-16bits)
3814 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3815 |  |  |  | HR3814 (Lo-16bits)
3816 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3817 |  |  |  | HR3816 (Lo-16bits)
3818 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3819 |  |  |  | HR3818 (Lo-16bits)
3820 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3821 |  |  |  | HR3820 (Lo-16bits)
3822 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3823 |  |  |  | HR3822 (Lo-16bits)
3824 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3825 |  |  |  | HR3824 (Lo-16bits)
3826 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3827 |  |  |  | HR3826 (Lo-16bits)
3828 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3829 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3830 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3831 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3832 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3833 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3834 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3835 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3836 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3837 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3838 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3839 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3840 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3841 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3842 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3843 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3844 | NEF1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
3845 |  |  |  | HR3844 (Lo-16bits)
3846 | NEF1:Delay type | RW | 1 | 0=DT;1=IDMT
3847 | NEF1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
3848 |  |  |  | HR3847 (Lo-16bits)
3849 | NEF1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
3850 | NEF1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3851 | NEF1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3852 | NEF1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
3853 | NEF1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
3854 |  |  |  | HR3853 (Lo-16bits)
3855 | NEF1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
3856 |  |  |  | HR3855 (Lo-16bits)
3857 | NEF1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
3858 |  |  |  | HR3857 (Lo-16bits)
3859 | NEF1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
3860 |  |  |  | HR3859 (Lo-16bits)
3861 | NEF1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
3862 | NEF1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
3863 | NEF2:I0>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3864 | NEF2:I0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3865 | NEF2:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3866 | NEF2:I0>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3867 | NEF2:I0>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3868 |  |  |  | HR3867 (Lo-16bits)
3869 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3870 |  |  |  | HR3869 (Lo-16bits)
3871 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3872 |  |  |  | HR3871 (Lo-16bits)
3873 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3874 |  |  |  | HR3873 (Lo-16bits)
3875 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3876 |  |  |  | HR3875 (Lo-16bits)
3877 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3878 |  |  |  | HR3877 (Lo-16bits)
3879 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3880 |  |  |  | HR3879 (Lo-16bits)
3881 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3882 |  |  |  | HR3881 (Lo-16bits)
3883 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3884 |  |  |  | HR3883 (Lo-16bits)
3885 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3886 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3887 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3888 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3889 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3890 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3891 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3892 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3893 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3894 |  |  |  | HR3893 (Lo-16bits)
3895 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3896 |  |  |  | HR3895 (Lo-16bits)
3897 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3898 |  |  |  | HR3897 (Lo-16bits)
3899 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3900 |  |  |  | HR3899 (Lo-16bits)
3901 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3902 |  |  |  | HR3901 (Lo-16bits)
3903 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3904 |  |  |  | HR3903 (Lo-16bits)
3905 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3906 |  |  |  | HR3905 (Lo-16bits)
3907 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3908 |  |  |  | HR3907 (Lo-16bits)
3909 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3910 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3911 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3912 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3913 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3914 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3915 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3916 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3917 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3918 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3919 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3920 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3921 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3922 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3923 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3924 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3925 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3926 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3927 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3928 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3929 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3930 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3931 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3932 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3933 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3934 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3935 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3936 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3937 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3938 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3939 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3940 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3941 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3942 |  |  |  | HR3941 (Lo-16bits)
3943 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3944 |  |  |  | HR3943 (Lo-16bits)
3945 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3946 |  |  |  | HR3945 (Lo-16bits)
3947 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3948 |  |  |  | HR3947 (Lo-16bits)
3949 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3950 |  |  |  | HR3949 (Lo-16bits)
3951 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3952 |  |  |  | HR3951 (Lo-16bits)
3953 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3954 |  |  |  | HR3953 (Lo-16bits)
3955 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3956 |  |  |  | HR3955 (Lo-16bits)
3957 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3958 |  |  |  | HR3957 (Lo-16bits)
3959 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3960 |  |  |  | HR3959 (Lo-16bits)
3961 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3962 |  |  |  | HR3961 (Lo-16bits)
3963 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3964 |  |  |  | HR3963 (Lo-16bits)
3965 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3966 |  |  |  | HR3965 (Lo-16bits)
3967 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3968 |  |  |  | HR3967 (Lo-16bits)
3969 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3970 |  |  |  | HR3969 (Lo-16bits)
3971 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3972 |  |  |  | HR3971 (Lo-16bits)
3973 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3974 |  |  |  | HR3973 (Lo-16bits)
3975 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3976 |  |  |  | HR3975 (Lo-16bits)
3977 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3978 |  |  |  | HR3977 (Lo-16bits)
3979 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3980 |  |  |  | HR3979 (Lo-16bits)
3981 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3982 |  |  |  | HR3981 (Lo-16bits)
3983 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3984 |  |  |  | HR3983 (Lo-16bits)
3985 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3986 |  |  |  | HR3985 (Lo-16bits)
3987 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3988 |  |  |  | HR3987 (Lo-16bits)
3989 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3990 |  |  |  | HR3989 (Lo-16bits)
3991 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3992 |  |  |  | HR3991 (Lo-16bits)
3993 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3994 |  |  |  | HR3993 (Lo-16bits)
3995 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3996 |  |  |  | HR3995 (Lo-16bits)
3997 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3998 |  |  |  | HR3997 (Lo-16bits)
3999 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4000 |  |  |  | HR3999 (Lo-16bits)
4001 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4002 |  |  |  | HR4001 (Lo-16bits)
4003 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4004 |  |  |  | HR4003 (Lo-16bits)
4005 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4006 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4007 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4008 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4009 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4010 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4011 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4012 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4013 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4014 |  |  |  | HR4013 (Lo-16bits)
4015 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4016 |  |  |  | HR4015 (Lo-16bits)
4017 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4018 |  |  |  | HR4017 (Lo-16bits)
4019 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4020 |  |  |  | HR4019 (Lo-16bits)
4021 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4022 |  |  |  | HR4021 (Lo-16bits)
4023 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4024 |  |  |  | HR4023 (Lo-16bits)
4025 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4026 |  |  |  | HR4025 (Lo-16bits)
4027 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4028 |  |  |  | HR4027 (Lo-16bits)
4029 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4030 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4031 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4032 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4033 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4034 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4035 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4036 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4037 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4038 |  |  |  | HR4037 (Lo-16bits)
4039 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4040 |  |  |  | HR4039 (Lo-16bits)
4041 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4042 |  |  |  | HR4041 (Lo-16bits)
4043 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4044 |  |  |  | HR4043 (Lo-16bits)
4045 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4046 |  |  |  | HR4045 (Lo-16bits)
4047 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4048 |  |  |  | HR4047 (Lo-16bits)
4049 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4050 |  |  |  | HR4049 (Lo-16bits)
4051 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4052 |  |  |  | HR4051 (Lo-16bits)
4053 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4054 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4055 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4056 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4057 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4058 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4059 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4060 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4061 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4062 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4063 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4064 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4065 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4066 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4067 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4068 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4069 | NEF2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4070 |  |  |  | HR4069 (Lo-16bits)
4071 | NEF2:Delay type | RW | 1 | 0=DT;1=IDMT
4072 | NEF2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4073 |  |  |  | HR4072 (Lo-16bits)
4074 | NEF2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4075 | NEF2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4076 | NEF2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4077 | NEF2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4078 | NEF2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4079 |  |  |  | HR4078 (Lo-16bits)
4080 | NEF2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4081 |  |  |  | HR4080 (Lo-16bits)
4082 | NEF2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4083 |  |  |  | HR4082 (Lo-16bits)
4084 | NEF2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4085 |  |  |  | HR4084 (Lo-16bits)
4086 | NEF2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4087 | NEF2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4088 | NEF3:I0>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4089 | NEF3:I0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4090 | NEF3:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4091 | NEF3:I0>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4092 | NEF3:I0>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4093 |  |  |  | HR4092 (Lo-16bits)
4094 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4095 |  |  |  | HR4094 (Lo-16bits)
4096 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4097 |  |  |  | HR4096 (Lo-16bits)
4098 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4099 |  |  |  | HR4098 (Lo-16bits)
4100 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4101 |  |  |  | HR4100 (Lo-16bits)
4102 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4103 |  |  |  | HR4102 (Lo-16bits)
4104 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4105 |  |  |  | HR4104 (Lo-16bits)
4106 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4107 |  |  |  | HR4106 (Lo-16bits)
4108 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4109 |  |  |  | HR4108 (Lo-16bits)
4110 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4111 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4112 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4113 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4114 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4115 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4116 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4117 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4118 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4119 |  |  |  | HR4118 (Lo-16bits)
4120 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4121 |  |  |  | HR4120 (Lo-16bits)
4122 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4123 |  |  |  | HR4122 (Lo-16bits)
4124 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4125 |  |  |  | HR4124 (Lo-16bits)
4126 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4127 |  |  |  | HR4126 (Lo-16bits)
4128 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4129 |  |  |  | HR4128 (Lo-16bits)
4130 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4131 |  |  |  | HR4130 (Lo-16bits)
4132 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4133 |  |  |  | HR4132 (Lo-16bits)
4134 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4135 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4136 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4137 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4138 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4139 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4140 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4141 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4142 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4143 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4144 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4145 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4146 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4147 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4148 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4149 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4150 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4151 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4152 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4153 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4154 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4155 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4156 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4157 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4158 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4159 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4160 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4161 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4162 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4163 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4164 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4165 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4166 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4167 |  |  |  | HR4166 (Lo-16bits)
4168 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4169 |  |  |  | HR4168 (Lo-16bits)
4170 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4171 |  |  |  | HR4170 (Lo-16bits)
4172 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4173 |  |  |  | HR4172 (Lo-16bits)
4174 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4175 |  |  |  | HR4174 (Lo-16bits)
4176 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4177 |  |  |  | HR4176 (Lo-16bits)
4178 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4179 |  |  |  | HR4178 (Lo-16bits)
4180 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4181 |  |  |  | HR4180 (Lo-16bits)
4182 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4183 |  |  |  | HR4182 (Lo-16bits)
4184 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4185 |  |  |  | HR4184 (Lo-16bits)
4186 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4187 |  |  |  | HR4186 (Lo-16bits)
4188 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4189 |  |  |  | HR4188 (Lo-16bits)
4190 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4191 |  |  |  | HR4190 (Lo-16bits)
4192 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4193 |  |  |  | HR4192 (Lo-16bits)
4194 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4195 |  |  |  | HR4194 (Lo-16bits)
4196 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4197 |  |  |  | HR4196 (Lo-16bits)
4198 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4199 |  |  |  | HR4198 (Lo-16bits)
4200 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4201 |  |  |  | HR4200 (Lo-16bits)
4202 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4203 |  |  |  | HR4202 (Lo-16bits)
4204 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4205 |  |  |  | HR4204 (Lo-16bits)
4206 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4207 |  |  |  | HR4206 (Lo-16bits)
4208 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4209 |  |  |  | HR4208 (Lo-16bits)
4210 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4211 |  |  |  | HR4210 (Lo-16bits)
4212 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4213 |  |  |  | HR4212 (Lo-16bits)
4214 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4215 |  |  |  | HR4214 (Lo-16bits)
4216 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4217 |  |  |  | HR4216 (Lo-16bits)
4218 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4219 |  |  |  | HR4218 (Lo-16bits)
4220 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4221 |  |  |  | HR4220 (Lo-16bits)
4222 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4223 |  |  |  | HR4222 (Lo-16bits)
4224 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4225 |  |  |  | HR4224 (Lo-16bits)
4226 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4227 |  |  |  | HR4226 (Lo-16bits)
4228 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4229 |  |  |  | HR4228 (Lo-16bits)
4230 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4231 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4232 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4233 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4234 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4235 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4236 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4237 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4238 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4239 |  |  |  | HR4238 (Lo-16bits)
4240 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4241 |  |  |  | HR4240 (Lo-16bits)
4242 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4243 |  |  |  | HR4242 (Lo-16bits)
4244 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4245 |  |  |  | HR4244 (Lo-16bits)
4246 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4247 |  |  |  | HR4246 (Lo-16bits)
4248 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4249 |  |  |  | HR4248 (Lo-16bits)
4250 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4251 |  |  |  | HR4250 (Lo-16bits)
4252 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4253 |  |  |  | HR4252 (Lo-16bits)
4254 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4255 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4256 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4257 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4258 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4259 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4260 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4261 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4262 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4263 |  |  |  | HR4262 (Lo-16bits)
4264 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4265 |  |  |  | HR4264 (Lo-16bits)
4266 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4267 |  |  |  | HR4266 (Lo-16bits)
4268 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4269 |  |  |  | HR4268 (Lo-16bits)
4270 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4271 |  |  |  | HR4270 (Lo-16bits)
4272 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4273 |  |  |  | HR4272 (Lo-16bits)
4274 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4275 |  |  |  | HR4274 (Lo-16bits)
4276 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4277 |  |  |  | HR4276 (Lo-16bits)
4278 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4279 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4280 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4281 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4282 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4283 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4284 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4285 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4286 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4287 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4288 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4289 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4290 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4291 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4292 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4293 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4294 | NEF3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4295 |  |  |  | HR4294 (Lo-16bits)
4296 | NEF3:Delay type | RW | 1 | 0=DT;1=IDMT
4297 | NEF3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4298 |  |  |  | HR4297 (Lo-16bits)
4299 | NEF3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4300 | NEF3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4301 | NEF3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4302 | NEF3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4303 | NEF3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4304 |  |  |  | HR4303 (Lo-16bits)
4305 | NEF3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4306 |  |  |  | HR4305 (Lo-16bits)
4307 | NEF3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4308 |  |  |  | HR4307 (Lo-16bits)
4309 | NEF3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4310 |  |  |  | HR4309 (Lo-16bits)
4311 | NEF3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4312 | NEF3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4313 | NEF4:I0>>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4314 | NEF4:I0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4315 | NEF4:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4316 | NEF4:I0>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4317 | NEF4:I0>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4318 |  |  |  | HR4317 (Lo-16bits)
4319 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4320 |  |  |  | HR4319 (Lo-16bits)
4321 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4322 |  |  |  | HR4321 (Lo-16bits)
4323 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4324 |  |  |  | HR4323 (Lo-16bits)
4325 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4326 |  |  |  | HR4325 (Lo-16bits)
4327 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4328 |  |  |  | HR4327 (Lo-16bits)
4329 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4330 |  |  |  | HR4329 (Lo-16bits)
4331 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4332 |  |  |  | HR4331 (Lo-16bits)
4333 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4334 |  |  |  | HR4333 (Lo-16bits)
4335 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4336 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4337 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4338 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4339 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4340 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4341 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4342 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4343 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4344 |  |  |  | HR4343 (Lo-16bits)
4345 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4346 |  |  |  | HR4345 (Lo-16bits)
4347 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4348 |  |  |  | HR4347 (Lo-16bits)
4349 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4350 |  |  |  | HR4349 (Lo-16bits)
4351 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4352 |  |  |  | HR4351 (Lo-16bits)
4353 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4354 |  |  |  | HR4353 (Lo-16bits)
4355 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4356 |  |  |  | HR4355 (Lo-16bits)
4357 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4358 |  |  |  | HR4357 (Lo-16bits)
4359 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4360 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4361 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4362 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4363 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4364 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4365 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4366 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4367 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4368 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4369 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4370 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4371 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4372 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4373 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4374 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4375 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4376 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4377 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4378 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4379 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4380 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4381 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4382 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4383 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4384 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4385 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4386 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4387 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4388 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4389 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4390 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4391 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4392 |  |  |  | HR4391 (Lo-16bits)
4393 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4394 |  |  |  | HR4393 (Lo-16bits)
4395 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4396 |  |  |  | HR4395 (Lo-16bits)
4397 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4398 |  |  |  | HR4397 (Lo-16bits)
4399 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4400 |  |  |  | HR4399 (Lo-16bits)
4401 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4402 |  |  |  | HR4401 (Lo-16bits)
4403 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4404 |  |  |  | HR4403 (Lo-16bits)
4405 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4406 |  |  |  | HR4405 (Lo-16bits)
4407 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4408 |  |  |  | HR4407 (Lo-16bits)
4409 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4410 |  |  |  | HR4409 (Lo-16bits)
4411 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4412 |  |  |  | HR4411 (Lo-16bits)
4413 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4414 |  |  |  | HR4413 (Lo-16bits)
4415 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4416 |  |  |  | HR4415 (Lo-16bits)
4417 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4418 |  |  |  | HR4417 (Lo-16bits)
4419 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4420 |  |  |  | HR4419 (Lo-16bits)
4421 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4422 |  |  |  | HR4421 (Lo-16bits)
4423 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4424 |  |  |  | HR4423 (Lo-16bits)
4425 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4426 |  |  |  | HR4425 (Lo-16bits)
4427 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4428 |  |  |  | HR4427 (Lo-16bits)
4429 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4430 |  |  |  | HR4429 (Lo-16bits)
4431 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4432 |  |  |  | HR4431 (Lo-16bits)
4433 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4434 |  |  |  | HR4433 (Lo-16bits)
4435 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4436 |  |  |  | HR4435 (Lo-16bits)
4437 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4438 |  |  |  | HR4437 (Lo-16bits)
4439 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4440 |  |  |  | HR4439 (Lo-16bits)
4441 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4442 |  |  |  | HR4441 (Lo-16bits)
4443 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4444 |  |  |  | HR4443 (Lo-16bits)
4445 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4446 |  |  |  | HR4445 (Lo-16bits)
4447 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4448 |  |  |  | HR4447 (Lo-16bits)
4449 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4450 |  |  |  | HR4449 (Lo-16bits)
4451 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4452 |  |  |  | HR4451 (Lo-16bits)
4453 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4454 |  |  |  | HR4453 (Lo-16bits)
4455 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4456 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4457 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4458 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4459 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4460 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4461 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4462 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4463 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4464 |  |  |  | HR4463 (Lo-16bits)
4465 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4466 |  |  |  | HR4465 (Lo-16bits)
4467 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4468 |  |  |  | HR4467 (Lo-16bits)
4469 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4470 |  |  |  | HR4469 (Lo-16bits)
4471 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4472 |  |  |  | HR4471 (Lo-16bits)
4473 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4474 |  |  |  | HR4473 (Lo-16bits)
4475 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4476 |  |  |  | HR4475 (Lo-16bits)
4477 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4478 |  |  |  | HR4477 (Lo-16bits)
4479 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4480 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4481 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4482 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4483 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4484 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4485 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4486 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4487 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4488 |  |  |  | HR4487 (Lo-16bits)
4489 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4490 |  |  |  | HR4489 (Lo-16bits)
4491 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4492 |  |  |  | HR4491 (Lo-16bits)
4493 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4494 |  |  |  | HR4493 (Lo-16bits)
4495 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4496 |  |  |  | HR4495 (Lo-16bits)
4497 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4498 |  |  |  | HR4497 (Lo-16bits)
4499 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4500 |  |  |  | HR4499 (Lo-16bits)
4501 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4502 |  |  |  | HR4501 (Lo-16bits)
4503 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4504 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4505 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4506 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4507 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4508 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4509 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4510 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4511 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4512 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4513 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4514 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4515 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4516 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4517 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4518 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4519 | NEF4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4520 |  |  |  | HR4519 (Lo-16bits)
4521 | NEF4:Delay type | RW | 1 | 0=DT;1=IDMT
4522 | NEF4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4523 |  |  |  | HR4522 (Lo-16bits)
4524 | NEF4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4525 | NEF4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4526 | NEF4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4527 | NEF4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4528 | NEF4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4529 |  |  |  | HR4528 (Lo-16bits)
4530 | NEF4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4531 |  |  |  | HR4530 (Lo-16bits)
4532 | NEF4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4533 |  |  |  | HR4532 (Lo-16bits)
4534 | NEF4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4535 |  |  |  | HR4534 (Lo-16bits)
4536 | NEF4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4537 | NEF4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4538 | DEF1:I0dir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4539 | DEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4540 | DEF1:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4541 | DEF1:I0dir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4542 | DEF1:I0dir> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4543 |  |  |  | HR4542 (Lo-16bits)
4544 | DEF1:I0dir> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4545 |  |  |  | HR4544 (Lo-16bits)
4546 | DEF1:I0dir> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4547 |  |  |  | HR4546 (Lo-16bits)
4548 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4549 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4550 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4551 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4552 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4553 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4554 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4555 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4556 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4557 |  |  |  | HR4556 (Lo-16bits)
4558 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4559 |  |  |  | HR4558 (Lo-16bits)
4560 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4561 |  |  |  | HR4560 (Lo-16bits)
4562 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4563 |  |  |  | HR4562 (Lo-16bits)
4564 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4565 |  |  |  | HR4564 (Lo-16bits)
4566 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4567 |  |  |  | HR4566 (Lo-16bits)
4568 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4569 |  |  |  | HR4568 (Lo-16bits)
4570 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4571 |  |  |  | HR4570 (Lo-16bits)
4572 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4573 |  |  |  | HR4572 (Lo-16bits)
4574 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4575 |  |  |  | HR4574 (Lo-16bits)
4576 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4577 |  |  |  | HR4576 (Lo-16bits)
4578 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4579 |  |  |  | HR4578 (Lo-16bits)
4580 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4581 |  |  |  | HR4580 (Lo-16bits)
4582 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4583 |  |  |  | HR4582 (Lo-16bits)
4584 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4585 |  |  |  | HR4584 (Lo-16bits)
4586 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4587 |  |  |  | HR4586 (Lo-16bits)
4588 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4589 |  |  |  | HR4588 (Lo-16bits)
4590 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4591 |  |  |  | HR4590 (Lo-16bits)
4592 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4593 |  |  |  | HR4592 (Lo-16bits)
4594 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4595 |  |  |  | HR4594 (Lo-16bits)
4596 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4597 |  |  |  | HR4596 (Lo-16bits)
4598 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4599 |  |  |  | HR4598 (Lo-16bits)
4600 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4601 |  |  |  | HR4600 (Lo-16bits)
4602 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4603 |  |  |  | HR4602 (Lo-16bits)
4604 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4605 |  |  |  | HR4604 (Lo-16bits)
4606 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4607 |  |  |  | HR4606 (Lo-16bits)
4608 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4609 |  |  |  | HR4608 (Lo-16bits)
4610 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4611 |  |  |  | HR4610 (Lo-16bits)
4612 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4613 |  |  |  | HR4612 (Lo-16bits)
4614 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4615 |  |  |  | HR4614 (Lo-16bits)
4616 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4617 |  |  |  | HR4616 (Lo-16bits)
4618 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4619 |  |  |  | HR4618 (Lo-16bits)
4620 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4621 |  |  |  | HR4620 (Lo-16bits)
4622 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4623 |  |  |  | HR4622 (Lo-16bits)
4624 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4625 |  |  |  | HR4624 (Lo-16bits)
4626 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4627 |  |  |  | HR4626 (Lo-16bits)
4628 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4629 |  |  |  | HR4628 (Lo-16bits)
4630 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4631 |  |  |  | HR4630 (Lo-16bits)
4632 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4633 |  |  |  | HR4632 (Lo-16bits)
4634 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4635 |  |  |  | HR4634 (Lo-16bits)
4636 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4637 |  |  |  | HR4636 (Lo-16bits)
4638 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4639 |  |  |  | HR4638 (Lo-16bits)
4640 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4641 |  |  |  | HR4640 (Lo-16bits)
4642 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4643 |  |  |  | HR4642 (Lo-16bits)
4644 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4645 |  |  |  | HR4644 (Lo-16bits)
4646 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4647 |  |  |  | HR4646 (Lo-16bits)
4648 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4649 |  |  |  | HR4648 (Lo-16bits)
4650 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4651 |  |  |  | HR4650 (Lo-16bits)
4652 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4653 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4654 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4655 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4656 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4657 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4658 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4659 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4660 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4661 |  |  |  | HR4660 (Lo-16bits)
4662 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4663 |  |  |  | HR4662 (Lo-16bits)
4664 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4665 |  |  |  | HR4664 (Lo-16bits)
4666 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4667 |  |  |  | HR4666 (Lo-16bits)
4668 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4669 |  |  |  | HR4668 (Lo-16bits)
4670 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4671 |  |  |  | HR4670 (Lo-16bits)
4672 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4673 |  |  |  | HR4672 (Lo-16bits)
4674 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4675 |  |  |  | HR4674 (Lo-16bits)
4676 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4677 |  |  |  | HR4676 (Lo-16bits)
4678 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4679 |  |  |  | HR4678 (Lo-16bits)
4680 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4681 |  |  |  | HR4680 (Lo-16bits)
4682 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4683 |  |  |  | HR4682 (Lo-16bits)
4684 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4685 |  |  |  | HR4684 (Lo-16bits)
4686 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4687 |  |  |  | HR4686 (Lo-16bits)
4688 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4689 |  |  |  | HR4688 (Lo-16bits)
4690 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4691 |  |  |  | HR4690 (Lo-16bits)
4692 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4693 |  |  |  | HR4692 (Lo-16bits)
4694 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4695 |  |  |  | HR4694 (Lo-16bits)
4696 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4697 |  |  |  | HR4696 (Lo-16bits)
4698 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4699 |  |  |  | HR4698 (Lo-16bits)
4700 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4701 |  |  |  | HR4700 (Lo-16bits)
4702 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4703 |  |  |  | HR4702 (Lo-16bits)
4704 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4705 |  |  |  | HR4704 (Lo-16bits)
4706 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4707 |  |  |  | HR4706 (Lo-16bits)
4708 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4709 |  |  |  | HR4708 (Lo-16bits)
4710 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4711 |  |  |  | HR4710 (Lo-16bits)
4712 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4713 |  |  |  | HR4712 (Lo-16bits)
4714 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4715 |  |  |  | HR4714 (Lo-16bits)
4716 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4717 |  |  |  | HR4716 (Lo-16bits)
4718 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4719 |  |  |  | HR4718 (Lo-16bits)
4720 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4721 |  |  |  | HR4720 (Lo-16bits)
4722 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4723 |  |  |  | HR4722 (Lo-16bits)
4724 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4725 |  |  |  | HR4724 (Lo-16bits)
4726 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4727 |  |  |  | HR4726 (Lo-16bits)
4728 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4729 |  |  |  | HR4728 (Lo-16bits)
4730 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4731 |  |  |  | HR4730 (Lo-16bits)
4732 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4733 |  |  |  | HR4732 (Lo-16bits)
4734 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4735 |  |  |  | HR4734 (Lo-16bits)
4736 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4737 |  |  |  | HR4736 (Lo-16bits)
4738 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4739 |  |  |  | HR4738 (Lo-16bits)
4740 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4741 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4742 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4743 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4744 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4745 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4746 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4747 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4748 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4749 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4750 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4751 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4752 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4753 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4754 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4755 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4756 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4757 |  |  |  | HR4756 (Lo-16bits)
4758 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4759 |  |  |  | HR4758 (Lo-16bits)
4760 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4761 |  |  |  | HR4760 (Lo-16bits)
4762 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4763 |  |  |  | HR4762 (Lo-16bits)
4764 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4765 |  |  |  | HR4764 (Lo-16bits)
4766 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4767 |  |  |  | HR4766 (Lo-16bits)
4768 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4769 |  |  |  | HR4768 (Lo-16bits)
4770 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4771 |  |  |  | HR4770 (Lo-16bits)
4772 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4773 |  |  |  | HR4772 (Lo-16bits)
4774 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4775 |  |  |  | HR4774 (Lo-16bits)
4776 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4777 |  |  |  | HR4776 (Lo-16bits)
4778 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4779 |  |  |  | HR4778 (Lo-16bits)
4780 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4781 |  |  |  | HR4780 (Lo-16bits)
4782 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4783 |  |  |  | HR4782 (Lo-16bits)
4784 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4785 |  |  |  | HR4784 (Lo-16bits)
4786 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4787 |  |  |  | HR4786 (Lo-16bits)
4788 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4789 |  |  |  | HR4788 (Lo-16bits)
4790 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4791 |  |  |  | HR4790 (Lo-16bits)
4792 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4793 |  |  |  | HR4792 (Lo-16bits)
4794 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4795 |  |  |  | HR4794 (Lo-16bits)
4796 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4797 |  |  |  | HR4796 (Lo-16bits)
4798 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4799 |  |  |  | HR4798 (Lo-16bits)
4800 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4801 |  |  |  | HR4800 (Lo-16bits)
4802 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4803 |  |  |  | HR4802 (Lo-16bits)
4804 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4805 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4806 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4807 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4808 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4809 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4810 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4811 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4812 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4813 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4814 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4815 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4816 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4817 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4818 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4819 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4820 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4821 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4822 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4823 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4824 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4825 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4826 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4827 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4828 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4829 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4830 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4831 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4832 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4833 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4834 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4835 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4836 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4837 |  |  |  | HR4836 (Lo-16bits)
4838 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4839 |  |  |  | HR4838 (Lo-16bits)
4840 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4841 |  |  |  | HR4840 (Lo-16bits)
4842 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4843 |  |  |  | HR4842 (Lo-16bits)
4844 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4845 |  |  |  | HR4844 (Lo-16bits)
4846 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4847 |  |  |  | HR4846 (Lo-16bits)
4848 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4849 |  |  |  | HR4848 (Lo-16bits)
4850 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4851 |  |  |  | HR4850 (Lo-16bits)
4852 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4853 |  |  |  | HR4852 (Lo-16bits)
4854 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4855 |  |  |  | HR4854 (Lo-16bits)
4856 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4857 |  |  |  | HR4856 (Lo-16bits)
4858 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4859 |  |  |  | HR4858 (Lo-16bits)
4860 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4861 |  |  |  | HR4860 (Lo-16bits)
4862 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4863 |  |  |  | HR4862 (Lo-16bits)
4864 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4865 |  |  |  | HR4864 (Lo-16bits)
4866 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4867 |  |  |  | HR4866 (Lo-16bits)
4868 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4869 |  |  |  | HR4868 (Lo-16bits)
4870 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4871 |  |  |  | HR4870 (Lo-16bits)
4872 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4873 |  |  |  | HR4872 (Lo-16bits)
4874 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4875 |  |  |  | HR4874 (Lo-16bits)
4876 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4877 |  |  |  | HR4876 (Lo-16bits)
4878 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4879 |  |  |  | HR4878 (Lo-16bits)
4880 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4881 |  |  |  | HR4880 (Lo-16bits)
4882 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4883 |  |  |  | HR4882 (Lo-16bits)
4884 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4885 |  |  |  | HR4884 (Lo-16bits)
4886 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4887 |  |  |  | HR4886 (Lo-16bits)
4888 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4889 |  |  |  | HR4888 (Lo-16bits)
4890 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4891 |  |  |  | HR4890 (Lo-16bits)
4892 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4893 |  |  |  | HR4892 (Lo-16bits)
4894 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4895 |  |  |  | HR4894 (Lo-16bits)
4896 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4897 |  |  |  | HR4896 (Lo-16bits)
4898 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4899 |  |  |  | HR4898 (Lo-16bits)
4900 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4901 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4902 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4903 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4904 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4905 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4906 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4907 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4908 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4909 |  |  |  | HR4908 (Lo-16bits)
4910 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4911 |  |  |  | HR4910 (Lo-16bits)
4912 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4913 |  |  |  | HR4912 (Lo-16bits)
4914 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4915 |  |  |  | HR4914 (Lo-16bits)
4916 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4917 |  |  |  | HR4916 (Lo-16bits)
4918 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4919 |  |  |  | HR4918 (Lo-16bits)
4920 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4921 |  |  |  | HR4920 (Lo-16bits)
4922 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4923 |  |  |  | HR4922 (Lo-16bits)
4924 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4925 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4926 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4927 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4928 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4929 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4930 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4931 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4932 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4933 |  |  |  | HR4932 (Lo-16bits)
4934 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4935 |  |  |  | HR4934 (Lo-16bits)
4936 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4937 |  |  |  | HR4936 (Lo-16bits)
4938 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4939 |  |  |  | HR4938 (Lo-16bits)
4940 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4941 |  |  |  | HR4940 (Lo-16bits)
4942 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4943 |  |  |  | HR4942 (Lo-16bits)
4944 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4945 |  |  |  | HR4944 (Lo-16bits)
4946 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4947 |  |  |  | HR4946 (Lo-16bits)
4948 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4949 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4950 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4951 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4952 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4953 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4954 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4955 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4956 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4957 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4958 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4959 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4960 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4961 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4962 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4963 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4964 | DEF2:I0dir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4965 | DEF2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4966 | DEF2:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4967 | DEF2:I0dir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4968 | DEF2:I0dir>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4969 |  |  |  | HR4968 (Lo-16bits)
4970 | DEF2:I0dir>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4971 |  |  |  | HR4970 (Lo-16bits)
4972 | DEF2:I0dir>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4973 |  |  |  | HR4972 (Lo-16bits)
4974 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4975 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4976 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4977 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4978 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4979 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4980 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4981 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4982 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4983 |  |  |  | HR4982 (Lo-16bits)
4984 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4985 |  |  |  | HR4984 (Lo-16bits)
4986 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4987 |  |  |  | HR4986 (Lo-16bits)
4988 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4989 |  |  |  | HR4988 (Lo-16bits)
4990 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4991 |  |  |  | HR4990 (Lo-16bits)
4992 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4993 |  |  |  | HR4992 (Lo-16bits)
4994 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4995 |  |  |  | HR4994 (Lo-16bits)
4996 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4997 |  |  |  | HR4996 (Lo-16bits)
4998 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4999 |  |  |  | HR4998 (Lo-16bits)
5000 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5001 |  |  |  | HR5000 (Lo-16bits)
5002 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5003 |  |  |  | HR5002 (Lo-16bits)
5004 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5005 |  |  |  | HR5004 (Lo-16bits)
5006 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5007 |  |  |  | HR5006 (Lo-16bits)
5008 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5009 |  |  |  | HR5008 (Lo-16bits)
5010 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5011 |  |  |  | HR5010 (Lo-16bits)
5012 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5013 |  |  |  | HR5012 (Lo-16bits)
5014 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5015 |  |  |  | HR5014 (Lo-16bits)
5016 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5017 |  |  |  | HR5016 (Lo-16bits)
5018 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5019 |  |  |  | HR5018 (Lo-16bits)
5020 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5021 |  |  |  | HR5020 (Lo-16bits)
5022 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5023 |  |  |  | HR5022 (Lo-16bits)
5024 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5025 |  |  |  | HR5024 (Lo-16bits)
5026 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5027 |  |  |  | HR5026 (Lo-16bits)
5028 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5029 |  |  |  | HR5028 (Lo-16bits)
5030 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5031 |  |  |  | HR5030 (Lo-16bits)
5032 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5033 |  |  |  | HR5032 (Lo-16bits)
5034 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5035 |  |  |  | HR5034 (Lo-16bits)
5036 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5037 |  |  |  | HR5036 (Lo-16bits)
5038 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5039 |  |  |  | HR5038 (Lo-16bits)
5040 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5041 |  |  |  | HR5040 (Lo-16bits)
5042 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5043 |  |  |  | HR5042 (Lo-16bits)
5044 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5045 |  |  |  | HR5044 (Lo-16bits)
5046 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5047 |  |  |  | HR5046 (Lo-16bits)
5048 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5049 |  |  |  | HR5048 (Lo-16bits)
5050 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5051 |  |  |  | HR5050 (Lo-16bits)
5052 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5053 |  |  |  | HR5052 (Lo-16bits)
5054 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5055 |  |  |  | HR5054 (Lo-16bits)
5056 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5057 |  |  |  | HR5056 (Lo-16bits)
5058 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5059 |  |  |  | HR5058 (Lo-16bits)
5060 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5061 |  |  |  | HR5060 (Lo-16bits)
5062 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5063 |  |  |  | HR5062 (Lo-16bits)
5064 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5065 |  |  |  | HR5064 (Lo-16bits)
5066 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5067 |  |  |  | HR5066 (Lo-16bits)
5068 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5069 |  |  |  | HR5068 (Lo-16bits)
5070 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5071 |  |  |  | HR5070 (Lo-16bits)
5072 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5073 |  |  |  | HR5072 (Lo-16bits)
5074 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5075 |  |  |  | HR5074 (Lo-16bits)
5076 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5077 |  |  |  | HR5076 (Lo-16bits)
5078 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5079 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5080 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5081 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5082 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5083 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5084 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5085 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5086 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5087 |  |  |  | HR5086 (Lo-16bits)
5088 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5089 |  |  |  | HR5088 (Lo-16bits)
5090 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5091 |  |  |  | HR5090 (Lo-16bits)
5092 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5093 |  |  |  | HR5092 (Lo-16bits)
5094 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5095 |  |  |  | HR5094 (Lo-16bits)
5096 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5097 |  |  |  | HR5096 (Lo-16bits)
5098 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5099 |  |  |  | HR5098 (Lo-16bits)
5100 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5101 |  |  |  | HR5100 (Lo-16bits)
5102 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5103 |  |  |  | HR5102 (Lo-16bits)
5104 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5105 |  |  |  | HR5104 (Lo-16bits)
5106 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5107 |  |  |  | HR5106 (Lo-16bits)
5108 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5109 |  |  |  | HR5108 (Lo-16bits)
5110 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5111 |  |  |  | HR5110 (Lo-16bits)
5112 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5113 |  |  |  | HR5112 (Lo-16bits)
5114 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5115 |  |  |  | HR5114 (Lo-16bits)
5116 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5117 |  |  |  | HR5116 (Lo-16bits)
5118 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5119 |  |  |  | HR5118 (Lo-16bits)
5120 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5121 |  |  |  | HR5120 (Lo-16bits)
5122 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5123 |  |  |  | HR5122 (Lo-16bits)
5124 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5125 |  |  |  | HR5124 (Lo-16bits)
5126 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5127 |  |  |  | HR5126 (Lo-16bits)
5128 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5129 |  |  |  | HR5128 (Lo-16bits)
5130 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5131 |  |  |  | HR5130 (Lo-16bits)
5132 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5133 |  |  |  | HR5132 (Lo-16bits)
5134 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5135 |  |  |  | HR5134 (Lo-16bits)
5136 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5137 |  |  |  | HR5136 (Lo-16bits)
5138 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5139 |  |  |  | HR5138 (Lo-16bits)
5140 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5141 |  |  |  | HR5140 (Lo-16bits)
5142 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5143 |  |  |  | HR5142 (Lo-16bits)
5144 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5145 |  |  |  | HR5144 (Lo-16bits)
5146 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5147 |  |  |  | HR5146 (Lo-16bits)
5148 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5149 |  |  |  | HR5148 (Lo-16bits)
5150 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5151 |  |  |  | HR5150 (Lo-16bits)
5152 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5153 |  |  |  | HR5152 (Lo-16bits)
5154 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5155 |  |  |  | HR5154 (Lo-16bits)
5156 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5157 |  |  |  | HR5156 (Lo-16bits)
5158 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5159 |  |  |  | HR5158 (Lo-16bits)
5160 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5161 |  |  |  | HR5160 (Lo-16bits)
5162 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5163 |  |  |  | HR5162 (Lo-16bits)
5164 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5165 |  |  |  | HR5164 (Lo-16bits)
5166 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5167 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5168 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5169 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5170 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5171 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5172 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5173 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5174 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5175 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5176 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5177 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5178 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5179 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5180 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5181 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5182 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5183 |  |  |  | HR5182 (Lo-16bits)
5184 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5185 |  |  |  | HR5184 (Lo-16bits)
5186 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5187 |  |  |  | HR5186 (Lo-16bits)
5188 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5189 |  |  |  | HR5188 (Lo-16bits)
5190 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5191 |  |  |  | HR5190 (Lo-16bits)
5192 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5193 |  |  |  | HR5192 (Lo-16bits)
5194 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5195 |  |  |  | HR5194 (Lo-16bits)
5196 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5197 |  |  |  | HR5196 (Lo-16bits)
5198 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5199 |  |  |  | HR5198 (Lo-16bits)
5200 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5201 |  |  |  | HR5200 (Lo-16bits)
5202 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5203 |  |  |  | HR5202 (Lo-16bits)
5204 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5205 |  |  |  | HR5204 (Lo-16bits)
5206 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5207 |  |  |  | HR5206 (Lo-16bits)
5208 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5209 |  |  |  | HR5208 (Lo-16bits)
5210 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5211 |  |  |  | HR5210 (Lo-16bits)
5212 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5213 |  |  |  | HR5212 (Lo-16bits)
5214 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5215 |  |  |  | HR5214 (Lo-16bits)
5216 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5217 |  |  |  | HR5216 (Lo-16bits)
5218 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5219 |  |  |  | HR5218 (Lo-16bits)
5220 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5221 |  |  |  | HR5220 (Lo-16bits)
5222 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5223 |  |  |  | HR5222 (Lo-16bits)
5224 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5225 |  |  |  | HR5224 (Lo-16bits)
5226 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5227 |  |  |  | HR5226 (Lo-16bits)
5228 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5229 |  |  |  | HR5228 (Lo-16bits)
5230 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5231 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5232 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5233 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5234 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5235 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5236 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5237 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5238 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5239 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5240 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5241 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5242 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5243 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5244 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5245 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5246 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5247 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5248 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5249 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5250 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5251 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5252 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5253 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5254 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5255 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5256 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5257 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5258 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5259 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5260 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5261 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5262 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5263 |  |  |  | HR5262 (Lo-16bits)
5264 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5265 |  |  |  | HR5264 (Lo-16bits)
5266 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5267 |  |  |  | HR5266 (Lo-16bits)
5268 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5269 |  |  |  | HR5268 (Lo-16bits)
5270 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5271 |  |  |  | HR5270 (Lo-16bits)
5272 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5273 |  |  |  | HR5272 (Lo-16bits)
5274 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5275 |  |  |  | HR5274 (Lo-16bits)
5276 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5277 |  |  |  | HR5276 (Lo-16bits)
5278 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5279 |  |  |  | HR5278 (Lo-16bits)
5280 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5281 |  |  |  | HR5280 (Lo-16bits)
5282 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5283 |  |  |  | HR5282 (Lo-16bits)
5284 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5285 |  |  |  | HR5284 (Lo-16bits)
5286 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5287 |  |  |  | HR5286 (Lo-16bits)
5288 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5289 |  |  |  | HR5288 (Lo-16bits)
5290 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5291 |  |  |  | HR5290 (Lo-16bits)
5292 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5293 |  |  |  | HR5292 (Lo-16bits)
5294 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5295 |  |  |  | HR5294 (Lo-16bits)
5296 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5297 |  |  |  | HR5296 (Lo-16bits)
5298 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5299 |  |  |  | HR5298 (Lo-16bits)
5300 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5301 |  |  |  | HR5300 (Lo-16bits)
5302 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5303 |  |  |  | HR5302 (Lo-16bits)
5304 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5305 |  |  |  | HR5304 (Lo-16bits)
5306 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5307 |  |  |  | HR5306 (Lo-16bits)
5308 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5309 |  |  |  | HR5308 (Lo-16bits)
5310 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5311 |  |  |  | HR5310 (Lo-16bits)
5312 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5313 |  |  |  | HR5312 (Lo-16bits)
5314 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5315 |  |  |  | HR5314 (Lo-16bits)
5316 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5317 |  |  |  | HR5316 (Lo-16bits)
5318 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5319 |  |  |  | HR5318 (Lo-16bits)
5320 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5321 |  |  |  | HR5320 (Lo-16bits)
5322 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5323 |  |  |  | HR5322 (Lo-16bits)
5324 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5325 |  |  |  | HR5324 (Lo-16bits)
5326 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5327 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5328 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5329 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5330 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5331 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5332 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5333 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5334 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5335 |  |  |  | HR5334 (Lo-16bits)
5336 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5337 |  |  |  | HR5336 (Lo-16bits)
5338 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5339 |  |  |  | HR5338 (Lo-16bits)
5340 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5341 |  |  |  | HR5340 (Lo-16bits)
5342 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5343 |  |  |  | HR5342 (Lo-16bits)
5344 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5345 |  |  |  | HR5344 (Lo-16bits)
5346 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5347 |  |  |  | HR5346 (Lo-16bits)
5348 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5349 |  |  |  | HR5348 (Lo-16bits)
5350 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5351 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5352 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5353 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5354 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5355 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5356 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5357 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5358 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5359 |  |  |  | HR5358 (Lo-16bits)
5360 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5361 |  |  |  | HR5360 (Lo-16bits)
5362 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5363 |  |  |  | HR5362 (Lo-16bits)
5364 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5365 |  |  |  | HR5364 (Lo-16bits)
5366 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5367 |  |  |  | HR5366 (Lo-16bits)
5368 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5369 |  |  |  | HR5368 (Lo-16bits)
5370 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5371 |  |  |  | HR5370 (Lo-16bits)
5372 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5373 |  |  |  | HR5372 (Lo-16bits)
5374 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5375 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5376 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5377 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5378 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5379 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5380 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5381 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5382 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5383 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5384 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5385 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5386 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5387 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5388 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5389 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5390 | DEF3:I0dir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5391 | DEF3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5392 | DEF3:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5393 | DEF3:I0dir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5394 | DEF3:I0dir>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5395 |  |  |  | HR5394 (Lo-16bits)
5396 | DEF3:I0dir>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5397 |  |  |  | HR5396 (Lo-16bits)
5398 | DEF3:I0dir>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5399 |  |  |  | HR5398 (Lo-16bits)
5400 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5401 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5402 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5403 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5404 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5405 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5406 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5407 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5408 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5409 |  |  |  | HR5408 (Lo-16bits)
5410 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5411 |  |  |  | HR5410 (Lo-16bits)
5412 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5413 |  |  |  | HR5412 (Lo-16bits)
5414 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5415 |  |  |  | HR5414 (Lo-16bits)
5416 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5417 |  |  |  | HR5416 (Lo-16bits)
5418 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5419 |  |  |  | HR5418 (Lo-16bits)
5420 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5421 |  |  |  | HR5420 (Lo-16bits)
5422 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5423 |  |  |  | HR5422 (Lo-16bits)
5424 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5425 |  |  |  | HR5424 (Lo-16bits)
5426 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5427 |  |  |  | HR5426 (Lo-16bits)
5428 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5429 |  |  |  | HR5428 (Lo-16bits)
5430 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5431 |  |  |  | HR5430 (Lo-16bits)
5432 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5433 |  |  |  | HR5432 (Lo-16bits)
5434 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5435 |  |  |  | HR5434 (Lo-16bits)
5436 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5437 |  |  |  | HR5436 (Lo-16bits)
5438 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5439 |  |  |  | HR5438 (Lo-16bits)
5440 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5441 |  |  |  | HR5440 (Lo-16bits)
5442 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5443 |  |  |  | HR5442 (Lo-16bits)
5444 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5445 |  |  |  | HR5444 (Lo-16bits)
5446 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5447 |  |  |  | HR5446 (Lo-16bits)
5448 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5449 |  |  |  | HR5448 (Lo-16bits)
5450 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5451 |  |  |  | HR5450 (Lo-16bits)
5452 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5453 |  |  |  | HR5452 (Lo-16bits)
5454 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5455 |  |  |  | HR5454 (Lo-16bits)
5456 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5457 |  |  |  | HR5456 (Lo-16bits)
5458 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5459 |  |  |  | HR5458 (Lo-16bits)
5460 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5461 |  |  |  | HR5460 (Lo-16bits)
5462 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5463 |  |  |  | HR5462 (Lo-16bits)
5464 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5465 |  |  |  | HR5464 (Lo-16bits)
5466 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5467 |  |  |  | HR5466 (Lo-16bits)
5468 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5469 |  |  |  | HR5468 (Lo-16bits)
5470 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5471 |  |  |  | HR5470 (Lo-16bits)
5472 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5473 |  |  |  | HR5472 (Lo-16bits)
5474 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5475 |  |  |  | HR5474 (Lo-16bits)
5476 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5477 |  |  |  | HR5476 (Lo-16bits)
5478 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5479 |  |  |  | HR5478 (Lo-16bits)
5480 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5481 |  |  |  | HR5480 (Lo-16bits)
5482 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5483 |  |  |  | HR5482 (Lo-16bits)
5484 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5485 |  |  |  | HR5484 (Lo-16bits)
5486 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5487 |  |  |  | HR5486 (Lo-16bits)
5488 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5489 |  |  |  | HR5488 (Lo-16bits)
5490 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5491 |  |  |  | HR5490 (Lo-16bits)
5492 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5493 |  |  |  | HR5492 (Lo-16bits)
5494 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5495 |  |  |  | HR5494 (Lo-16bits)
5496 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5497 |  |  |  | HR5496 (Lo-16bits)
5498 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5499 |  |  |  | HR5498 (Lo-16bits)
5500 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5501 |  |  |  | HR5500 (Lo-16bits)
5502 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5503 |  |  |  | HR5502 (Lo-16bits)
5504 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5505 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5506 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5507 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5508 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5509 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5510 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5511 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5512 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5513 |  |  |  | HR5512 (Lo-16bits)
5514 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5515 |  |  |  | HR5514 (Lo-16bits)
5516 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5517 |  |  |  | HR5516 (Lo-16bits)
5518 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5519 |  |  |  | HR5518 (Lo-16bits)
5520 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5521 |  |  |  | HR5520 (Lo-16bits)
5522 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5523 |  |  |  | HR5522 (Lo-16bits)
5524 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5525 |  |  |  | HR5524 (Lo-16bits)
5526 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5527 |  |  |  | HR5526 (Lo-16bits)
5528 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5529 |  |  |  | HR5528 (Lo-16bits)
5530 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5531 |  |  |  | HR5530 (Lo-16bits)
5532 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5533 |  |  |  | HR5532 (Lo-16bits)
5534 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5535 |  |  |  | HR5534 (Lo-16bits)
5536 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5537 |  |  |  | HR5536 (Lo-16bits)
5538 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5539 |  |  |  | HR5538 (Lo-16bits)
5540 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5541 |  |  |  | HR5540 (Lo-16bits)
5542 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5543 |  |  |  | HR5542 (Lo-16bits)
5544 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5545 |  |  |  | HR5544 (Lo-16bits)
5546 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5547 |  |  |  | HR5546 (Lo-16bits)
5548 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5549 |  |  |  | HR5548 (Lo-16bits)
5550 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5551 |  |  |  | HR5550 (Lo-16bits)
5552 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5553 |  |  |  | HR5552 (Lo-16bits)
5554 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5555 |  |  |  | HR5554 (Lo-16bits)
5556 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5557 |  |  |  | HR5556 (Lo-16bits)
5558 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5559 |  |  |  | HR5558 (Lo-16bits)
5560 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5561 |  |  |  | HR5560 (Lo-16bits)
5562 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5563 |  |  |  | HR5562 (Lo-16bits)
5564 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5565 |  |  |  | HR5564 (Lo-16bits)
5566 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5567 |  |  |  | HR5566 (Lo-16bits)
5568 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5569 |  |  |  | HR5568 (Lo-16bits)
5570 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5571 |  |  |  | HR5570 (Lo-16bits)
5572 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5573 |  |  |  | HR5572 (Lo-16bits)
5574 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5575 |  |  |  | HR5574 (Lo-16bits)
5576 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5577 |  |  |  | HR5576 (Lo-16bits)
5578 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5579 |  |  |  | HR5578 (Lo-16bits)
5580 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5581 |  |  |  | HR5580 (Lo-16bits)
5582 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5583 |  |  |  | HR5582 (Lo-16bits)
5584 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5585 |  |  |  | HR5584 (Lo-16bits)
5586 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5587 |  |  |  | HR5586 (Lo-16bits)
5588 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5589 |  |  |  | HR5588 (Lo-16bits)
5590 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5591 |  |  |  | HR5590 (Lo-16bits)
5592 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5593 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5594 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5595 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5596 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5597 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5598 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5599 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5600 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5601 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5602 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5603 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5604 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5605 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5606 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5607 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5608 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5609 |  |  |  | HR5608 (Lo-16bits)
5610 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5611 |  |  |  | HR5610 (Lo-16bits)
5612 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5613 |  |  |  | HR5612 (Lo-16bits)
5614 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5615 |  |  |  | HR5614 (Lo-16bits)
5616 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5617 |  |  |  | HR5616 (Lo-16bits)
5618 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5619 |  |  |  | HR5618 (Lo-16bits)
5620 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5621 |  |  |  | HR5620 (Lo-16bits)
5622 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5623 |  |  |  | HR5622 (Lo-16bits)
5624 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5625 |  |  |  | HR5624 (Lo-16bits)
5626 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5627 |  |  |  | HR5626 (Lo-16bits)
5628 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5629 |  |  |  | HR5628 (Lo-16bits)
5630 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5631 |  |  |  | HR5630 (Lo-16bits)
5632 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5633 |  |  |  | HR5632 (Lo-16bits)
5634 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5635 |  |  |  | HR5634 (Lo-16bits)
5636 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5637 |  |  |  | HR5636 (Lo-16bits)
5638 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5639 |  |  |  | HR5638 (Lo-16bits)
5640 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5641 |  |  |  | HR5640 (Lo-16bits)
5642 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5643 |  |  |  | HR5642 (Lo-16bits)
5644 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5645 |  |  |  | HR5644 (Lo-16bits)
5646 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5647 |  |  |  | HR5646 (Lo-16bits)
5648 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5649 |  |  |  | HR5648 (Lo-16bits)
5650 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5651 |  |  |  | HR5650 (Lo-16bits)
5652 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5653 |  |  |  | HR5652 (Lo-16bits)
5654 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5655 |  |  |  | HR5654 (Lo-16bits)
5656 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5657 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5658 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5659 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5660 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5661 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5662 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5663 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5664 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5665 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5666 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5667 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5668 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5669 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5670 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5671 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5672 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5673 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5674 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5675 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5676 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5677 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5678 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5679 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5680 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5681 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5682 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5683 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5684 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5685 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5686 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5687 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5688 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5689 |  |  |  | HR5688 (Lo-16bits)
5690 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5691 |  |  |  | HR5690 (Lo-16bits)
5692 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5693 |  |  |  | HR5692 (Lo-16bits)
5694 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5695 |  |  |  | HR5694 (Lo-16bits)
5696 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5697 |  |  |  | HR5696 (Lo-16bits)
5698 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5699 |  |  |  | HR5698 (Lo-16bits)
5700 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5701 |  |  |  | HR5700 (Lo-16bits)
5702 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5703 |  |  |  | HR5702 (Lo-16bits)
5704 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5705 |  |  |  | HR5704 (Lo-16bits)
5706 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5707 |  |  |  | HR5706 (Lo-16bits)
5708 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5709 |  |  |  | HR5708 (Lo-16bits)
5710 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5711 |  |  |  | HR5710 (Lo-16bits)
5712 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5713 |  |  |  | HR5712 (Lo-16bits)
5714 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5715 |  |  |  | HR5714 (Lo-16bits)
5716 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5717 |  |  |  | HR5716 (Lo-16bits)
5718 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5719 |  |  |  | HR5718 (Lo-16bits)
5720 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5721 |  |  |  | HR5720 (Lo-16bits)
5722 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5723 |  |  |  | HR5722 (Lo-16bits)
5724 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5725 |  |  |  | HR5724 (Lo-16bits)
5726 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5727 |  |  |  | HR5726 (Lo-16bits)
5728 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5729 |  |  |  | HR5728 (Lo-16bits)
5730 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5731 |  |  |  | HR5730 (Lo-16bits)
5732 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5733 |  |  |  | HR5732 (Lo-16bits)
5734 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5735 |  |  |  | HR5734 (Lo-16bits)
5736 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5737 |  |  |  | HR5736 (Lo-16bits)
5738 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5739 |  |  |  | HR5738 (Lo-16bits)
5740 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5741 |  |  |  | HR5740 (Lo-16bits)
5742 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5743 |  |  |  | HR5742 (Lo-16bits)
5744 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5745 |  |  |  | HR5744 (Lo-16bits)
5746 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5747 |  |  |  | HR5746 (Lo-16bits)
5748 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5749 |  |  |  | HR5748 (Lo-16bits)
5750 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5751 |  |  |  | HR5750 (Lo-16bits)
5752 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5753 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5754 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5755 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5756 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5757 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5758 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5759 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5760 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5761 |  |  |  | HR5760 (Lo-16bits)
5762 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5763 |  |  |  | HR5762 (Lo-16bits)
5764 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5765 |  |  |  | HR5764 (Lo-16bits)
5766 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5767 |  |  |  | HR5766 (Lo-16bits)
5768 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5769 |  |  |  | HR5768 (Lo-16bits)
5770 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5771 |  |  |  | HR5770 (Lo-16bits)
5772 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5773 |  |  |  | HR5772 (Lo-16bits)
5774 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5775 |  |  |  | HR5774 (Lo-16bits)
5776 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5777 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5778 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5779 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5780 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5781 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5782 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5783 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5784 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5785 |  |  |  | HR5784 (Lo-16bits)
5786 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5787 |  |  |  | HR5786 (Lo-16bits)
5788 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5789 |  |  |  | HR5788 (Lo-16bits)
5790 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5791 |  |  |  | HR5790 (Lo-16bits)
5792 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5793 |  |  |  | HR5792 (Lo-16bits)
5794 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5795 |  |  |  | HR5794 (Lo-16bits)
5796 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5797 |  |  |  | HR5796 (Lo-16bits)
5798 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5799 |  |  |  | HR5798 (Lo-16bits)
5800 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5801 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5802 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5803 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5804 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5805 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5806 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5807 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5808 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5809 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5810 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5811 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5812 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5813 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5814 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5815 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5816 | DEF4:I0dir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5817 | DEF4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5818 | DEF4:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5819 | DEF4:I0dir>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5820 | DEF4:I0dir>>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5821 |  |  |  | HR5820 (Lo-16bits)
5822 | DEF4:I0dir>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5823 |  |  |  | HR5822 (Lo-16bits)
5824 | DEF4:I0dir>>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5825 |  |  |  | HR5824 (Lo-16bits)
5826 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5827 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5828 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5829 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5830 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5831 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5832 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5833 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5834 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5835 |  |  |  | HR5834 (Lo-16bits)
5836 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5837 |  |  |  | HR5836 (Lo-16bits)
5838 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5839 |  |  |  | HR5838 (Lo-16bits)
5840 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5841 |  |  |  | HR5840 (Lo-16bits)
5842 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5843 |  |  |  | HR5842 (Lo-16bits)
5844 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5845 |  |  |  | HR5844 (Lo-16bits)
5846 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5847 |  |  |  | HR5846 (Lo-16bits)
5848 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5849 |  |  |  | HR5848 (Lo-16bits)
5850 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5851 |  |  |  | HR5850 (Lo-16bits)
5852 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5853 |  |  |  | HR5852 (Lo-16bits)
5854 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5855 |  |  |  | HR5854 (Lo-16bits)
5856 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5857 |  |  |  | HR5856 (Lo-16bits)
5858 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5859 |  |  |  | HR5858 (Lo-16bits)
5860 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5861 |  |  |  | HR5860 (Lo-16bits)
5862 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5863 |  |  |  | HR5862 (Lo-16bits)
5864 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5865 |  |  |  | HR5864 (Lo-16bits)
5866 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5867 |  |  |  | HR5866 (Lo-16bits)
5868 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5869 |  |  |  | HR5868 (Lo-16bits)
5870 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5871 |  |  |  | HR5870 (Lo-16bits)
5872 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5873 |  |  |  | HR5872 (Lo-16bits)
5874 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5875 |  |  |  | HR5874 (Lo-16bits)
5876 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5877 |  |  |  | HR5876 (Lo-16bits)
5878 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5879 |  |  |  | HR5878 (Lo-16bits)
5880 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5881 |  |  |  | HR5880 (Lo-16bits)
5882 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5883 |  |  |  | HR5882 (Lo-16bits)
5884 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5885 |  |  |  | HR5884 (Lo-16bits)
5886 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5887 |  |  |  | HR5886 (Lo-16bits)
5888 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5889 |  |  |  | HR5888 (Lo-16bits)
5890 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5891 |  |  |  | HR5890 (Lo-16bits)
5892 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5893 |  |  |  | HR5892 (Lo-16bits)
5894 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5895 |  |  |  | HR5894 (Lo-16bits)
5896 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5897 |  |  |  | HR5896 (Lo-16bits)
5898 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5899 |  |  |  | HR5898 (Lo-16bits)
5900 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5901 |  |  |  | HR5900 (Lo-16bits)
5902 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5903 |  |  |  | HR5902 (Lo-16bits)
5904 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5905 |  |  |  | HR5904 (Lo-16bits)
5906 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5907 |  |  |  | HR5906 (Lo-16bits)
5908 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5909 |  |  |  | HR5908 (Lo-16bits)
5910 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5911 |  |  |  | HR5910 (Lo-16bits)
5912 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5913 |  |  |  | HR5912 (Lo-16bits)
5914 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5915 |  |  |  | HR5914 (Lo-16bits)
5916 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5917 |  |  |  | HR5916 (Lo-16bits)
5918 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5919 |  |  |  | HR5918 (Lo-16bits)
5920 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5921 |  |  |  | HR5920 (Lo-16bits)
5922 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5923 |  |  |  | HR5922 (Lo-16bits)
5924 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5925 |  |  |  | HR5924 (Lo-16bits)
5926 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5927 |  |  |  | HR5926 (Lo-16bits)
5928 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5929 |  |  |  | HR5928 (Lo-16bits)
5930 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5931 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5932 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5933 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5934 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5935 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5936 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5937 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5938 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5939 |  |  |  | HR5938 (Lo-16bits)
5940 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5941 |  |  |  | HR5940 (Lo-16bits)
5942 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5943 |  |  |  | HR5942 (Lo-16bits)
5944 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5945 |  |  |  | HR5944 (Lo-16bits)
5946 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5947 |  |  |  | HR5946 (Lo-16bits)
5948 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5949 |  |  |  | HR5948 (Lo-16bits)
5950 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5951 |  |  |  | HR5950 (Lo-16bits)
5952 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5953 |  |  |  | HR5952 (Lo-16bits)
5954 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5955 |  |  |  | HR5954 (Lo-16bits)
5956 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5957 |  |  |  | HR5956 (Lo-16bits)
5958 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5959 |  |  |  | HR5958 (Lo-16bits)
5960 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5961 |  |  |  | HR5960 (Lo-16bits)
5962 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5963 |  |  |  | HR5962 (Lo-16bits)
5964 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5965 |  |  |  | HR5964 (Lo-16bits)
5966 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5967 |  |  |  | HR5966 (Lo-16bits)
5968 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5969 |  |  |  | HR5968 (Lo-16bits)
5970 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5971 |  |  |  | HR5970 (Lo-16bits)
5972 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5973 |  |  |  | HR5972 (Lo-16bits)
5974 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5975 |  |  |  | HR5974 (Lo-16bits)
5976 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5977 |  |  |  | HR5976 (Lo-16bits)
5978 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5979 |  |  |  | HR5978 (Lo-16bits)
5980 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5981 |  |  |  | HR5980 (Lo-16bits)
5982 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5983 |  |  |  | HR5982 (Lo-16bits)
5984 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5985 |  |  |  | HR5984 (Lo-16bits)
5986 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5987 |  |  |  | HR5986 (Lo-16bits)
5988 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5989 |  |  |  | HR5988 (Lo-16bits)
5990 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5991 |  |  |  | HR5990 (Lo-16bits)
5992 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5993 |  |  |  | HR5992 (Lo-16bits)
5994 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5995 |  |  |  | HR5994 (Lo-16bits)
5996 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5997 |  |  |  | HR5996 (Lo-16bits)
5998 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5999 |  |  |  | HR5998 (Lo-16bits)
6000 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6001 |  |  |  | HR6000 (Lo-16bits)
6002 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6003 |  |  |  | HR6002 (Lo-16bits)
6004 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6005 |  |  |  | HR6004 (Lo-16bits)
6006 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6007 |  |  |  | HR6006 (Lo-16bits)
6008 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6009 |  |  |  | HR6008 (Lo-16bits)
6010 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6011 |  |  |  | HR6010 (Lo-16bits)
6012 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6013 |  |  |  | HR6012 (Lo-16bits)
6014 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6015 |  |  |  | HR6014 (Lo-16bits)
6016 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6017 |  |  |  | HR6016 (Lo-16bits)
6018 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6019 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6020 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6021 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6022 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6023 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6024 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6025 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6026 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6027 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6028 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6029 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6030 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6031 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6032 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6033 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6034 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6035 |  |  |  | HR6034 (Lo-16bits)
6036 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6037 |  |  |  | HR6036 (Lo-16bits)
6038 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6039 |  |  |  | HR6038 (Lo-16bits)
6040 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6041 |  |  |  | HR6040 (Lo-16bits)
6042 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6043 |  |  |  | HR6042 (Lo-16bits)
6044 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6045 |  |  |  | HR6044 (Lo-16bits)
6046 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6047 |  |  |  | HR6046 (Lo-16bits)
6048 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6049 |  |  |  | HR6048 (Lo-16bits)
6050 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6051 |  |  |  | HR6050 (Lo-16bits)
6052 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6053 |  |  |  | HR6052 (Lo-16bits)
6054 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6055 |  |  |  | HR6054 (Lo-16bits)
6056 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6057 |  |  |  | HR6056 (Lo-16bits)
6058 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6059 |  |  |  | HR6058 (Lo-16bits)
6060 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6061 |  |  |  | HR6060 (Lo-16bits)
6062 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6063 |  |  |  | HR6062 (Lo-16bits)
6064 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6065 |  |  |  | HR6064 (Lo-16bits)
6066 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6067 |  |  |  | HR6066 (Lo-16bits)
6068 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6069 |  |  |  | HR6068 (Lo-16bits)
6070 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6071 |  |  |  | HR6070 (Lo-16bits)
6072 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6073 |  |  |  | HR6072 (Lo-16bits)
6074 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6075 |  |  |  | HR6074 (Lo-16bits)
6076 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6077 |  |  |  | HR6076 (Lo-16bits)
6078 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6079 |  |  |  | HR6078 (Lo-16bits)
6080 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6081 |  |  |  | HR6080 (Lo-16bits)
6082 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6083 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6084 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6085 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6086 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6087 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6088 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6089 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6090 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6091 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6092 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6093 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6094 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6095 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6096 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6097 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6098 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6099 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6100 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6101 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6102 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6103 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6104 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6105 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6106 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6107 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6108 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6109 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6110 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6111 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6112 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6113 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6114 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6115 |  |  |  | HR6114 (Lo-16bits)
6116 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6117 |  |  |  | HR6116 (Lo-16bits)
6118 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6119 |  |  |  | HR6118 (Lo-16bits)
6120 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6121 |  |  |  | HR6120 (Lo-16bits)
6122 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6123 |  |  |  | HR6122 (Lo-16bits)
6124 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6125 |  |  |  | HR6124 (Lo-16bits)
6126 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6127 |  |  |  | HR6126 (Lo-16bits)
6128 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6129 |  |  |  | HR6128 (Lo-16bits)
6130 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6131 |  |  |  | HR6130 (Lo-16bits)
6132 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6133 |  |  |  | HR6132 (Lo-16bits)
6134 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6135 |  |  |  | HR6134 (Lo-16bits)
6136 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6137 |  |  |  | HR6136 (Lo-16bits)
6138 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6139 |  |  |  | HR6138 (Lo-16bits)
6140 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6141 |  |  |  | HR6140 (Lo-16bits)
6142 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6143 |  |  |  | HR6142 (Lo-16bits)
6144 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6145 |  |  |  | HR6144 (Lo-16bits)
6146 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6147 |  |  |  | HR6146 (Lo-16bits)
6148 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6149 |  |  |  | HR6148 (Lo-16bits)
6150 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6151 |  |  |  | HR6150 (Lo-16bits)
6152 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6153 |  |  |  | HR6152 (Lo-16bits)
6154 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6155 |  |  |  | HR6154 (Lo-16bits)
6156 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6157 |  |  |  | HR6156 (Lo-16bits)
6158 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6159 |  |  |  | HR6158 (Lo-16bits)
6160 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6161 |  |  |  | HR6160 (Lo-16bits)
6162 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6163 |  |  |  | HR6162 (Lo-16bits)
6164 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6165 |  |  |  | HR6164 (Lo-16bits)
6166 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6167 |  |  |  | HR6166 (Lo-16bits)
6168 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6169 |  |  |  | HR6168 (Lo-16bits)
6170 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6171 |  |  |  | HR6170 (Lo-16bits)
6172 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6173 |  |  |  | HR6172 (Lo-16bits)
6174 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6175 |  |  |  | HR6174 (Lo-16bits)
6176 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6177 |  |  |  | HR6176 (Lo-16bits)
6178 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6179 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6180 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6181 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6182 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6183 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6184 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6185 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6186 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6187 |  |  |  | HR6186 (Lo-16bits)
6188 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6189 |  |  |  | HR6188 (Lo-16bits)
6190 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6191 |  |  |  | HR6190 (Lo-16bits)
6192 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6193 |  |  |  | HR6192 (Lo-16bits)
6194 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6195 |  |  |  | HR6194 (Lo-16bits)
6196 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6197 |  |  |  | HR6196 (Lo-16bits)
6198 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6199 |  |  |  | HR6198 (Lo-16bits)
6200 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6201 |  |  |  | HR6200 (Lo-16bits)
6202 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6203 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6204 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6205 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6206 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6207 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6208 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6209 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6210 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6211 |  |  |  | HR6210 (Lo-16bits)
6212 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6213 |  |  |  | HR6212 (Lo-16bits)
6214 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6215 |  |  |  | HR6214 (Lo-16bits)
6216 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6217 |  |  |  | HR6216 (Lo-16bits)
6218 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6219 |  |  |  | HR6218 (Lo-16bits)
6220 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6221 |  |  |  | HR6220 (Lo-16bits)
6222 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6223 |  |  |  | HR6222 (Lo-16bits)
6224 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6225 |  |  |  | HR6224 (Lo-16bits)
6226 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6227 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6228 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6229 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6230 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6231 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6232 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6233 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6234 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6235 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6236 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6237 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6238 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6239 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6240 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6241 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6242 | IEF1:I0Int> condition | R | 1 | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
6243 | IEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
6244 | CUB1:I2> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6245 | CUB1:I2> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6246 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6247 |  |  |  | HR6246 (Lo-16bits)
6248 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6249 |  |  |  | HR6248 (Lo-16bits)
6250 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6251 |  |  |  | HR6250 (Lo-16bits)
6252 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6253 |  |  |  | HR6252 (Lo-16bits)
6254 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6255 |  |  |  | HR6254 (Lo-16bits)
6256 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6257 |  |  |  | HR6256 (Lo-16bits)
6258 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6259 |  |  |  | HR6258 (Lo-16bits)
6260 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6261 |  |  |  | HR6260 (Lo-16bits)
6262 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6263 |  |  |  | HR6262 (Lo-16bits)
6264 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6265 |  |  |  | HR6264 (Lo-16bits)
6266 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6267 |  |  |  | HR6266 (Lo-16bits)
6268 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6269 |  |  |  | HR6268 (Lo-16bits)
6270 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6271 |  |  |  | HR6270 (Lo-16bits)
6272 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6273 |  |  |  | HR6272 (Lo-16bits)
6274 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6275 |  |  |  | HR6274 (Lo-16bits)
6276 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6277 |  |  |  | HR6276 (Lo-16bits)
6278 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6279 |  |  |  | HR6278 (Lo-16bits)
6280 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6281 |  |  |  | HR6280 (Lo-16bits)
6282 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6283 |  |  |  | HR6282 (Lo-16bits)
6284 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6285 |  |  |  | HR6284 (Lo-16bits)
6286 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6287 |  |  |  | HR6286 (Lo-16bits)
6288 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6289 |  |  |  | HR6288 (Lo-16bits)
6290 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6291 |  |  |  | HR6290 (Lo-16bits)
6292 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6293 |  |  |  | HR6292 (Lo-16bits)
6294 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6295 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6296 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6297 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6298 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6299 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6300 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6301 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6302 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6303 |  |  |  | HR6302 (Lo-16bits)
6304 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6305 |  |  |  | HR6304 (Lo-16bits)
6306 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6307 |  |  |  | HR6306 (Lo-16bits)
6308 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6309 |  |  |  | HR6308 (Lo-16bits)
6310 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6311 |  |  |  | HR6310 (Lo-16bits)
6312 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6313 |  |  |  | HR6312 (Lo-16bits)
6314 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6315 |  |  |  | HR6314 (Lo-16bits)
6316 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6317 |  |  |  | HR6316 (Lo-16bits)
6318 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6319 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6320 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6321 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6322 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6323 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6324 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6325 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6326 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6327 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6328 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6329 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6330 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6331 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6332 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6333 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6334 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6335 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6336 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6337 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6338 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6339 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6340 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6341 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6342 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6343 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6344 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6345 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6346 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6347 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6348 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6349 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6350 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6351 |  |  |  | HR6350 (Lo-16bits)
6352 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6353 |  |  |  | HR6352 (Lo-16bits)
6354 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6355 |  |  |  | HR6354 (Lo-16bits)
6356 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6357 |  |  |  | HR6356 (Lo-16bits)
6358 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6359 |  |  |  | HR6358 (Lo-16bits)
6360 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6361 |  |  |  | HR6360 (Lo-16bits)
6362 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6363 |  |  |  | HR6362 (Lo-16bits)
6364 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6365 |  |  |  | HR6364 (Lo-16bits)
6366 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6367 |  |  |  | HR6366 (Lo-16bits)
6368 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6369 |  |  |  | HR6368 (Lo-16bits)
6370 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6371 |  |  |  | HR6370 (Lo-16bits)
6372 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6373 |  |  |  | HR6372 (Lo-16bits)
6374 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6375 |  |  |  | HR6374 (Lo-16bits)
6376 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6377 |  |  |  | HR6376 (Lo-16bits)
6378 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6379 |  |  |  | HR6378 (Lo-16bits)
6380 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6381 |  |  |  | HR6380 (Lo-16bits)
6382 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6383 |  |  |  | HR6382 (Lo-16bits)
6384 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6385 |  |  |  | HR6384 (Lo-16bits)
6386 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6387 |  |  |  | HR6386 (Lo-16bits)
6388 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6389 |  |  |  | HR6388 (Lo-16bits)
6390 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6391 |  |  |  | HR6390 (Lo-16bits)
6392 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6393 |  |  |  | HR6392 (Lo-16bits)
6394 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6395 |  |  |  | HR6394 (Lo-16bits)
6396 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6397 |  |  |  | HR6396 (Lo-16bits)
6398 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6399 |  |  |  | HR6398 (Lo-16bits)
6400 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6401 |  |  |  | HR6400 (Lo-16bits)
6402 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6403 |  |  |  | HR6402 (Lo-16bits)
6404 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6405 |  |  |  | HR6404 (Lo-16bits)
6406 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6407 |  |  |  | HR6406 (Lo-16bits)
6408 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6409 |  |  |  | HR6408 (Lo-16bits)
6410 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6411 |  |  |  | HR6410 (Lo-16bits)
6412 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6413 |  |  |  | HR6412 (Lo-16bits)
6414 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6415 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6416 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6417 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6418 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6419 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6420 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6421 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6422 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6423 |  |  |  | HR6422 (Lo-16bits)
6424 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6425 |  |  |  | HR6424 (Lo-16bits)
6426 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6427 |  |  |  | HR6426 (Lo-16bits)
6428 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6429 |  |  |  | HR6428 (Lo-16bits)
6430 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6431 |  |  |  | HR6430 (Lo-16bits)
6432 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6433 |  |  |  | HR6432 (Lo-16bits)
6434 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6435 |  |  |  | HR6434 (Lo-16bits)
6436 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6437 |  |  |  | HR6436 (Lo-16bits)
6438 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6439 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6440 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6441 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6442 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6443 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6444 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6445 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6446 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6447 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6448 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6449 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6450 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6451 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6452 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6453 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6454 | CUB2:I2>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6455 | CUB2:I2>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6456 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6457 |  |  |  | HR6456 (Lo-16bits)
6458 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6459 |  |  |  | HR6458 (Lo-16bits)
6460 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6461 |  |  |  | HR6460 (Lo-16bits)
6462 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6463 |  |  |  | HR6462 (Lo-16bits)
6464 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6465 |  |  |  | HR6464 (Lo-16bits)
6466 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6467 |  |  |  | HR6466 (Lo-16bits)
6468 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6469 |  |  |  | HR6468 (Lo-16bits)
6470 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6471 |  |  |  | HR6470 (Lo-16bits)
6472 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6473 |  |  |  | HR6472 (Lo-16bits)
6474 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6475 |  |  |  | HR6474 (Lo-16bits)
6476 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6477 |  |  |  | HR6476 (Lo-16bits)
6478 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6479 |  |  |  | HR6478 (Lo-16bits)
6480 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6481 |  |  |  | HR6480 (Lo-16bits)
6482 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6483 |  |  |  | HR6482 (Lo-16bits)
6484 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6485 |  |  |  | HR6484 (Lo-16bits)
6486 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6487 |  |  |  | HR6486 (Lo-16bits)
6488 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6489 |  |  |  | HR6488 (Lo-16bits)
6490 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6491 |  |  |  | HR6490 (Lo-16bits)
6492 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6493 |  |  |  | HR6492 (Lo-16bits)
6494 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6495 |  |  |  | HR6494 (Lo-16bits)
6496 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6497 |  |  |  | HR6496 (Lo-16bits)
6498 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6499 |  |  |  | HR6498 (Lo-16bits)
6500 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6501 |  |  |  | HR6500 (Lo-16bits)
6502 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6503 |  |  |  | HR6502 (Lo-16bits)
6504 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6505 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6506 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6507 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6508 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6509 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6510 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6511 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6512 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6513 |  |  |  | HR6512 (Lo-16bits)
6514 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6515 |  |  |  | HR6514 (Lo-16bits)
6516 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6517 |  |  |  | HR6516 (Lo-16bits)
6518 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6519 |  |  |  | HR6518 (Lo-16bits)
6520 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6521 |  |  |  | HR6520 (Lo-16bits)
6522 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6523 |  |  |  | HR6522 (Lo-16bits)
6524 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6525 |  |  |  | HR6524 (Lo-16bits)
6526 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6527 |  |  |  | HR6526 (Lo-16bits)
6528 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6529 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6530 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6531 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6532 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6533 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6534 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6535 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6536 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6537 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6538 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6539 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6540 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6541 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6542 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6543 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6544 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6545 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6546 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6547 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6548 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6549 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6550 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6551 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6552 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6553 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6554 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6555 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6556 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6557 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6558 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6559 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6560 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6561 |  |  |  | HR6560 (Lo-16bits)
6562 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6563 |  |  |  | HR6562 (Lo-16bits)
6564 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6565 |  |  |  | HR6564 (Lo-16bits)
6566 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6567 |  |  |  | HR6566 (Lo-16bits)
6568 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6569 |  |  |  | HR6568 (Lo-16bits)
6570 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6571 |  |  |  | HR6570 (Lo-16bits)
6572 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6573 |  |  |  | HR6572 (Lo-16bits)
6574 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6575 |  |  |  | HR6574 (Lo-16bits)
6576 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6577 |  |  |  | HR6576 (Lo-16bits)
6578 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6579 |  |  |  | HR6578 (Lo-16bits)
6580 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6581 |  |  |  | HR6580 (Lo-16bits)
6582 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6583 |  |  |  | HR6582 (Lo-16bits)
6584 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6585 |  |  |  | HR6584 (Lo-16bits)
6586 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6587 |  |  |  | HR6586 (Lo-16bits)
6588 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6589 |  |  |  | HR6588 (Lo-16bits)
6590 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6591 |  |  |  | HR6590 (Lo-16bits)
6592 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6593 |  |  |  | HR6592 (Lo-16bits)
6594 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6595 |  |  |  | HR6594 (Lo-16bits)
6596 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6597 |  |  |  | HR6596 (Lo-16bits)
6598 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6599 |  |  |  | HR6598 (Lo-16bits)
6600 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6601 |  |  |  | HR6600 (Lo-16bits)
6602 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6603 |  |  |  | HR6602 (Lo-16bits)
6604 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6605 |  |  |  | HR6604 (Lo-16bits)
6606 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6607 |  |  |  | HR6606 (Lo-16bits)
6608 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6609 |  |  |  | HR6608 (Lo-16bits)
6610 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6611 |  |  |  | HR6610 (Lo-16bits)
6612 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6613 |  |  |  | HR6612 (Lo-16bits)
6614 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6615 |  |  |  | HR6614 (Lo-16bits)
6616 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6617 |  |  |  | HR6616 (Lo-16bits)
6618 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6619 |  |  |  | HR6618 (Lo-16bits)
6620 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6621 |  |  |  | HR6620 (Lo-16bits)
6622 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6623 |  |  |  | HR6622 (Lo-16bits)
6624 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6625 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6626 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6627 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6628 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6629 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6630 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6631 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6632 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6633 |  |  |  | HR6632 (Lo-16bits)
6634 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6635 |  |  |  | HR6634 (Lo-16bits)
6636 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6637 |  |  |  | HR6636 (Lo-16bits)
6638 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6639 |  |  |  | HR6638 (Lo-16bits)
6640 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6641 |  |  |  | HR6640 (Lo-16bits)
6642 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6643 |  |  |  | HR6642 (Lo-16bits)
6644 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6645 |  |  |  | HR6644 (Lo-16bits)
6646 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6647 |  |  |  | HR6646 (Lo-16bits)
6648 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6649 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6650 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6651 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6652 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6653 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6654 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6655 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6656 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6657 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6658 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6659 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6660 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6661 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6662 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6663 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6664 | CUB3:I2>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6665 | CUB3:I2>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6666 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6667 |  |  |  | HR6666 (Lo-16bits)
6668 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6669 |  |  |  | HR6668 (Lo-16bits)
6670 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6671 |  |  |  | HR6670 (Lo-16bits)
6672 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6673 |  |  |  | HR6672 (Lo-16bits)
6674 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6675 |  |  |  | HR6674 (Lo-16bits)
6676 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6677 |  |  |  | HR6676 (Lo-16bits)
6678 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6679 |  |  |  | HR6678 (Lo-16bits)
6680 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6681 |  |  |  | HR6680 (Lo-16bits)
6682 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6683 |  |  |  | HR6682 (Lo-16bits)
6684 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6685 |  |  |  | HR6684 (Lo-16bits)
6686 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6687 |  |  |  | HR6686 (Lo-16bits)
6688 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6689 |  |  |  | HR6688 (Lo-16bits)
6690 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6691 |  |  |  | HR6690 (Lo-16bits)
6692 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6693 |  |  |  | HR6692 (Lo-16bits)
6694 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6695 |  |  |  | HR6694 (Lo-16bits)
6696 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6697 |  |  |  | HR6696 (Lo-16bits)
6698 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6699 |  |  |  | HR6698 (Lo-16bits)
6700 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6701 |  |  |  | HR6700 (Lo-16bits)
6702 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6703 |  |  |  | HR6702 (Lo-16bits)
6704 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6705 |  |  |  | HR6704 (Lo-16bits)
6706 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6707 |  |  |  | HR6706 (Lo-16bits)
6708 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6709 |  |  |  | HR6708 (Lo-16bits)
6710 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6711 |  |  |  | HR6710 (Lo-16bits)
6712 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6713 |  |  |  | HR6712 (Lo-16bits)
6714 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6715 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6716 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6717 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6718 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6719 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6720 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6721 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6722 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6723 |  |  |  | HR6722 (Lo-16bits)
6724 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6725 |  |  |  | HR6724 (Lo-16bits)
6726 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6727 |  |  |  | HR6726 (Lo-16bits)
6728 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6729 |  |  |  | HR6728 (Lo-16bits)
6730 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6731 |  |  |  | HR6730 (Lo-16bits)
6732 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6733 |  |  |  | HR6732 (Lo-16bits)
6734 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6735 |  |  |  | HR6734 (Lo-16bits)
6736 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6737 |  |  |  | HR6736 (Lo-16bits)
6738 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6739 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6740 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6741 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6742 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6743 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6744 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6745 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6746 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6747 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6748 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6749 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6750 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6751 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6752 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6753 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6754 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6755 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6756 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6757 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6758 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6759 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6760 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6761 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6762 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6763 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6764 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6765 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6766 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6767 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6768 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6769 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6770 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6771 |  |  |  | HR6770 (Lo-16bits)
6772 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6773 |  |  |  | HR6772 (Lo-16bits)
6774 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6775 |  |  |  | HR6774 (Lo-16bits)
6776 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6777 |  |  |  | HR6776 (Lo-16bits)
6778 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6779 |  |  |  | HR6778 (Lo-16bits)
6780 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6781 |  |  |  | HR6780 (Lo-16bits)
6782 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6783 |  |  |  | HR6782 (Lo-16bits)
6784 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6785 |  |  |  | HR6784 (Lo-16bits)
6786 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6787 |  |  |  | HR6786 (Lo-16bits)
6788 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6789 |  |  |  | HR6788 (Lo-16bits)
6790 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6791 |  |  |  | HR6790 (Lo-16bits)
6792 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6793 |  |  |  | HR6792 (Lo-16bits)
6794 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6795 |  |  |  | HR6794 (Lo-16bits)
6796 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6797 |  |  |  | HR6796 (Lo-16bits)
6798 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6799 |  |  |  | HR6798 (Lo-16bits)
6800 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6801 |  |  |  | HR6800 (Lo-16bits)
6802 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6803 |  |  |  | HR6802 (Lo-16bits)
6804 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6805 |  |  |  | HR6804 (Lo-16bits)
6806 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6807 |  |  |  | HR6806 (Lo-16bits)
6808 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6809 |  |  |  | HR6808 (Lo-16bits)
6810 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6811 |  |  |  | HR6810 (Lo-16bits)
6812 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6813 |  |  |  | HR6812 (Lo-16bits)
6814 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6815 |  |  |  | HR6814 (Lo-16bits)
6816 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6817 |  |  |  | HR6816 (Lo-16bits)
6818 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6819 |  |  |  | HR6818 (Lo-16bits)
6820 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6821 |  |  |  | HR6820 (Lo-16bits)
6822 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6823 |  |  |  | HR6822 (Lo-16bits)
6824 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6825 |  |  |  | HR6824 (Lo-16bits)
6826 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6827 |  |  |  | HR6826 (Lo-16bits)
6828 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6829 |  |  |  | HR6828 (Lo-16bits)
6830 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6831 |  |  |  | HR6830 (Lo-16bits)
6832 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6833 |  |  |  | HR6832 (Lo-16bits)
6834 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6835 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6836 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6837 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6838 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6839 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6840 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6841 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6842 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6843 |  |  |  | HR6842 (Lo-16bits)
6844 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6845 |  |  |  | HR6844 (Lo-16bits)
6846 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6847 |  |  |  | HR6846 (Lo-16bits)
6848 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6849 |  |  |  | HR6848 (Lo-16bits)
6850 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6851 |  |  |  | HR6850 (Lo-16bits)
6852 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6853 |  |  |  | HR6852 (Lo-16bits)
6854 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6855 |  |  |  | HR6854 (Lo-16bits)
6856 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6857 |  |  |  | HR6856 (Lo-16bits)
6858 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6859 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6860 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6861 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6862 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6863 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6864 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6865 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6866 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6867 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6868 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6869 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6870 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6871 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6872 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6873 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6874 | CUB4:I2>>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6875 | CUB4:I2>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6876 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6877 |  |  |  | HR6876 (Lo-16bits)
6878 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6879 |  |  |  | HR6878 (Lo-16bits)
6880 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6881 |  |  |  | HR6880 (Lo-16bits)
6882 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6883 |  |  |  | HR6882 (Lo-16bits)
6884 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6885 |  |  |  | HR6884 (Lo-16bits)
6886 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6887 |  |  |  | HR6886 (Lo-16bits)
6888 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6889 |  |  |  | HR6888 (Lo-16bits)
6890 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6891 |  |  |  | HR6890 (Lo-16bits)
6892 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6893 |  |  |  | HR6892 (Lo-16bits)
6894 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6895 |  |  |  | HR6894 (Lo-16bits)
6896 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6897 |  |  |  | HR6896 (Lo-16bits)
6898 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6899 |  |  |  | HR6898 (Lo-16bits)
6900 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6901 |  |  |  | HR6900 (Lo-16bits)
6902 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6903 |  |  |  | HR6902 (Lo-16bits)
6904 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6905 |  |  |  | HR6904 (Lo-16bits)
6906 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6907 |  |  |  | HR6906 (Lo-16bits)
6908 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6909 |  |  |  | HR6908 (Lo-16bits)
6910 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6911 |  |  |  | HR6910 (Lo-16bits)
6912 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6913 |  |  |  | HR6912 (Lo-16bits)
6914 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6915 |  |  |  | HR6914 (Lo-16bits)
6916 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6917 |  |  |  | HR6916 (Lo-16bits)
6918 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6919 |  |  |  | HR6918 (Lo-16bits)
6920 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6921 |  |  |  | HR6920 (Lo-16bits)
6922 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6923 |  |  |  | HR6922 (Lo-16bits)
6924 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6925 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6926 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6927 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6928 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6929 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6930 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6931 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6932 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6933 |  |  |  | HR6932 (Lo-16bits)
6934 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6935 |  |  |  | HR6934 (Lo-16bits)
6936 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6937 |  |  |  | HR6936 (Lo-16bits)
6938 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6939 |  |  |  | HR6938 (Lo-16bits)
6940 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6941 |  |  |  | HR6940 (Lo-16bits)
6942 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6943 |  |  |  | HR6942 (Lo-16bits)
6944 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6945 |  |  |  | HR6944 (Lo-16bits)
6946 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6947 |  |  |  | HR6946 (Lo-16bits)
6948 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6949 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6950 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6951 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6952 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6953 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6954 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6955 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6956 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6957 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6958 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6959 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6960 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6961 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6962 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6963 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6964 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6965 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6966 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6967 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6968 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6969 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6970 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6971 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6972 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6973 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6974 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6975 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6976 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6977 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6978 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6979 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6980 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6981 |  |  |  | HR6980 (Lo-16bits)
6982 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6983 |  |  |  | HR6982 (Lo-16bits)
6984 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6985 |  |  |  | HR6984 (Lo-16bits)
6986 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6987 |  |  |  | HR6986 (Lo-16bits)
6988 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6989 |  |  |  | HR6988 (Lo-16bits)
6990 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6991 |  |  |  | HR6990 (Lo-16bits)
6992 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6993 |  |  |  | HR6992 (Lo-16bits)
6994 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6995 |  |  |  | HR6994 (Lo-16bits)
6996 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6997 |  |  |  | HR6996 (Lo-16bits)
6998 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6999 |  |  |  | HR6998 (Lo-16bits)
7000 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7001 |  |  |  | HR7000 (Lo-16bits)
7002 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7003 |  |  |  | HR7002 (Lo-16bits)
7004 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7005 |  |  |  | HR7004 (Lo-16bits)
7006 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7007 |  |  |  | HR7006 (Lo-16bits)
7008 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7009 |  |  |  | HR7008 (Lo-16bits)
7010 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7011 |  |  |  | HR7010 (Lo-16bits)
7012 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7013 |  |  |  | HR7012 (Lo-16bits)
7014 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7015 |  |  |  | HR7014 (Lo-16bits)
7016 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7017 |  |  |  | HR7016 (Lo-16bits)
7018 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7019 |  |  |  | HR7018 (Lo-16bits)
7020 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7021 |  |  |  | HR7020 (Lo-16bits)
7022 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7023 |  |  |  | HR7022 (Lo-16bits)
7024 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7025 |  |  |  | HR7024 (Lo-16bits)
7026 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7027 |  |  |  | HR7026 (Lo-16bits)
7028 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7029 |  |  |  | HR7028 (Lo-16bits)
7030 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7031 |  |  |  | HR7030 (Lo-16bits)
7032 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7033 |  |  |  | HR7032 (Lo-16bits)
7034 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7035 |  |  |  | HR7034 (Lo-16bits)
7036 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7037 |  |  |  | HR7036 (Lo-16bits)
7038 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7039 |  |  |  | HR7038 (Lo-16bits)
7040 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7041 |  |  |  | HR7040 (Lo-16bits)
7042 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7043 |  |  |  | HR7042 (Lo-16bits)
7044 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7045 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7046 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7047 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7048 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7049 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7050 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7051 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7052 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7053 |  |  |  | HR7052 (Lo-16bits)
7054 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7055 |  |  |  | HR7054 (Lo-16bits)
7056 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7057 |  |  |  | HR7056 (Lo-16bits)
7058 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7059 |  |  |  | HR7058 (Lo-16bits)
7060 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7061 |  |  |  | HR7060 (Lo-16bits)
7062 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7063 |  |  |  | HR7062 (Lo-16bits)
7064 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7065 |  |  |  | HR7064 (Lo-16bits)
7066 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7067 |  |  |  | HR7066 (Lo-16bits)
7068 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7069 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7070 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7071 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7072 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7073 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7074 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7075 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7076 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7077 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7078 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7079 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7080 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7081 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7082 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7083 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7084 | HOC1:Ih> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7085 | HOC1:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7086 |  |  |  | HR7085 (Lo-16bits)
7087 | HOC1:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7088 |  |  |  | HR7087 (Lo-16bits)
7089 | HOC1:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7090 |  |  |  | HR7089 (Lo-16bits)
7091 | HOC1:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7092 |  |  |  | HR7091 (Lo-16bits)
7093 | HOC1:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7094 |  |  |  | HR7093 (Lo-16bits)
7095 | HOC1:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7096 |  |  |  | HR7095 (Lo-16bits)
7097 | HOC1:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7098 |  |  |  | HR7097 (Lo-16bits)
7099 | HOC1:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7100 |  |  |  | HR7099 (Lo-16bits)
7101 | HOC1:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7102 |  |  |  | HR7101 (Lo-16bits)
7103 | HOC1:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7104 |  |  |  | HR7103 (Lo-16bits)
7105 | HOC2:Ih>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7106 | HOC2:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7107 |  |  |  | HR7106 (Lo-16bits)
7108 | HOC2:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7109 |  |  |  | HR7108 (Lo-16bits)
7110 | HOC2:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7111 |  |  |  | HR7110 (Lo-16bits)
7112 | HOC2:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7113 |  |  |  | HR7112 (Lo-16bits)
7114 | HOC2:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7115 |  |  |  | HR7114 (Lo-16bits)
7116 | HOC2:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7117 |  |  |  | HR7116 (Lo-16bits)
7118 | HOC2:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7119 |  |  |  | HR7118 (Lo-16bits)
7120 | HOC2:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7121 |  |  |  | HR7120 (Lo-16bits)
7122 | HOC2:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7123 |  |  |  | HR7122 (Lo-16bits)
7124 | HOC2:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7125 |  |  |  | HR7124 (Lo-16bits)
7126 | HOC3:Ih>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7127 | HOC3:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7128 |  |  |  | HR7127 (Lo-16bits)
7129 | HOC3:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7130 |  |  |  | HR7129 (Lo-16bits)
7131 | HOC3:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7132 |  |  |  | HR7131 (Lo-16bits)
7133 | HOC3:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7134 |  |  |  | HR7133 (Lo-16bits)
7135 | HOC3:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7136 |  |  |  | HR7135 (Lo-16bits)
7137 | HOC3:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7138 |  |  |  | HR7137 (Lo-16bits)
7139 | HOC3:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7140 |  |  |  | HR7139 (Lo-16bits)
7141 | HOC3:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7142 |  |  |  | HR7141 (Lo-16bits)
7143 | HOC3:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7144 |  |  |  | HR7143 (Lo-16bits)
7145 | HOC3:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7146 |  |  |  | HR7145 (Lo-16bits)
7147 | HOC4:Ih>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7148 | HOC4:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7149 |  |  |  | HR7148 (Lo-16bits)
7150 | HOC4:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7151 |  |  |  | HR7150 (Lo-16bits)
7152 | HOC4:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7153 |  |  |  | HR7152 (Lo-16bits)
7154 | HOC4:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7155 |  |  |  | HR7154 (Lo-16bits)
7156 | HOC4:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7157 |  |  |  | HR7156 (Lo-16bits)
7158 | HOC4:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7159 |  |  |  | HR7158 (Lo-16bits)
7160 | HOC4:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7161 |  |  |  | HR7160 (Lo-16bits)
7162 | HOC4:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7163 |  |  |  | HR7162 (Lo-16bits)
7164 | HOC4:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7165 |  |  |  | HR7164 (Lo-16bits)
7166 | HOC4:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7167 |  |  |  | HR7166 (Lo-16bits)
7168 | CLP1:CLP condition | R | 1 | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
7169 | CBF1:CBFP condition | R | 1 | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
7170 | MST1:Motor is now | R | 1 | 0=Stopped;1=Starting;2=Running;3=Stalled
7171 | TRF1:Transformer is now | R | 1 | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
7172 | DIF1:Idx> condition | R | 2 | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On (Hi-16bits)
7173 |  |  |  | HR7172 (Lo-16bits)
7174 | DIF1:REFHV> condition | R | 2 | 0b=HV REF Blocked;1b=HV REF Trip (Hi-16bits)
7175 |  |  |  | HR7174 (Lo-16bits)
7176 | DIF1:REFLV> condition | R | 2 | 0b=LV REF Blocked;1b=LV REF Trip (Hi-16bits)
7177 |  |  |  | HR7176 (Lo-16bits)
7178 | DIF1:L1 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7179 | DIF1:L2 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7180 | DIF1:L3 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7181 | REF1:I0d> condition | R | 1 | 0=Normal;1=Trip;2=Blocked
7182 | TOLT1:TT> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7183 | TOLT1:TT> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7184 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7185 | TOLT1:TT> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7186 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7187 | TOLT1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7188 | TOLT1:Temp C or F deg | RW | 1 | 0=C;1=F
7189 | TOLT1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7190 | TOLT1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7191 | TOLT1:TT> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7192 |  |  |  | HR7191 (Lo-16bits)
7193 | TOLF1:TF> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7194 | TOLF1:TF> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7195 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7196 | TOLF1:TF> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7197 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7198 | TOLF1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7199 | TOLF1:Temp C or F deg | RW | 1 | 0=C;1=F
7200 | TOLF1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7201 | TOLF1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7202 | TOLF1:Set or Estimate tau (t const) | RW | 1 | 0=Set;1=Estimate
7203 | TOLF1:TF> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7204 |  |  |  | HR7203 (Lo-16bits)
7205 | TOLM1:TM> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7206 | TOLM1:TM> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7207 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7208 | TOLM1:TM> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7209 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7210 | TOLM1:Motor status | R | 1 | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
7211 | TOLM1:Temp C or F deg | RW | 1 | 0=C;1=F
7212 | TOLM1:NPS Biasing in use | RW | 1 | 0=No NPS biasing;1=NPS Biasing in use
7213 | TOLM1:Time constants | RW | 1 | 0=Single;1=Multiple
7214 | TOLM1:Estimate Short TC and timings | RW | 1 | 0=Set manually;1=Estimate (on-line)
7215 | TOLM1:T const dyn. balancing | RW | 1 | 0=Fixed;1=Dynamic
7216 | TOLM1:Dev.Temp (tmax) | RW | 1 | 0=A;1=B;2=F;3=H;4=Manual set
7217 | TOLM1:Amb. T Selection | RW | 1 | 0=Manual set;1=RTD
7218 | TOLM1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7219 | TOLM1:TM> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7220 |  |  |  | HR7219 (Lo-16bits)
7221 | LCR1:ISt> condition | R | 1 | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
7222 | FSP1:N> condition | R | 1 | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
7223 | NUC1:I< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7224 | MJP1:Im> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7225 | OV1:U> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7226 | OV1:U> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7227 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7228 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7229 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7230 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7231 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7232 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7233 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7234 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7235 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7236 |  |  |  | HR7235 (Lo-16bits)
7237 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7238 |  |  |  | HR7237 (Lo-16bits)
7239 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7240 |  |  |  | HR7239 (Lo-16bits)
7241 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7242 |  |  |  | HR7241 (Lo-16bits)
7243 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7244 |  |  |  | HR7243 (Lo-16bits)
7245 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7246 |  |  |  | HR7245 (Lo-16bits)
7247 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7248 |  |  |  | HR7247 (Lo-16bits)
7249 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7250 |  |  |  | HR7249 (Lo-16bits)
7251 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7252 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7253 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7254 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7255 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7256 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7257 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7258 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7259 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7260 |  |  |  | HR7259 (Lo-16bits)
7261 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7262 |  |  |  | HR7261 (Lo-16bits)
7263 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7264 |  |  |  | HR7263 (Lo-16bits)
7265 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7266 |  |  |  | HR7265 (Lo-16bits)
7267 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7268 |  |  |  | HR7267 (Lo-16bits)
7269 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7270 |  |  |  | HR7269 (Lo-16bits)
7271 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7272 |  |  |  | HR7271 (Lo-16bits)
7273 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7274 |  |  |  | HR7273 (Lo-16bits)
7275 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7276 |  |  |  | HR7275 (Lo-16bits)
7277 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7278 |  |  |  | HR7277 (Lo-16bits)
7279 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7280 |  |  |  | HR7279 (Lo-16bits)
7281 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7282 |  |  |  | HR7281 (Lo-16bits)
7283 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7284 |  |  |  | HR7283 (Lo-16bits)
7285 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7286 |  |  |  | HR7285 (Lo-16bits)
7287 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7288 |  |  |  | HR7287 (Lo-16bits)
7289 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7290 |  |  |  | HR7289 (Lo-16bits)
7291 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7292 |  |  |  | HR7291 (Lo-16bits)
7293 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7294 |  |  |  | HR7293 (Lo-16bits)
7295 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7296 |  |  |  | HR7295 (Lo-16bits)
7297 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7298 |  |  |  | HR7297 (Lo-16bits)
7299 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7300 |  |  |  | HR7299 (Lo-16bits)
7301 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7302 |  |  |  | HR7301 (Lo-16bits)
7303 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7304 |  |  |  | HR7303 (Lo-16bits)
7305 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7306 |  |  |  | HR7305 (Lo-16bits)
7307 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7308 |  |  |  | HR7307 (Lo-16bits)
7309 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7310 |  |  |  | HR7309 (Lo-16bits)
7311 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7312 |  |  |  | HR7311 (Lo-16bits)
7313 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7314 |  |  |  | HR7313 (Lo-16bits)
7315 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7316 |  |  |  | HR7315 (Lo-16bits)
7317 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7318 |  |  |  | HR7317 (Lo-16bits)
7319 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7320 |  |  |  | HR7319 (Lo-16bits)
7321 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7322 |  |  |  | HR7321 (Lo-16bits)
7323 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7324 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7325 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7326 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7327 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7328 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7329 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7330 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7331 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7332 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7333 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7334 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7335 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7336 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7337 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7338 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7339 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7340 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7341 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7342 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7343 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7344 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7345 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7346 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7347 | OV2:U>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7348 | OV2:U>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7349 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7350 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7351 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7352 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7353 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7354 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7355 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7356 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7357 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7358 |  |  |  | HR7357 (Lo-16bits)
7359 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7360 |  |  |  | HR7359 (Lo-16bits)
7361 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7362 |  |  |  | HR7361 (Lo-16bits)
7363 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7364 |  |  |  | HR7363 (Lo-16bits)
7365 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7366 |  |  |  | HR7365 (Lo-16bits)
7367 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7368 |  |  |  | HR7367 (Lo-16bits)
7369 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7370 |  |  |  | HR7369 (Lo-16bits)
7371 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7372 |  |  |  | HR7371 (Lo-16bits)
7373 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7374 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7375 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7376 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7377 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7378 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7379 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7380 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7381 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7382 |  |  |  | HR7381 (Lo-16bits)
7383 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7384 |  |  |  | HR7383 (Lo-16bits)
7385 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7386 |  |  |  | HR7385 (Lo-16bits)
7387 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7388 |  |  |  | HR7387 (Lo-16bits)
7389 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7390 |  |  |  | HR7389 (Lo-16bits)
7391 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7392 |  |  |  | HR7391 (Lo-16bits)
7393 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7394 |  |  |  | HR7393 (Lo-16bits)
7395 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7396 |  |  |  | HR7395 (Lo-16bits)
7397 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7398 |  |  |  | HR7397 (Lo-16bits)
7399 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7400 |  |  |  | HR7399 (Lo-16bits)
7401 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7402 |  |  |  | HR7401 (Lo-16bits)
7403 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7404 |  |  |  | HR7403 (Lo-16bits)
7405 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7406 |  |  |  | HR7405 (Lo-16bits)
7407 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7408 |  |  |  | HR7407 (Lo-16bits)
7409 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7410 |  |  |  | HR7409 (Lo-16bits)
7411 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7412 |  |  |  | HR7411 (Lo-16bits)
7413 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7414 |  |  |  | HR7413 (Lo-16bits)
7415 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7416 |  |  |  | HR7415 (Lo-16bits)
7417 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7418 |  |  |  | HR7417 (Lo-16bits)
7419 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7420 |  |  |  | HR7419 (Lo-16bits)
7421 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7422 |  |  |  | HR7421 (Lo-16bits)
7423 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7424 |  |  |  | HR7423 (Lo-16bits)
7425 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7426 |  |  |  | HR7425 (Lo-16bits)
7427 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7428 |  |  |  | HR7427 (Lo-16bits)
7429 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7430 |  |  |  | HR7429 (Lo-16bits)
7431 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7432 |  |  |  | HR7431 (Lo-16bits)
7433 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7434 |  |  |  | HR7433 (Lo-16bits)
7435 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7436 |  |  |  | HR7435 (Lo-16bits)
7437 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7438 |  |  |  | HR7437 (Lo-16bits)
7439 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7440 |  |  |  | HR7439 (Lo-16bits)
7441 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7442 |  |  |  | HR7441 (Lo-16bits)
7443 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7444 |  |  |  | HR7443 (Lo-16bits)
7445 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7446 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7447 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7448 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7449 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7450 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7451 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7452 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7453 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7454 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7455 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7456 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7457 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7458 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7459 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7460 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7461 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7462 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7463 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7464 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7465 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7466 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7467 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7468 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7469 | OV3:U>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7470 | OV3:U>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7471 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7472 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7473 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7474 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7475 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7476 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7477 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7478 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7479 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7480 |  |  |  | HR7479 (Lo-16bits)
7481 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7482 |  |  |  | HR7481 (Lo-16bits)
7483 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7484 |  |  |  | HR7483 (Lo-16bits)
7485 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7486 |  |  |  | HR7485 (Lo-16bits)
7487 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7488 |  |  |  | HR7487 (Lo-16bits)
7489 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7490 |  |  |  | HR7489 (Lo-16bits)
7491 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7492 |  |  |  | HR7491 (Lo-16bits)
7493 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7494 |  |  |  | HR7493 (Lo-16bits)
7495 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7496 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7497 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7498 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7499 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7500 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7501 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7502 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7503 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7504 |  |  |  | HR7503 (Lo-16bits)
7505 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7506 |  |  |  | HR7505 (Lo-16bits)
7507 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7508 |  |  |  | HR7507 (Lo-16bits)
7509 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7510 |  |  |  | HR7509 (Lo-16bits)
7511 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7512 |  |  |  | HR7511 (Lo-16bits)
7513 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7514 |  |  |  | HR7513 (Lo-16bits)
7515 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7516 |  |  |  | HR7515 (Lo-16bits)
7517 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7518 |  |  |  | HR7517 (Lo-16bits)
7519 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7520 |  |  |  | HR7519 (Lo-16bits)
7521 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7522 |  |  |  | HR7521 (Lo-16bits)
7523 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7524 |  |  |  | HR7523 (Lo-16bits)
7525 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7526 |  |  |  | HR7525 (Lo-16bits)
7527 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7528 |  |  |  | HR7527 (Lo-16bits)
7529 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7530 |  |  |  | HR7529 (Lo-16bits)
7531 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7532 |  |  |  | HR7531 (Lo-16bits)
7533 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7534 |  |  |  | HR7533 (Lo-16bits)
7535 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7536 |  |  |  | HR7535 (Lo-16bits)
7537 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7538 |  |  |  | HR7537 (Lo-16bits)
7539 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7540 |  |  |  | HR7539 (Lo-16bits)
7541 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7542 |  |  |  | HR7541 (Lo-16bits)
7543 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7544 |  |  |  | HR7543 (Lo-16bits)
7545 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7546 |  |  |  | HR7545 (Lo-16bits)
7547 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7548 |  |  |  | HR7547 (Lo-16bits)
7549 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7550 |  |  |  | HR7549 (Lo-16bits)
7551 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7552 |  |  |  | HR7551 (Lo-16bits)
7553 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7554 |  |  |  | HR7553 (Lo-16bits)
7555 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7556 |  |  |  | HR7555 (Lo-16bits)
7557 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7558 |  |  |  | HR7557 (Lo-16bits)
7559 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7560 |  |  |  | HR7559 (Lo-16bits)
7561 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7562 |  |  |  | HR7561 (Lo-16bits)
7563 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7564 |  |  |  | HR7563 (Lo-16bits)
7565 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7566 |  |  |  | HR7565 (Lo-16bits)
7567 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7568 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7569 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7570 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7571 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7572 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7573 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7574 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7575 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7576 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7577 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7578 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7579 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7580 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7581 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7582 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7583 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7584 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7585 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7586 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7587 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7588 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7589 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7590 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7591 | OV4:U>>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7592 | OV4:U>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7593 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7594 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7595 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7596 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7597 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7598 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7599 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7600 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7601 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7602 |  |  |  | HR7601 (Lo-16bits)
7603 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7604 |  |  |  | HR7603 (Lo-16bits)
7605 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7606 |  |  |  | HR7605 (Lo-16bits)
7607 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7608 |  |  |  | HR7607 (Lo-16bits)
7609 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7610 |  |  |  | HR7609 (Lo-16bits)
7611 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7612 |  |  |  | HR7611 (Lo-16bits)
7613 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7614 |  |  |  | HR7613 (Lo-16bits)
7615 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7616 |  |  |  | HR7615 (Lo-16bits)
7617 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7618 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7619 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7620 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7621 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7622 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7623 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7624 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7625 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7626 |  |  |  | HR7625 (Lo-16bits)
7627 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7628 |  |  |  | HR7627 (Lo-16bits)
7629 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7630 |  |  |  | HR7629 (Lo-16bits)
7631 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7632 |  |  |  | HR7631 (Lo-16bits)
7633 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7634 |  |  |  | HR7633 (Lo-16bits)
7635 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7636 |  |  |  | HR7635 (Lo-16bits)
7637 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7638 |  |  |  | HR7637 (Lo-16bits)
7639 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7640 |  |  |  | HR7639 (Lo-16bits)
7641 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7642 |  |  |  | HR7641 (Lo-16bits)
7643 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7644 |  |  |  | HR7643 (Lo-16bits)
7645 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7646 |  |  |  | HR7645 (Lo-16bits)
7647 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7648 |  |  |  | HR7647 (Lo-16bits)
7649 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7650 |  |  |  | HR7649 (Lo-16bits)
7651 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7652 |  |  |  | HR7651 (Lo-16bits)
7653 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7654 |  |  |  | HR7653 (Lo-16bits)
7655 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7656 |  |  |  | HR7655 (Lo-16bits)
7657 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7658 |  |  |  | HR7657 (Lo-16bits)
7659 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7660 |  |  |  | HR7659 (Lo-16bits)
7661 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7662 |  |  |  | HR7661 (Lo-16bits)
7663 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7664 |  |  |  | HR7663 (Lo-16bits)
7665 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7666 |  |  |  | HR7665 (Lo-16bits)
7667 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7668 |  |  |  | HR7667 (Lo-16bits)
7669 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7670 |  |  |  | HR7669 (Lo-16bits)
7671 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7672 |  |  |  | HR7671 (Lo-16bits)
7673 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7674 |  |  |  | HR7673 (Lo-16bits)
7675 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7676 |  |  |  | HR7675 (Lo-16bits)
7677 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7678 |  |  |  | HR7677 (Lo-16bits)
7679 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7680 |  |  |  | HR7679 (Lo-16bits)
7681 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7682 |  |  |  | HR7681 (Lo-16bits)
7683 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7684 |  |  |  | HR7683 (Lo-16bits)
7685 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7686 |  |  |  | HR7685 (Lo-16bits)
7687 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7688 |  |  |  | HR7687 (Lo-16bits)
7689 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7690 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7691 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7692 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7693 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7694 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7695 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7696 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7697 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7698 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7699 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7700 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7701 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7702 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7703 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7704 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7705 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7706 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7707 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7708 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7709 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7710 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7711 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7712 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7713 | UV1:U< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7714 | UV1:U< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7715 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7716 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7717 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7718 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7719 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7720 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7721 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7722 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7723 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7724 |  |  |  | HR7723 (Lo-16bits)
7725 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7726 |  |  |  | HR7725 (Lo-16bits)
7727 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7728 |  |  |  | HR7727 (Lo-16bits)
7729 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7730 |  |  |  | HR7729 (Lo-16bits)
7731 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7732 |  |  |  | HR7731 (Lo-16bits)
7733 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7734 |  |  |  | HR7733 (Lo-16bits)
7735 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7736 |  |  |  | HR7735 (Lo-16bits)
7737 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7738 |  |  |  | HR7737 (Lo-16bits)
7739 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7740 |  |  |  | HR7739 (Lo-16bits)
7741 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7742 |  |  |  | HR7741 (Lo-16bits)
7743 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7744 |  |  |  | HR7743 (Lo-16bits)
7745 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7746 |  |  |  | HR7745 (Lo-16bits)
7747 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7748 |  |  |  | HR7747 (Lo-16bits)
7749 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7750 |  |  |  | HR7749 (Lo-16bits)
7751 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7752 |  |  |  | HR7751 (Lo-16bits)
7753 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7754 |  |  |  | HR7753 (Lo-16bits)
7755 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7756 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7757 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7758 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7759 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7760 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7761 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7762 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7763 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7764 |  |  |  | HR7763 (Lo-16bits)
7765 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7766 |  |  |  | HR7765 (Lo-16bits)
7767 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7768 |  |  |  | HR7767 (Lo-16bits)
7769 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7770 |  |  |  | HR7769 (Lo-16bits)
7771 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7772 |  |  |  | HR7771 (Lo-16bits)
7773 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7774 |  |  |  | HR7773 (Lo-16bits)
7775 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7776 |  |  |  | HR7775 (Lo-16bits)
7777 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7778 |  |  |  | HR7777 (Lo-16bits)
7779 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7780 |  |  |  | HR7779 (Lo-16bits)
7781 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7782 |  |  |  | HR7781 (Lo-16bits)
7783 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7784 |  |  |  | HR7783 (Lo-16bits)
7785 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7786 |  |  |  | HR7785 (Lo-16bits)
7787 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7788 |  |  |  | HR7787 (Lo-16bits)
7789 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7790 |  |  |  | HR7789 (Lo-16bits)
7791 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7792 |  |  |  | HR7791 (Lo-16bits)
7793 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7794 |  |  |  | HR7793 (Lo-16bits)
7795 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7796 |  |  |  | HR7795 (Lo-16bits)
7797 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7798 |  |  |  | HR7797 (Lo-16bits)
7799 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7800 |  |  |  | HR7799 (Lo-16bits)
7801 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7802 |  |  |  | HR7801 (Lo-16bits)
7803 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7804 |  |  |  | HR7803 (Lo-16bits)
7805 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7806 |  |  |  | HR7805 (Lo-16bits)
7807 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7808 |  |  |  | HR7807 (Lo-16bits)
7809 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7810 |  |  |  | HR7809 (Lo-16bits)
7811 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7812 |  |  |  | HR7811 (Lo-16bits)
7813 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7814 |  |  |  | HR7813 (Lo-16bits)
7815 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7816 |  |  |  | HR7815 (Lo-16bits)
7817 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7818 |  |  |  | HR7817 (Lo-16bits)
7819 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7820 |  |  |  | HR7819 (Lo-16bits)
7821 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7822 |  |  |  | HR7821 (Lo-16bits)
7823 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7824 |  |  |  | HR7823 (Lo-16bits)
7825 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7826 |  |  |  | HR7825 (Lo-16bits)
7827 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7828 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7829 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7830 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7831 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7832 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7833 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7834 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7835 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7836 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7837 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7838 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7839 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7840 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7841 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7842 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7843 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7844 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7845 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7846 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7847 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7848 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7849 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7850 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7851 | UV2:U<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7852 | UV2:U<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7853 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7854 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7855 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7856 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7857 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7858 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7859 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7860 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7861 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7862 |  |  |  | HR7861 (Lo-16bits)
7863 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7864 |  |  |  | HR7863 (Lo-16bits)
7865 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7866 |  |  |  | HR7865 (Lo-16bits)
7867 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7868 |  |  |  | HR7867 (Lo-16bits)
7869 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7870 |  |  |  | HR7869 (Lo-16bits)
7871 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7872 |  |  |  | HR7871 (Lo-16bits)
7873 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7874 |  |  |  | HR7873 (Lo-16bits)
7875 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7876 |  |  |  | HR7875 (Lo-16bits)
7877 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7878 |  |  |  | HR7877 (Lo-16bits)
7879 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7880 |  |  |  | HR7879 (Lo-16bits)
7881 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7882 |  |  |  | HR7881 (Lo-16bits)
7883 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7884 |  |  |  | HR7883 (Lo-16bits)
7885 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7886 |  |  |  | HR7885 (Lo-16bits)
7887 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7888 |  |  |  | HR7887 (Lo-16bits)
7889 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7890 |  |  |  | HR7889 (Lo-16bits)
7891 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7892 |  |  |  | HR7891 (Lo-16bits)
7893 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7894 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7895 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7896 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7897 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7898 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7899 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7900 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7901 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7902 |  |  |  | HR7901 (Lo-16bits)
7903 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7904 |  |  |  | HR7903 (Lo-16bits)
7905 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7906 |  |  |  | HR7905 (Lo-16bits)
7907 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7908 |  |  |  | HR7907 (Lo-16bits)
7909 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7910 |  |  |  | HR7909 (Lo-16bits)
7911 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7912 |  |  |  | HR7911 (Lo-16bits)
7913 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7914 |  |  |  | HR7913 (Lo-16bits)
7915 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7916 |  |  |  | HR7915 (Lo-16bits)
7917 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7918 |  |  |  | HR7917 (Lo-16bits)
7919 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7920 |  |  |  | HR7919 (Lo-16bits)
7921 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7922 |  |  |  | HR7921 (Lo-16bits)
7923 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7924 |  |  |  | HR7923 (Lo-16bits)
7925 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7926 |  |  |  | HR7925 (Lo-16bits)
7927 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7928 |  |  |  | HR7927 (Lo-16bits)
7929 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7930 |  |  |  | HR7929 (Lo-16bits)
7931 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7932 |  |  |  | HR7931 (Lo-16bits)
7933 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7934 |  |  |  | HR7933 (Lo-16bits)
7935 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7936 |  |  |  | HR7935 (Lo-16bits)
7937 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7938 |  |  |  | HR7937 (Lo-16bits)
7939 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7940 |  |  |  | HR7939 (Lo-16bits)
7941 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7942 |  |  |  | HR7941 (Lo-16bits)
7943 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7944 |  |  |  | HR7943 (Lo-16bits)
7945 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7946 |  |  |  | HR7945 (Lo-16bits)
7947 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7948 |  |  |  | HR7947 (Lo-16bits)
7949 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7950 |  |  |  | HR7949 (Lo-16bits)
7951 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7952 |  |  |  | HR7951 (Lo-16bits)
7953 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7954 |  |  |  | HR7953 (Lo-16bits)
7955 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7956 |  |  |  | HR7955 (Lo-16bits)
7957 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7958 |  |  |  | HR7957 (Lo-16bits)
7959 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7960 |  |  |  | HR7959 (Lo-16bits)
7961 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7962 |  |  |  | HR7961 (Lo-16bits)
7963 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7964 |  |  |  | HR7963 (Lo-16bits)
7965 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7966 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7967 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7968 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7969 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7970 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7971 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7972 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7973 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7974 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7975 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7976 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7977 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7978 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7979 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7980 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7981 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7982 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7983 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7984 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7985 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7986 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7987 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7988 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7989 | UV3:U<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7990 | UV3:U<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7991 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7992 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7993 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7994 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7995 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7996 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7997 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7998 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7999 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8000 |  |  |  | HR7999 (Lo-16bits)
8001 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8002 |  |  |  | HR8001 (Lo-16bits)
8003 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8004 |  |  |  | HR8003 (Lo-16bits)
8005 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8006 |  |  |  | HR8005 (Lo-16bits)
8007 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8008 |  |  |  | HR8007 (Lo-16bits)
8009 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8010 |  |  |  | HR8009 (Lo-16bits)
8011 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8012 |  |  |  | HR8011 (Lo-16bits)
8013 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8014 |  |  |  | HR8013 (Lo-16bits)
8015 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8016 |  |  |  | HR8015 (Lo-16bits)
8017 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8018 |  |  |  | HR8017 (Lo-16bits)
8019 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8020 |  |  |  | HR8019 (Lo-16bits)
8021 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8022 |  |  |  | HR8021 (Lo-16bits)
8023 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8024 |  |  |  | HR8023 (Lo-16bits)
8025 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8026 |  |  |  | HR8025 (Lo-16bits)
8027 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8028 |  |  |  | HR8027 (Lo-16bits)
8029 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8030 |  |  |  | HR8029 (Lo-16bits)
8031 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8032 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8033 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8034 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8035 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8036 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8037 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8038 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8039 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8040 |  |  |  | HR8039 (Lo-16bits)
8041 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8042 |  |  |  | HR8041 (Lo-16bits)
8043 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8044 |  |  |  | HR8043 (Lo-16bits)
8045 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8046 |  |  |  | HR8045 (Lo-16bits)
8047 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8048 |  |  |  | HR8047 (Lo-16bits)
8049 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8050 |  |  |  | HR8049 (Lo-16bits)
8051 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8052 |  |  |  | HR8051 (Lo-16bits)
8053 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8054 |  |  |  | HR8053 (Lo-16bits)
8055 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8056 |  |  |  | HR8055 (Lo-16bits)
8057 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8058 |  |  |  | HR8057 (Lo-16bits)
8059 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8060 |  |  |  | HR8059 (Lo-16bits)
8061 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8062 |  |  |  | HR8061 (Lo-16bits)
8063 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8064 |  |  |  | HR8063 (Lo-16bits)
8065 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8066 |  |  |  | HR8065 (Lo-16bits)
8067 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8068 |  |  |  | HR8067 (Lo-16bits)
8069 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8070 |  |  |  | HR8069 (Lo-16bits)
8071 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8072 |  |  |  | HR8071 (Lo-16bits)
8073 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8074 |  |  |  | HR8073 (Lo-16bits)
8075 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8076 |  |  |  | HR8075 (Lo-16bits)
8077 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8078 |  |  |  | HR8077 (Lo-16bits)
8079 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8080 |  |  |  | HR8079 (Lo-16bits)
8081 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8082 |  |  |  | HR8081 (Lo-16bits)
8083 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8084 |  |  |  | HR8083 (Lo-16bits)
8085 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8086 |  |  |  | HR8085 (Lo-16bits)
8087 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8088 |  |  |  | HR8087 (Lo-16bits)
8089 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8090 |  |  |  | HR8089 (Lo-16bits)
8091 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8092 |  |  |  | HR8091 (Lo-16bits)
8093 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8094 |  |  |  | HR8093 (Lo-16bits)
8095 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8096 |  |  |  | HR8095 (Lo-16bits)
8097 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8098 |  |  |  | HR8097 (Lo-16bits)
8099 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8100 |  |  |  | HR8099 (Lo-16bits)
8101 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8102 |  |  |  | HR8101 (Lo-16bits)
8103 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8104 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8105 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8106 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8107 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8108 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8109 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8110 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8111 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8112 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8113 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8114 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8115 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8116 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8117 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8118 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8119 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8120 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8121 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8122 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8123 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8124 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8125 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8126 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8127 | UV4:U<<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
8128 | UV4:U<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
8129 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8130 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8131 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8132 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8133 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8134 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8135 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8136 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8137 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8138 |  |  |  | HR8137 (Lo-16bits)
8139 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8140 |  |  |  | HR8139 (Lo-16bits)
8141 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8142 |  |  |  | HR8141 (Lo-16bits)
8143 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8144 |  |  |  | HR8143 (Lo-16bits)
8145 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8146 |  |  |  | HR8145 (Lo-16bits)
8147 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8148 |  |  |  | HR8147 (Lo-16bits)
8149 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8150 |  |  |  | HR8149 (Lo-16bits)
8151 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8152 |  |  |  | HR8151 (Lo-16bits)
8153 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8154 |  |  |  | HR8153 (Lo-16bits)
8155 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8156 |  |  |  | HR8155 (Lo-16bits)
8157 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8158 |  |  |  | HR8157 (Lo-16bits)
8159 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8160 |  |  |  | HR8159 (Lo-16bits)
8161 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8162 |  |  |  | HR8161 (Lo-16bits)
8163 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8164 |  |  |  | HR8163 (Lo-16bits)
8165 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8166 |  |  |  | HR8165 (Lo-16bits)
8167 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8168 |  |  |  | HR8167 (Lo-16bits)
8169 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8170 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8171 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8172 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8173 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8174 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8175 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8176 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8177 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8178 |  |  |  | HR8177 (Lo-16bits)
8179 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8180 |  |  |  | HR8179 (Lo-16bits)
8181 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8182 |  |  |  | HR8181 (Lo-16bits)
8183 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8184 |  |  |  | HR8183 (Lo-16bits)
8185 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8186 |  |  |  | HR8185 (Lo-16bits)
8187 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8188 |  |  |  | HR8187 (Lo-16bits)
8189 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8190 |  |  |  | HR8189 (Lo-16bits)
8191 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8192 |  |  |  | HR8191 (Lo-16bits)
8193 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8194 |  |  |  | HR8193 (Lo-16bits)
8195 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8196 |  |  |  | HR8195 (Lo-16bits)
8197 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8198 |  |  |  | HR8197 (Lo-16bits)
8199 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8200 |  |  |  | HR8199 (Lo-16bits)
8201 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8202 |  |  |  | HR8201 (Lo-16bits)
8203 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8204 |  |  |  | HR8203 (Lo-16bits)
8205 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8206 |  |  |  | HR8205 (Lo-16bits)
8207 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8208 |  |  |  | HR8207 (Lo-16bits)
8209 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8210 |  |  |  | HR8209 (Lo-16bits)
8211 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8212 |  |  |  | HR8211 (Lo-16bits)
8213 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8214 |  |  |  | HR8213 (Lo-16bits)
8215 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8216 |  |  |  | HR8215 (Lo-16bits)
8217 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8218 |  |  |  | HR8217 (Lo-16bits)
8219 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8220 |  |  |  | HR8219 (Lo-16bits)
8221 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8222 |  |  |  | HR8221 (Lo-16bits)
8223 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8224 |  |  |  | HR8223 (Lo-16bits)
8225 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8226 |  |  |  | HR8225 (Lo-16bits)
8227 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8228 |  |  |  | HR8227 (Lo-16bits)
8229 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8230 |  |  |  | HR8229 (Lo-16bits)
8231 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8232 |  |  |  | HR8231 (Lo-16bits)
8233 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8234 |  |  |  | HR8233 (Lo-16bits)
8235 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8236 |  |  |  | HR8235 (Lo-16bits)
8237 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8238 |  |  |  | HR8237 (Lo-16bits)
8239 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8240 |  |  |  | HR8239 (Lo-16bits)
8241 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8242 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8243 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8244 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8245 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8246 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8247 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8248 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8249 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8250 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8251 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8252 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8253 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8254 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8255 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8256 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8257 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8258 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8259 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8260 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8261 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8262 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8263 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8264 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8265 | NOV1:U0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8266 | NOV1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8267 | NOV2:U0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8268 | NOV2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8269 | NOV3:U0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8270 | NOV3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8271 | NOV4:U0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8272 | NOV4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8273 | VUB1:U1/2 >/< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8274 | VUB1:U1/2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8275 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8276 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8277 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8278 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8279 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8280 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8281 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8282 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8283 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8284 |  |  |  | HR8283 (Lo-16bits)
8285 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8286 |  |  |  | HR8285 (Lo-16bits)
8287 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8288 |  |  |  | HR8287 (Lo-16bits)
8289 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8290 |  |  |  | HR8289 (Lo-16bits)
8291 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8292 |  |  |  | HR8291 (Lo-16bits)
8293 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8294 |  |  |  | HR8293 (Lo-16bits)
8295 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8296 |  |  |  | HR8295 (Lo-16bits)
8297 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8298 |  |  |  | HR8297 (Lo-16bits)
8299 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8300 |  |  |  | HR8299 (Lo-16bits)
8301 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8302 |  |  |  | HR8301 (Lo-16bits)
8303 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8304 |  |  |  | HR8303 (Lo-16bits)
8305 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8306 |  |  |  | HR8305 (Lo-16bits)
8307 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8308 |  |  |  | HR8307 (Lo-16bits)
8309 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8310 |  |  |  | HR8309 (Lo-16bits)
8311 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8312 |  |  |  | HR8311 (Lo-16bits)
8313 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8314 |  |  |  | HR8313 (Lo-16bits)
8315 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8316 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8317 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8318 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8319 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8320 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8321 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8322 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8323 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8324 |  |  |  | HR8323 (Lo-16bits)
8325 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8326 |  |  |  | HR8325 (Lo-16bits)
8327 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8328 |  |  |  | HR8327 (Lo-16bits)
8329 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8330 |  |  |  | HR8329 (Lo-16bits)
8331 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8332 |  |  |  | HR8331 (Lo-16bits)
8333 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8334 |  |  |  | HR8333 (Lo-16bits)
8335 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8336 |  |  |  | HR8335 (Lo-16bits)
8337 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8338 |  |  |  | HR8337 (Lo-16bits)
8339 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8340 |  |  |  | HR8339 (Lo-16bits)
8341 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8342 |  |  |  | HR8341 (Lo-16bits)
8343 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8344 |  |  |  | HR8343 (Lo-16bits)
8345 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8346 |  |  |  | HR8345 (Lo-16bits)
8347 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8348 |  |  |  | HR8347 (Lo-16bits)
8349 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8350 |  |  |  | HR8349 (Lo-16bits)
8351 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8352 |  |  |  | HR8351 (Lo-16bits)
8353 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8354 |  |  |  | HR8353 (Lo-16bits)
8355 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8356 |  |  |  | HR8355 (Lo-16bits)
8357 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8358 |  |  |  | HR8357 (Lo-16bits)
8359 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8360 |  |  |  | HR8359 (Lo-16bits)
8361 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8362 |  |  |  | HR8361 (Lo-16bits)
8363 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8364 |  |  |  | HR8363 (Lo-16bits)
8365 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8366 |  |  |  | HR8365 (Lo-16bits)
8367 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8368 |  |  |  | HR8367 (Lo-16bits)
8369 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8370 |  |  |  | HR8369 (Lo-16bits)
8371 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8372 |  |  |  | HR8371 (Lo-16bits)
8373 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8374 |  |  |  | HR8373 (Lo-16bits)
8375 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8376 |  |  |  | HR8375 (Lo-16bits)
8377 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8378 |  |  |  | HR8377 (Lo-16bits)
8379 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8380 |  |  |  | HR8379 (Lo-16bits)
8381 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8382 |  |  |  | HR8381 (Lo-16bits)
8383 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8384 |  |  |  | HR8383 (Lo-16bits)
8385 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8386 |  |  |  | HR8385 (Lo-16bits)
8387 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8388 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8389 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8390 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8391 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8392 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8393 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8394 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8395 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8396 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8397 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8398 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8399 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8400 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8401 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8402 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8403 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8404 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8405 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8406 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8407 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8408 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8409 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8410 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8411 | VUB2:U1/2 >>/<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8412 | VUB2:U1/2 >>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8413 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8414 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8415 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8416 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8417 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8418 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8419 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8420 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8421 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8422 |  |  |  | HR8421 (Lo-16bits)
8423 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8424 |  |  |  | HR8423 (Lo-16bits)
8425 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8426 |  |  |  | HR8425 (Lo-16bits)
8427 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8428 |  |  |  | HR8427 (Lo-16bits)
8429 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8430 |  |  |  | HR8429 (Lo-16bits)
8431 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8432 |  |  |  | HR8431 (Lo-16bits)
8433 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8434 |  |  |  | HR8433 (Lo-16bits)
8435 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8436 |  |  |  | HR8435 (Lo-16bits)
8437 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8438 |  |  |  | HR8437 (Lo-16bits)
8439 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8440 |  |  |  | HR8439 (Lo-16bits)
8441 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8442 |  |  |  | HR8441 (Lo-16bits)
8443 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8444 |  |  |  | HR8443 (Lo-16bits)
8445 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8446 |  |  |  | HR8445 (Lo-16bits)
8447 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8448 |  |  |  | HR8447 (Lo-16bits)
8449 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8450 |  |  |  | HR8449 (Lo-16bits)
8451 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8452 |  |  |  | HR8451 (Lo-16bits)
8453 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8454 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8455 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8456 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8457 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8458 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8459 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8460 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8461 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8462 |  |  |  | HR8461 (Lo-16bits)
8463 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8464 |  |  |  | HR8463 (Lo-16bits)
8465 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8466 |  |  |  | HR8465 (Lo-16bits)
8467 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8468 |  |  |  | HR8467 (Lo-16bits)
8469 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8470 |  |  |  | HR8469 (Lo-16bits)
8471 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8472 |  |  |  | HR8471 (Lo-16bits)
8473 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8474 |  |  |  | HR8473 (Lo-16bits)
8475 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8476 |  |  |  | HR8475 (Lo-16bits)
8477 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8478 |  |  |  | HR8477 (Lo-16bits)
8479 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8480 |  |  |  | HR8479 (Lo-16bits)
8481 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8482 |  |  |  | HR8481 (Lo-16bits)
8483 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8484 |  |  |  | HR8483 (Lo-16bits)
8485 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8486 |  |  |  | HR8485 (Lo-16bits)
8487 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8488 |  |  |  | HR8487 (Lo-16bits)
8489 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8490 |  |  |  | HR8489 (Lo-16bits)
8491 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8492 |  |  |  | HR8491 (Lo-16bits)
8493 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8494 |  |  |  | HR8493 (Lo-16bits)
8495 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8496 |  |  |  | HR8495 (Lo-16bits)
8497 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8498 |  |  |  | HR8497 (Lo-16bits)
8499 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8500 |  |  |  | HR8499 (Lo-16bits)
8501 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8502 |  |  |  | HR8501 (Lo-16bits)
8503 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8504 |  |  |  | HR8503 (Lo-16bits)
8505 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8506 |  |  |  | HR8505 (Lo-16bits)
8507 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8508 |  |  |  | HR8507 (Lo-16bits)
8509 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8510 |  |  |  | HR8509 (Lo-16bits)
8511 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8512 |  |  |  | HR8511 (Lo-16bits)
8513 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8514 |  |  |  | HR8513 (Lo-16bits)
8515 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8516 |  |  |  | HR8515 (Lo-16bits)
8517 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8518 |  |  |  | HR8517 (Lo-16bits)
8519 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8520 |  |  |  | HR8519 (Lo-16bits)
8521 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8522 |  |  |  | HR8521 (Lo-16bits)
8523 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8524 |  |  |  | HR8523 (Lo-16bits)
8525 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8526 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8527 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8528 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8529 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8530 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8531 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8532 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8533 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8534 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8535 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8536 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8537 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8538 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8539 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8540 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8541 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8542 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8543 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8544 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8545 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8546 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8547 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8548 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8549 | VUB3:U1/2 >>>/<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8550 | VUB3:U1/2 >>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8551 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8552 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8553 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8554 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8555 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8556 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8557 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8558 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8559 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8560 |  |  |  | HR8559 (Lo-16bits)
8561 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8562 |  |  |  | HR8561 (Lo-16bits)
8563 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8564 |  |  |  | HR8563 (Lo-16bits)
8565 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8566 |  |  |  | HR8565 (Lo-16bits)
8567 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8568 |  |  |  | HR8567 (Lo-16bits)
8569 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8570 |  |  |  | HR8569 (Lo-16bits)
8571 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8572 |  |  |  | HR8571 (Lo-16bits)
8573 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8574 |  |  |  | HR8573 (Lo-16bits)
8575 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8576 |  |  |  | HR8575 (Lo-16bits)
8577 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8578 |  |  |  | HR8577 (Lo-16bits)
8579 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8580 |  |  |  | HR8579 (Lo-16bits)
8581 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8582 |  |  |  | HR8581 (Lo-16bits)
8583 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8584 |  |  |  | HR8583 (Lo-16bits)
8585 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8586 |  |  |  | HR8585 (Lo-16bits)
8587 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8588 |  |  |  | HR8587 (Lo-16bits)
8589 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8590 |  |  |  | HR8589 (Lo-16bits)
8591 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8592 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8593 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8594 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8595 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8596 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8597 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8598 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8599 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8600 |  |  |  | HR8599 (Lo-16bits)
8601 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8602 |  |  |  | HR8601 (Lo-16bits)
8603 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8604 |  |  |  | HR8603 (Lo-16bits)
8605 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8606 |  |  |  | HR8605 (Lo-16bits)
8607 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8608 |  |  |  | HR8607 (Lo-16bits)
8609 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8610 |  |  |  | HR8609 (Lo-16bits)
8611 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8612 |  |  |  | HR8611 (Lo-16bits)
8613 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8614 |  |  |  | HR8613 (Lo-16bits)
8615 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8616 |  |  |  | HR8615 (Lo-16bits)
8617 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8618 |  |  |  | HR8617 (Lo-16bits)
8619 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8620 |  |  |  | HR8619 (Lo-16bits)
8621 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8622 |  |  |  | HR8621 (Lo-16bits)
8623 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8624 |  |  |  | HR8623 (Lo-16bits)
8625 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8626 |  |  |  | HR8625 (Lo-16bits)
8627 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8628 |  |  |  | HR8627 (Lo-16bits)
8629 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8630 |  |  |  | HR8629 (Lo-16bits)
8631 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8632 |  |  |  | HR8631 (Lo-16bits)
8633 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8634 |  |  |  | HR8633 (Lo-16bits)
8635 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8636 |  |  |  | HR8635 (Lo-16bits)
8637 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8638 |  |  |  | HR8637 (Lo-16bits)
8639 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8640 |  |  |  | HR8639 (Lo-16bits)
8641 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8642 |  |  |  | HR8641 (Lo-16bits)
8643 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8644 |  |  |  | HR8643 (Lo-16bits)
8645 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8646 |  |  |  | HR8645 (Lo-16bits)
8647 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8648 |  |  |  | HR8647 (Lo-16bits)
8649 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8650 |  |  |  | HR8649 (Lo-16bits)
8651 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8652 |  |  |  | HR8651 (Lo-16bits)
8653 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8654 |  |  |  | HR8653 (Lo-16bits)
8655 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8656 |  |  |  | HR8655 (Lo-16bits)
8657 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8658 |  |  |  | HR8657 (Lo-16bits)
8659 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8660 |  |  |  | HR8659 (Lo-16bits)
8661 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8662 |  |  |  | HR8661 (Lo-16bits)
8663 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8664 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8665 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8666 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8667 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8668 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8669 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8670 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8671 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8672 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8673 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8674 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8675 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8676 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8677 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8678 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8679 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8680 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8681 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8682 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8683 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8684 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8685 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8686 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8687 | VUB4:U1/2 >>>>/<<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8688 | VUB4:U1/2 >>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8689 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8690 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8691 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8692 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8693 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8694 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8695 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8696 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8697 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8698 |  |  |  | HR8697 (Lo-16bits)
8699 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8700 |  |  |  | HR8699 (Lo-16bits)
8701 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8702 |  |  |  | HR8701 (Lo-16bits)
8703 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8704 |  |  |  | HR8703 (Lo-16bits)
8705 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8706 |  |  |  | HR8705 (Lo-16bits)
8707 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8708 |  |  |  | HR8707 (Lo-16bits)
8709 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8710 |  |  |  | HR8709 (Lo-16bits)
8711 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8712 |  |  |  | HR8711 (Lo-16bits)
8713 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8714 |  |  |  | HR8713 (Lo-16bits)
8715 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8716 |  |  |  | HR8715 (Lo-16bits)
8717 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8718 |  |  |  | HR8717 (Lo-16bits)
8719 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8720 |  |  |  | HR8719 (Lo-16bits)
8721 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8722 |  |  |  | HR8721 (Lo-16bits)
8723 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8724 |  |  |  | HR8723 (Lo-16bits)
8725 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8726 |  |  |  | HR8725 (Lo-16bits)
8727 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8728 |  |  |  | HR8727 (Lo-16bits)
8729 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8730 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8731 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8732 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8733 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8734 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8735 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8736 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8737 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8738 |  |  |  | HR8737 (Lo-16bits)
8739 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8740 |  |  |  | HR8739 (Lo-16bits)
8741 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8742 |  |  |  | HR8741 (Lo-16bits)
8743 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8744 |  |  |  | HR8743 (Lo-16bits)
8745 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8746 |  |  |  | HR8745 (Lo-16bits)
8747 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8748 |  |  |  | HR8747 (Lo-16bits)
8749 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8750 |  |  |  | HR8749 (Lo-16bits)
8751 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8752 |  |  |  | HR8751 (Lo-16bits)
8753 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8754 |  |  |  | HR8753 (Lo-16bits)
8755 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8756 |  |  |  | HR8755 (Lo-16bits)
8757 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8758 |  |  |  | HR8757 (Lo-16bits)
8759 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8760 |  |  |  | HR8759 (Lo-16bits)
8761 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8762 |  |  |  | HR8761 (Lo-16bits)
8763 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8764 |  |  |  | HR8763 (Lo-16bits)
8765 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8766 |  |  |  | HR8765 (Lo-16bits)
8767 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8768 |  |  |  | HR8767 (Lo-16bits)
8769 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8770 |  |  |  | HR8769 (Lo-16bits)
8771 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8772 |  |  |  | HR8771 (Lo-16bits)
8773 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8774 |  |  |  | HR8773 (Lo-16bits)
8775 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8776 |  |  |  | HR8775 (Lo-16bits)
8777 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8778 |  |  |  | HR8777 (Lo-16bits)
8779 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8780 |  |  |  | HR8779 (Lo-16bits)
8781 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8782 |  |  |  | HR8781 (Lo-16bits)
8783 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8784 |  |  |  | HR8783 (Lo-16bits)
8785 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8786 |  |  |  | HR8785 (Lo-16bits)
8787 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8788 |  |  |  | HR8787 (Lo-16bits)
8789 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8790 |  |  |  | HR8789 (Lo-16bits)
8791 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8792 |  |  |  | HR8791 (Lo-16bits)
8793 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8794 |  |  |  | HR8793 (Lo-16bits)
8795 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8796 |  |  |  | HR8795 (Lo-16bits)
8797 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8798 |  |  |  | HR8797 (Lo-16bits)
8799 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8800 |  |  |  | HR8799 (Lo-16bits)
8801 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8802 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8803 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8804 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8805 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8806 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8807 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8808 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8809 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8810 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8811 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8812 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8813 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8814 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8815 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8816 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8817 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8818 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8819 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8820 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8821 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8822 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8823 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8824 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8825 | PGS1:PS1 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8826 | PGS1:PS2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8827 | PGS1:PS3 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8828 | PGS1:PS4 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8829 | PGS1:PS5 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8830 | PGS1:PS6 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8831 | PGS1:PS7 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8832 | PGS1:PS8 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8833 | PGS1:PS9 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8834 | PGS1:PS10 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8835 | FRQC1:f> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8836 | FRQC1:f>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8837 | FRQC1:f>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8838 | FRQC1:f>>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8839 | FRQC1:f< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8840 | FRQC1:f<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8841 | FRQC1:f<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8842 | FRQC1:f<<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8843 | FRQV1:f</> [81O/81U] mode | R(W) | 1 | 0=Disabled;1=Activated
8844 | FRQV1:f> Enable | R(W) | 1 | 0=No;1=Yes
8845 | FRQV1:f> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8846 | FRQV1:f>> Enable | R(W) | 1 | 0=No;1=Yes
8847 | FRQV1:f>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8848 | FRQV1:f>>> Enable | R(W) | 1 | 0=No;1=Yes
8849 | FRQV1:f>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8850 | FRQV1:f>>>> Enable | R(W) | 1 | 0=No;1=Yes
8851 | FRQV1:f>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8852 | FRQV1:f< Enable | R(W) | 1 | 0=No;1=Yes
8853 | FRQV1:f< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8854 | FRQV1:f<< Enable | R(W) | 1 | 0=No;1=Yes
8855 | FRQV1:f<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8856 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8857 | FRQV1:f<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8858 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8859 | FRQV1:f<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8860 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8861 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8862 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8863 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8864 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8865 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8866 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8867 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8868 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8869 |  |  |  | HR8868 (Lo-16bits)
8870 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8871 |  |  |  | HR8870 (Lo-16bits)
8872 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8873 |  |  |  | HR8872 (Lo-16bits)
8874 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8875 |  |  |  | HR8874 (Lo-16bits)
8876 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8877 |  |  |  | HR8876 (Lo-16bits)
8878 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8879 |  |  |  | HR8878 (Lo-16bits)
8880 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8881 |  |  |  | HR8880 (Lo-16bits)
8882 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8883 |  |  |  | HR8882 (Lo-16bits)
8884 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8885 |  |  |  | HR8884 (Lo-16bits)
8886 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8887 |  |  |  | HR8886 (Lo-16bits)
8888 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8889 |  |  |  | HR8888 (Lo-16bits)
8890 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8891 |  |  |  | HR8890 (Lo-16bits)
8892 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8893 |  |  |  | HR8892 (Lo-16bits)
8894 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8895 |  |  |  | HR8894 (Lo-16bits)
8896 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8897 |  |  |  | HR8896 (Lo-16bits)
8898 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8899 |  |  |  | HR8898 (Lo-16bits)
8900 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8901 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8902 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8903 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8904 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8905 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8906 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8907 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8908 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8909 |  |  |  | HR8908 (Lo-16bits)
8910 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8911 |  |  |  | HR8910 (Lo-16bits)
8912 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8913 |  |  |  | HR8912 (Lo-16bits)
8914 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8915 |  |  |  | HR8914 (Lo-16bits)
8916 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8917 |  |  |  | HR8916 (Lo-16bits)
8918 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8919 |  |  |  | HR8918 (Lo-16bits)
8920 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8921 |  |  |  | HR8920 (Lo-16bits)
8922 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8923 |  |  |  | HR8922 (Lo-16bits)
8924 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8925 |  |  |  | HR8924 (Lo-16bits)
8926 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8927 |  |  |  | HR8926 (Lo-16bits)
8928 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8929 |  |  |  | HR8928 (Lo-16bits)
8930 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8931 |  |  |  | HR8930 (Lo-16bits)
8932 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8933 |  |  |  | HR8932 (Lo-16bits)
8934 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8935 |  |  |  | HR8934 (Lo-16bits)
8936 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8937 |  |  |  | HR8936 (Lo-16bits)
8938 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8939 |  |  |  | HR8938 (Lo-16bits)
8940 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8941 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8942 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8943 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8944 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8945 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8946 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8947 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8948 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8949 |  |  |  | HR8948 (Lo-16bits)
8950 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8951 |  |  |  | HR8950 (Lo-16bits)
8952 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8953 |  |  |  | HR8952 (Lo-16bits)
8954 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8955 |  |  |  | HR8954 (Lo-16bits)
8956 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8957 |  |  |  | HR8956 (Lo-16bits)
8958 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8959 |  |  |  | HR8958 (Lo-16bits)
8960 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8961 |  |  |  | HR8960 (Lo-16bits)
8962 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8963 |  |  |  | HR8962 (Lo-16bits)
8964 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8965 |  |  |  | HR8964 (Lo-16bits)
8966 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8967 |  |  |  | HR8966 (Lo-16bits)
8968 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8969 |  |  |  | HR8968 (Lo-16bits)
8970 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8971 |  |  |  | HR8970 (Lo-16bits)
8972 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8973 |  |  |  | HR8972 (Lo-16bits)
8974 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8975 |  |  |  | HR8974 (Lo-16bits)
8976 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8977 |  |  |  | HR8976 (Lo-16bits)
8978 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8979 |  |  |  | HR8978 (Lo-16bits)
8980 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8981 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8982 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8983 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8984 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8985 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8986 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8987 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8988 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8989 |  |  |  | HR8988 (Lo-16bits)
8990 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8991 |  |  |  | HR8990 (Lo-16bits)
8992 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8993 |  |  |  | HR8992 (Lo-16bits)
8994 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8995 |  |  |  | HR8994 (Lo-16bits)
8996 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8997 |  |  |  | HR8996 (Lo-16bits)
8998 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8999 |  |  |  | HR8998 (Lo-16bits)
9000 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9001 |  |  |  | HR9000 (Lo-16bits)
9002 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9003 |  |  |  | HR9002 (Lo-16bits)
9004 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9005 |  |  |  | HR9004 (Lo-16bits)
9006 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9007 |  |  |  | HR9006 (Lo-16bits)
9008 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9009 |  |  |  | HR9008 (Lo-16bits)
9010 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9011 |  |  |  | HR9010 (Lo-16bits)
9012 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9013 |  |  |  | HR9012 (Lo-16bits)
9014 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9015 |  |  |  | HR9014 (Lo-16bits)
9016 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9017 |  |  |  | HR9016 (Lo-16bits)
9018 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9019 |  |  |  | HR9018 (Lo-16bits)
9020 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9021 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9022 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9023 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9024 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9025 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9026 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9027 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9028 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9029 |  |  |  | HR9028 (Lo-16bits)
9030 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9031 |  |  |  | HR9030 (Lo-16bits)
9032 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9033 |  |  |  | HR9032 (Lo-16bits)
9034 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9035 |  |  |  | HR9034 (Lo-16bits)
9036 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9037 |  |  |  | HR9036 (Lo-16bits)
9038 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9039 |  |  |  | HR9038 (Lo-16bits)
9040 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9041 |  |  |  | HR9040 (Lo-16bits)
9042 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9043 |  |  |  | HR9042 (Lo-16bits)
9044 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9045 |  |  |  | HR9044 (Lo-16bits)
9046 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9047 |  |  |  | HR9046 (Lo-16bits)
9048 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9049 |  |  |  | HR9048 (Lo-16bits)
9050 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9051 |  |  |  | HR9050 (Lo-16bits)
9052 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9053 |  |  |  | HR9052 (Lo-16bits)
9054 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9055 |  |  |  | HR9054 (Lo-16bits)
9056 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9057 |  |  |  | HR9056 (Lo-16bits)
9058 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9059 |  |  |  | HR9058 (Lo-16bits)
9060 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9061 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9062 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9063 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9064 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9065 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9066 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9067 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9068 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9069 |  |  |  | HR9068 (Lo-16bits)
9070 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9071 |  |  |  | HR9070 (Lo-16bits)
9072 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9073 |  |  |  | HR9072 (Lo-16bits)
9074 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9075 |  |  |  | HR9074 (Lo-16bits)
9076 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9077 |  |  |  | HR9076 (Lo-16bits)
9078 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9079 |  |  |  | HR9078 (Lo-16bits)
9080 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9081 |  |  |  | HR9080 (Lo-16bits)
9082 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9083 |  |  |  | HR9082 (Lo-16bits)
9084 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9085 |  |  |  | HR9084 (Lo-16bits)
9086 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9087 |  |  |  | HR9086 (Lo-16bits)
9088 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9089 |  |  |  | HR9088 (Lo-16bits)
9090 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9091 |  |  |  | HR9090 (Lo-16bits)
9092 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9093 |  |  |  | HR9092 (Lo-16bits)
9094 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9095 |  |  |  | HR9094 (Lo-16bits)
9096 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9097 |  |  |  | HR9096 (Lo-16bits)
9098 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9099 |  |  |  | HR9098 (Lo-16bits)
9100 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9101 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9102 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9103 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9104 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9105 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9106 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9107 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9108 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9109 |  |  |  | HR9108 (Lo-16bits)
9110 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9111 |  |  |  | HR9110 (Lo-16bits)
9112 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9113 |  |  |  | HR9112 (Lo-16bits)
9114 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9115 |  |  |  | HR9114 (Lo-16bits)
9116 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9117 |  |  |  | HR9116 (Lo-16bits)
9118 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9119 |  |  |  | HR9118 (Lo-16bits)
9120 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9121 |  |  |  | HR9120 (Lo-16bits)
9122 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9123 |  |  |  | HR9122 (Lo-16bits)
9124 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9125 |  |  |  | HR9124 (Lo-16bits)
9126 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9127 |  |  |  | HR9126 (Lo-16bits)
9128 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9129 |  |  |  | HR9128 (Lo-16bits)
9130 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9131 |  |  |  | HR9130 (Lo-16bits)
9132 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9133 |  |  |  | HR9132 (Lo-16bits)
9134 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9135 |  |  |  | HR9134 (Lo-16bits)
9136 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9137 |  |  |  | HR9136 (Lo-16bits)
9138 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9139 |  |  |  | HR9138 (Lo-16bits)
9140 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9141 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9142 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9143 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9144 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9145 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9146 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9147 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9148 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9149 |  |  |  | HR9148 (Lo-16bits)
9150 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9151 |  |  |  | HR9150 (Lo-16bits)
9152 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9153 |  |  |  | HR9152 (Lo-16bits)
9154 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9155 |  |  |  | HR9154 (Lo-16bits)
9156 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9157 |  |  |  | HR9156 (Lo-16bits)
9158 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9159 |  |  |  | HR9158 (Lo-16bits)
9160 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9161 |  |  |  | HR9160 (Lo-16bits)
9162 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9163 |  |  |  | HR9162 (Lo-16bits)
9164 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9165 |  |  |  | HR9164 (Lo-16bits)
9166 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9167 |  |  |  | HR9166 (Lo-16bits)
9168 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9169 |  |  |  | HR9168 (Lo-16bits)
9170 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9171 |  |  |  | HR9170 (Lo-16bits)
9172 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9173 |  |  |  | HR9172 (Lo-16bits)
9174 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9175 |  |  |  | HR9174 (Lo-16bits)
9176 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9177 |  |  |  | HR9176 (Lo-16bits)
9178 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9179 |  |  |  | HR9178 (Lo-16bits)
9180 | DFT1:df/dt >/< (1) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9181 | DFT1:df/dt >/< (2) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9182 | DFT1:df/dt >/< (3) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9183 | DFT1:df/dt >/< (4) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9184 | DFT1:df/dt >/< (5) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9185 | DFT1:df/dt >/< (6) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9186 | DFT1:df/dt >/< (7) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9187 | DFT1:df/dt >/< (8) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9188 | RHC1:Counter is now | R | 1 | 0=Idle;1=Counting
9189 | RHC1:Running hours | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9190 |  |  |  | HR9189 (Lo-16bits)
9191 | RHC1:Start count | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9192 |  |  |  | HR9191 (Lo-16bits)
9193 | GST1:Generator is now | R | 1 | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
9194 | PWR1:PQS>/< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9195 | PWR2:PQS>>/<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9196 | PWR3:PQS>>>/<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9197 | PWR4:PQS>>>>/<<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9198 | OPW1:P> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9199 | UPW1:P< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9200 | RPW1:Prev> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9201 | SEF1:U03rd< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9202 | SEF1:U03rd< Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
9203 | UEX1:Q< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9204 | UIM1:Z< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9205 | UIM2:Z<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9206 | VOC1:Iv> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9207 | VOC1:Voltage measurement | R | 1 | 0=Invalid U1 not avail.;1=Ok
9208 | VHZ1:V/Hz(1) > condition | R | 1 | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
9209 | VHZ1:V/Hz(2) > condition | R | 1 | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
9210 | UPF1:PF< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
9211 | RTDIN:S1 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9212 |  |  |  | HR9211 (Lo-16bits)
9213 | RTDIN:S1 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9214 |  |  |  | HR9213 (Lo-16bits)
9215 | RTDIN:S1 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9216 | RTDIN:S1 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9217 |  |  |  | HR9216 (Lo-16bits)
9218 | RTDIN:S2 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9219 |  |  |  | HR9218 (Lo-16bits)
9220 | RTDIN:S2 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9221 |  |  |  | HR9220 (Lo-16bits)
9222 | RTDIN:S2 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9223 | RTDIN:S2 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9224 |  |  |  | HR9223 (Lo-16bits)
9225 | RTDIN:S3 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9226 |  |  |  | HR9225 (Lo-16bits)
9227 | RTDIN:S3 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9228 |  |  |  | HR9227 (Lo-16bits)
9229 | RTDIN:S3 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9230 | RTDIN:S3 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9231 |  |  |  | HR9230 (Lo-16bits)
9232 | RTDIN:S4 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9233 |  |  |  | HR9232 (Lo-16bits)
9234 | RTDIN:S4 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9235 |  |  |  | HR9234 (Lo-16bits)
9236 | RTDIN:S4 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9237 | RTDIN:S4 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9238 |  |  |  | HR9237 (Lo-16bits)
9239 | RTDIN:S5 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9240 |  |  |  | HR9239 (Lo-16bits)
9241 | RTDIN:S5 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9242 |  |  |  | HR9241 (Lo-16bits)
9243 | RTDIN:S5 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9244 | RTDIN:S5 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9245 |  |  |  | HR9244 (Lo-16bits)
9246 | RTDIN:S6 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9247 |  |  |  | HR9246 (Lo-16bits)
9248 | RTDIN:S6 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9249 |  |  |  | HR9248 (Lo-16bits)
9250 | RTDIN:S6 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9251 | RTDIN:S6 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9252 |  |  |  | HR9251 (Lo-16bits)
9253 | RTDIN:S7 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9254 |  |  |  | HR9253 (Lo-16bits)
9255 | RTDIN:S7 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9256 |  |  |  | HR9255 (Lo-16bits)
9257 | RTDIN:S7 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9258 |  |  |  | HR9257 (Lo-16bits)
9259 | RTDIN:S7 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9260 | RTDIN:S7 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9261 |  |  |  | HR9260 (Lo-16bits)
9262 | RTDIN:S8 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9263 |  |  |  | HR9262 (Lo-16bits)
9264 | RTDIN:S8 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9265 |  |  |  | HR9264 (Lo-16bits)
9266 | RTDIN:S8 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9267 |  |  |  | HR9266 (Lo-16bits)
9268 | RTDIN:S8 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9269 | RTDIN:S8 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9270 |  |  |  | HR9269 (Lo-16bits)
9271 | RTDIN:S9 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9272 |  |  |  | HR9271 (Lo-16bits)
9273 | RTDIN:S9 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9274 |  |  |  | HR9273 (Lo-16bits)
9275 | RTDIN:S9 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9276 | RTDIN:S9 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9277 |  |  |  | HR9276 (Lo-16bits)
9278 | RTDIN:S10 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9279 |  |  |  | HR9278 (Lo-16bits)
9280 | RTDIN:S10 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9281 |  |  |  | HR9280 (Lo-16bits)
9282 | RTDIN:S10 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9283 | RTDIN:S10 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9284 |  |  |  | HR9283 (Lo-16bits)
9285 | RTDIN:S11 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9286 |  |  |  | HR9285 (Lo-16bits)
9287 | RTDIN:S11 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9288 |  |  |  | HR9287 (Lo-16bits)
9289 | RTDIN:S11 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9290 | RTDIN:S11 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9291 |  |  |  | HR9290 (Lo-16bits)
9292 | RTDIN:S12 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9293 |  |  |  | HR9292 (Lo-16bits)
9294 | RTDIN:S12 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9295 |  |  |  | HR9294 (Lo-16bits)
9296 | RTDIN:S12 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9297 | RTDIN:S12 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9298 |  |  |  | HR9297 (Lo-16bits)
9299 | RTDIN:S13 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9300 |  |  |  | HR9299 (Lo-16bits)
9301 | RTDIN:S13 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9302 |  |  |  | HR9301 (Lo-16bits)
9303 | RTDIN:S13 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9304 | RTDIN:S13 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9305 |  |  |  | HR9304 (Lo-16bits)
9306 | RTDIN:S14 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9307 |  |  |  | HR9306 (Lo-16bits)
9308 | RTDIN:S14 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9309 |  |  |  | HR9308 (Lo-16bits)
9310 | RTDIN:S14 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9311 | RTDIN:S14 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9312 |  |  |  | HR9311 (Lo-16bits)
9313 | RTDIN:S15 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9314 |  |  |  | HR9313 (Lo-16bits)
9315 | RTDIN:S15 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9316 |  |  |  | HR9315 (Lo-16bits)
9317 | RTDIN:S15 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9318 |  |  |  | HR9317 (Lo-16bits)
9319 | RTDIN:S15 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9320 | RTDIN:S15 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9321 |  |  |  | HR9320 (Lo-16bits)
9322 | RTDIN:S16 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9323 |  |  |  | HR9322 (Lo-16bits)
9324 | RTDIN:S16 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9325 |  |  |  | HR9324 (Lo-16bits)
9326 | RTDIN:S16 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9327 |  |  |  | HR9326 (Lo-16bits)
9328 | RTDIN:S16 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9329 | RTDIN:S16 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9330 |  |  |  | HR9329 (Lo-16bits)
9331 | RTD1:S1 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9332 |  |  |  | HR9331 (Lo-16bits)
9333 | RTD1:S2 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9334 |  |  |  | HR9333 (Lo-16bits)
9335 | RTD1:S3 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9336 |  |  |  | HR9335 (Lo-16bits)
9337 | RTD1:S4 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9338 |  |  |  | HR9337 (Lo-16bits)
9339 | RTD1:S5 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9340 |  |  |  | HR9339 (Lo-16bits)
9341 | RTD1:S6 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9342 |  |  |  | HR9341 (Lo-16bits)
9343 | RTD1:S7 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9344 |  |  |  | HR9343 (Lo-16bits)
9345 | RTD1:S8 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9346 |  |  |  | HR9345 (Lo-16bits)
9347 | RTD1:S9 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9348 |  |  |  | HR9347 (Lo-16bits)
9349 | RTD1:S10 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9350 |  |  |  | HR9349 (Lo-16bits)
9351 | RTD1:S11 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9352 |  |  |  | HR9351 (Lo-16bits)
9353 | RTD1:S12 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9354 |  |  |  | HR9353 (Lo-16bits)
9355 | RTD1:S13 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9356 |  |  |  | HR9355 (Lo-16bits)
9357 | RTD1:S14 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9358 |  |  |  | HR9357 (Lo-16bits)
9359 | RTD1:S15 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9360 |  |  |  | HR9359 (Lo-16bits)
9361 | RTD1:S16 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9362 |  |  |  | HR9361 (Lo-16bits)
9363 | RTD1:S1 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9364 |  |  |  | HR9363 (Lo-16bits)
9365 | RTD1:S1 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9366 |  |  |  | HR9365 (Lo-16bits)
9367 | RTD1:S1 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9368 |  |  |  | HR9367 (Lo-16bits)
9369 | RTD1:S2 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9370 |  |  |  | HR9369 (Lo-16bits)
9371 | RTD1:S2 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9372 |  |  |  | HR9371 (Lo-16bits)
9373 | RTD1:S2 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9374 |  |  |  | HR9373 (Lo-16bits)
9375 | RTD1:S3 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9376 |  |  |  | HR9375 (Lo-16bits)
9377 | RTD1:S3 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9378 |  |  |  | HR9377 (Lo-16bits)
9379 | RTD1:S3 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9380 |  |  |  | HR9379 (Lo-16bits)
9381 | RTD1:S4 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9382 |  |  |  | HR9381 (Lo-16bits)
9383 | RTD1:S4 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9384 |  |  |  | HR9383 (Lo-16bits)
9385 | RTD1:S4 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9386 |  |  |  | HR9385 (Lo-16bits)
9387 | RTD1:S5 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9388 |  |  |  | HR9387 (Lo-16bits)
9389 | RTD1:S5 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9390 |  |  |  | HR9389 (Lo-16bits)
9391 | RTD1:S5 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9392 |  |  |  | HR9391 (Lo-16bits)
9393 | RTD1:S6 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9394 |  |  |  | HR9393 (Lo-16bits)
9395 | RTD1:S6 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9396 |  |  |  | HR9395 (Lo-16bits)
9397 | RTD1:S6 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9398 |  |  |  | HR9397 (Lo-16bits)
9399 | RTD1:S7 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9400 |  |  |  | HR9399 (Lo-16bits)
9401 | RTD1:S7 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9402 |  |  |  | HR9401 (Lo-16bits)
9403 | RTD1:S7 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9404 |  |  |  | HR9403 (Lo-16bits)
9405 | RTD1:S8 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9406 |  |  |  | HR9405 (Lo-16bits)
9407 | RTD1:S8 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9408 |  |  |  | HR9407 (Lo-16bits)
9409 | RTD1:S8 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9410 |  |  |  | HR9409 (Lo-16bits)
9411 | RTD1:S9 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9412 |  |  |  | HR9411 (Lo-16bits)
9413 | RTD1:S9 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9414 |  |  |  | HR9413 (Lo-16bits)
9415 | RTD1:S9 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9416 |  |  |  | HR9415 (Lo-16bits)
9417 | RTD1:S10 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9418 |  |  |  | HR9417 (Lo-16bits)
9419 | RTD1:S10 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9420 |  |  |  | HR9419 (Lo-16bits)
9421 | RTD1:S10 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9422 |  |  |  | HR9421 (Lo-16bits)
9423 | RTD1:S11 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9424 |  |  |  | HR9423 (Lo-16bits)
9425 | RTD1:S11 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9426 |  |  |  | HR9425 (Lo-16bits)
9427 | RTD1:S11 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9428 |  |  |  | HR9427 (Lo-16bits)
9429 | RTD1:S12 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9430 |  |  |  | HR9429 (Lo-16bits)
9431 | RTD1:S12 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9432 |  |  |  | HR9431 (Lo-16bits)
9433 | RTD1:S12 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9434 |  |  |  | HR9433 (Lo-16bits)
9435 | RTD1:S13 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9436 |  |  |  | HR9435 (Lo-16bits)
9437 | RTD1:S13 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9438 |  |  |  | HR9437 (Lo-16bits)
9439 | RTD1:S13 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9440 |  |  |  | HR9439 (Lo-16bits)
9441 | RTD1:S14 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9442 |  |  |  | HR9441 (Lo-16bits)
9443 | RTD1:S14 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9444 |  |  |  | HR9443 (Lo-16bits)
9445 | RTD1:S14 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9446 |  |  |  | HR9445 (Lo-16bits)
9447 | RTD1:S15 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9448 |  |  |  | HR9447 (Lo-16bits)
9449 | RTD1:S15 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9450 |  |  |  | HR9449 (Lo-16bits)
9451 | RTD1:S15 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9452 |  |  |  | HR9451 (Lo-16bits)
9453 | RTD1:S16 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9454 |  |  |  | HR9453 (Lo-16bits)
9455 | RTD1:S16 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9456 |  |  |  | HR9455 (Lo-16bits)
9457 | RTD1:S16 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9458 |  |  |  | HR9457 (Lo-16bits)
9459 | ARC1:I/I0 Arc> condition | R | 1 | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
9460 | ARC1:I/I0 Arc> S1 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9461 |  |  |  | HR9460 (Lo-16bits)
9462 | ARC1:I/I0 Arc> S2 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9463 |  |  |  | HR9462 (Lo-16bits)
9464 | ARC1:I/I0 Arc> S3 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9465 |  |  |  | HR9464 (Lo-16bits)
9466 | ARC1:I/I0 Arc> S4 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9467 |  |  |  | HR9466 (Lo-16bits)
9468 | ARC1:I/I0 Arc> IO unit fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9469 |  |  |  | HR9468 (Lo-16bits)
9470 | CTS1:CTS1 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9471 | CTS2:CTS2 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9472 | VTS1:VTS condition | R | 1 | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
9473 | VTS1:Bus voltages | R | 1 | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
9474 | FLX1:Fault locator condition | R | 1 | 0=Idle;1=Triggered;2=Calc ready
9475 | THD1:THD condition | R | 1 | 0=Normal;1=Start;2=Alarm;3=Blocked
9476 | CBW1:CBW condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On
9477 | NJK1:U0> RECL condition | R | 1 | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
9478 | SOF1:SOTF condition | R | 1 | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
9479 | PCS1:PCS1 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9480 |  |  |  | HR9479 (Lo-16bits)
9481 | PCS2:PCS2 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9482 |  |  |  | HR9481 (Lo-16bits)
9483 | PCS3:PCS3 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9484 |  |  |  | HR9483 (Lo-16bits)
9485 | PCS4:PCS4 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9486 |  |  |  | HR9485 (Lo-16bits)
9487 | PCS5:PCS5 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9488 |  |  |  | HR9487 (Lo-16bits)
9489 | SYN1:SYN1 Condition | R | 2 | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok (Hi-16bits)
9490 |  |  |  | HR9489 (Lo-16bits)
9491 | SYN1:SYN2 Condition | R | 2 | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok (Hi-16bits)
9492 |  |  |  | HR9491 (Lo-16bits)
9493 | SYN1:SYN3 Condition | R | 2 | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok (Hi-16bits)
9494 |  |  |  | HR9493 (Lo-16bits)
9495 | SYN1:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9496 |  |  |  | HR9495 (Lo-16bits)
9497 | SYN1:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9498 |  |  |  | HR9497 (Lo-16bits)
9499 | SYN1:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9500 |  |  |  | HR9499 (Lo-16bits)
9501 | SYN1:SYN2 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9502 |  |  |  | HR9501 (Lo-16bits)
9503 | SYN1:SYN2 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9504 |  |  |  | HR9503 (Lo-16bits)
9505 | SYN1:SYN2 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9506 |  |  |  | HR9505 (Lo-16bits)
9507 | SYN1:SYN3 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9508 |  |  |  | HR9507 (Lo-16bits)
9509 | SYN1:SYN3 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9510 |  |  |  | HR9509 (Lo-16bits)
9511 | SYN1:SYN3 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9512 |  |  |  | HR9511 (Lo-16bits)
9513 | VJP1:<DELTA><alpha> > condition | R | 1 | 0=Normal;1=Blocked;2=Trip;3=Alarm
9514 | VJP1:Voltage meas selected | R | 1 | 0=Selection Ok;1=Selection not available
9515 | OBJ1:Object1 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9516 | OBJ2:Object2 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9517 | OBJ3:Object3 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9518 | OBJ4:Object4 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9519 | OBJ5:Object5 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9520 | OBJ6:Object6 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9521 | OBJ7:Object7 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9522 | OBJ8:Object8 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9523 | OBJ9:Object9 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9524 | OBJ10:Object10 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9525 | CIN1:Ind.1 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9526 | CIN2:Ind.2 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9527 | CIN3:Ind.3 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9528 | CIN4:Ind.4 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9529 | CIN5:Ind.5 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9530 | AR1:Auto-recloser [79] Mode | RW | 1 | 0=Disabled;1=Activated
9531 | AR1:AR Status | R | 2 | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear (Hi-16bits)
9532 |  |  |  | HR9531 (Lo-16bits)
9533 | AR1:Timer active | R | 1 | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
9534 | VRG1:Vreg settings condition | R | 2 | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok (Hi-16bits)
9535 |  |  |  | HR9534 (Lo-16bits)
9536 | VRG1:Vreg condition | R | 2 | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on (Hi-16bits)
9537 |  |  |  | HR9536 (Lo-16bits)
9538 | VRG1:Vreg timer active | R | 1 | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
9539 | VRG1:Voltage now | R | 2 | FLOAT [0...140] (Hi-16bits)
9540 |  |  |  | HR9539 (Lo-16bits)
9541 | VRG1:Voltage difference to set target | R | 2 | FLOAT [-140...140] (Hi-16bits)
9542 |  |  |  | HR9541 (Lo-16bits)
9543 | VRG1:Voltage meas condition | R | 1 | 0=Not configured;1=System U12;2=System U23;3=System U31;4=VT4 meas U12;5=VT4 meas U23;6=VT4 meas U31;7=VT4 conf not ok
9544 | VRG1:Tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
9545 |  |  |  | HR9544 (Lo-16bits)
9546 | VRG1:Absolute tap location | R | 2 | FLOAT [0...50] (Hi-16bits)
9547 |  |  |  | HR9546 (Lo-16bits)
9548 | VRG1:Control mode | R | 1 | 0=Auto;1=Manual (loc&rem)
9549 | VRG1:Remote tap control input | RW | 1 | 0=Stop;1=Lower;2=Higher
9550 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9551 |  |  |  | HR9550 (Lo-16bits)
9552 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9553 |  |  |  | HR9552 (Lo-16bits)
9554 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9555 |  |  |  | HR9554 (Lo-16bits)
9556 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9557 |  |  |  | HR9556 (Lo-16bits)
9558 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9559 |  |  |  | HR9558 (Lo-16bits)
9560 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9561 |  |  |  | HR9560 (Lo-16bits)
9562 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9563 |  |  |  | HR9562 (Lo-16bits)
9564 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9565 |  |  |  | HR9564 (Lo-16bits)
9566 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9567 |  |  |  | HR9566 (Lo-16bits)
9568 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9569 |  |  |  | HR9568 (Lo-16bits)
9570 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9571 |  |  |  | HR9570 (Lo-16bits)
9572 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9573 |  |  |  | HR9572 (Lo-16bits)
9574 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9575 |  |  |  | HR9574 (Lo-16bits)
9576 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9577 |  |  |  | HR9576 (Lo-16bits)
9578 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9579 |  |  |  | HR9578 (Lo-16bits)
9580 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9581 |  |  |  | HR9580 (Lo-16bits)
9582 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9583 |  |  |  | HR9582 (Lo-16bits)
9584 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9585 |  |  |  | HR9584 (Lo-16bits)
9586 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9587 |  |  |  | HR9586 (Lo-16bits)
9588 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9589 |  |  |  | HR9588 (Lo-16bits)
9590 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9591 |  |  |  | HR9590 (Lo-16bits)
9592 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9593 |  |  |  | HR9592 (Lo-16bits)
9594 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9595 |  |  |  | HR9594 (Lo-16bits)
9596 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9597 |  |  |  | HR9596 (Lo-16bits)
9598 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9599 |  |  |  | HR9598 (Lo-16bits)
9600 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9601 |  |  |  | HR9600 (Lo-16bits)
9602 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9603 |  |  |  | HR9602 (Lo-16bits)
9604 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9605 |  |  |  | HR9604 (Lo-16bits)
9606 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9607 |  |  |  | HR9606 (Lo-16bits)
9608 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9609 |  |  |  | HR9608 (Lo-16bits)
9610 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9611 |  |  |  | HR9610 (Lo-16bits)
9612 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9613 |  |  |  | HR9612 (Lo-16bits)
9614 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9615 |  |  |  | HR9614 (Lo-16bits)
9616 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9617 |  |  |  | HR9616 (Lo-16bits)
9618 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9619 |  |  |  | HR9618 (Lo-16bits)
9620 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9621 |  |  |  | HR9620 (Lo-16bits)
9622 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9623 |  |  |  | HR9622 (Lo-16bits)
9624 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9625 |  |  |  | HR9624 (Lo-16bits)
9626 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9627 |  |  |  | HR9626 (Lo-16bits)
9628 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9629 |  |  |  | HR9628 (Lo-16bits)
9630 | EMON1:I> (50) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9631 | EMON1:I0> (50N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9632 | EMON1:Idir> (67) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9633 | EMON1:I0dir> (67N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9634 | EMON1:I0Int> (67NT) Monitor condition | R | 1 | 0=Normal;1=FLT FW;2=FLT REV
9635 | EMON1:U< (27) Monitor condition | R | 1 | 0=Normal;1=Undervoltage;2=No voltage
9636 | EMON1:U0> (59N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9637 | EMON1:FL (21FL) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9638 | ALARM:Alarms 1-32 | R | 2 | 0b=A1;1b=A2;2b=A3;3b=A4;4b=A5;5b=A6;6b=A7;7b=A8;8b=A9;9b=A10;10b=A11;11b=A12;12b=A13;13b=A14;14b=A15;15b=A16;16b=A17;17b=A18;18b=A19;19b=A20;20b=A21;21b=A22;22b=A23;23b=A24;24b=A25;25b=A26;26b=A27;27b=A28;28b=A29;29b=A30;30b=A31;31b=A32 (Hi-16bits)
9639 |  |  |  | HR9638 (Lo-16bits)
9640 | ALARM:Alarms 33-64 | R | 2 | 0b=A33;1b=A34;2b=A35;3b=A36;4b=A37;5b=A38;6b=A39;7b=A40;8b=A41;9b=A42;10b=A43;11b=A44;12b=A45;13b=A46;14b=A47;15b=A48;16b=A49;17b=A50;18b=A51;19b=A52;20b=A53;21b=A54;22b=A55;23b=A56;24b=A57;25b=A58;26b=A59;27b=A60;28b=A61;29b=A62;30b=A63;31b=A64 (Hi-16bits)
9641 |  |  |  | HR9640 (Lo-16bits)
9642 | GSYN:Synchronizer mode | RW | 1 | 0=Disabled;1=Activated
9643 | GSYN:Synchronizing by | RW | 1 | 0=Autosynchronizer;1=Manual commands
9644 | GSYN:Manual switching mode | RW | 1 | 0=Assisted synchroswitch;1=I know what I am doing
9645 | GSYN:Magnitude side A | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9646 |  |  |  | HR9645 (Lo-16bits)
9647 | GSYN:Magnitude side B | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9648 |  |  |  | HR9647 (Lo-16bits)
9649 | GSYN:Frequency side A | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9650 |  |  |  | HR9649 (Lo-16bits)
9651 | GSYN:Frequency side B | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9652 |  |  |  | HR9651 (Lo-16bits)
9653 | GSYN:Magnitude difference | R | 2 | FLOAT [-200...200] (Hi-16bits)
9654 |  |  |  | HR9653 (Lo-16bits)
9655 | GSYN:Frequency difference | R | 2 | FLOAT [-100...100] (Hi-16bits)
9656 |  |  |  | HR9655 (Lo-16bits)
9657 | GSYN:Angle difference | R | 2 | FLOAT [-360...360] (Hi-16bits)
9658 |  |  |  | HR9657 (Lo-16bits)
9659 | GSYN:Magnitude difference on closing BRK | R | 2 | FLOAT [-200...200] (Hi-16bits)
9660 |  |  |  | HR9659 (Lo-16bits)
9661 | GSYN:Frequency difference on closing BRK | R | 2 | FLOAT [-100...100] (Hi-16bits)
9662 |  |  |  | HR9661 (Lo-16bits)
9663 | GSYN:Angle difference on closing BRK | R | 2 | FLOAT [-360...360] (Hi-16bits)
9664 |  |  |  | HR9663 (Lo-16bits)
9665 | GSYN:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9666 |  |  |  | HR9665 (Lo-16bits)
9667 | GSYN:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9668 |  |  |  | HR9667 (Lo-16bits)
9669 | GSYN:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9670 |  |  |  | HR9669 (Lo-16bits)
9671 | GSYN:Synchronizing time left | R | 2 | FLOAT [0...1800] (Hi-16bits)
9672 |  |  |  | HR9671 (Lo-16bits)
9673 | GSYN:Magnitude difference fine tune | RW | 2 | FLOAT [-200...200] (Hi-16bits)
9674 |  |  |  | HR9673 (Lo-16bits)
9675 | GSYN:Frequency difference fine tune | RW | 2 | FLOAT [-100...100] (Hi-16bits)
9676 |  |  |  | HR9675 (Lo-16bits)
9677 | GSYN:Angle difference fine tune | RW | 2 | FLOAT [-360...360] (Hi-16bits)
9678 |  |  |  | HR9677 (Lo-16bits)
9679 | GSYN:Start Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9680 |  |  |  | HR9679 (Lo-16bits)
9681 | GSYN:Stop Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9682 |  |  |  | HR9681 (Lo-16bits)
9683 | GSYN:Block and Interrupt Synchronizing | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9684 |  |  |  | HR9683 (Lo-16bits)
9685 | GSYN:Breaker Closed | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9686 |  |  |  | HR9685 (Lo-16bits)
9687 | GSYN:Manual increase voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9688 |  |  |  | HR9687 (Lo-16bits)
9689 | GSYN:Manual decrease voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9690 |  |  |  | HR9689 (Lo-16bits)
9691 | GSYN:Manual increase frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9692 |  |  |  | HR9691 (Lo-16bits)
9693 | GSYN:Manual decrease frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9694 |  |  |  | HR9693 (Lo-16bits)
9695 | GSYN:Manual Close Breaker | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9696 |  |  |  | HR9695 (Lo-16bits)
9697 | GSYN:GSYN Voltage Mag.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9698 |  |  |  | HR9697 (Lo-16bits)
9699 | GSYN:GSYN Voltage Freq.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9700 |  |  |  | HR9699 (Lo-16bits)
9701 | GSYN:GSYN Voltage Ang.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9702 |  |  |  | HR9701 (Lo-16bits)
9703 | GSYN:GSYN Blocked | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9704 |  |  |  | HR9703 (Lo-16bits)
9705 | GSYN:GSYN Running | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9706 |  |  |  | HR9705 (Lo-16bits)
9707 | GSYN:GSYN Increase Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9708 |  |  |  | HR9707 (Lo-16bits)
9709 | GSYN:GSYN Decrease Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9710 |  |  |  | HR9709 (Lo-16bits)
9711 | GSYN:GSYN Increase Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9712 |  |  |  | HR9711 (Lo-16bits)
9713 | GSYN:GSYN Decrease Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9714 |  |  |  | HR9713 (Lo-16bits)
9715 | GSYN:GSYN Breaker Close Pulse | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9716 |  |  |  | HR9715 (Lo-16bits)
9717 | GSYN:GSYN Long Sync Time | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9718 |  |  |  | HR9717 (Lo-16bits)
9719 | GSYN:GSYN Nets Standstill | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9720 |  |  |  | HR9719 (Lo-16bits)
9721 | GSYN:GSYN Nets Departing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9722 |  |  |  | HR9721 (Lo-16bits)
9723 | GSYN:GSYN Nets Enclosing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9724 |  |  |  | HR9723 (Lo-16bits)
9725 | VREC:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9726 | VREC:Scale current values to primary | RW | 1 | 0=No;1=Yes
9727 | VREC:Record fault types (Overcurrrent & Voltage Over/Under) faults | RW | 1 | 0=No;1=Yes
9728 | VREC:Trigger register to memory | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9729 |  |  |  | HR9728 (Lo-16bits)
9730 | VREC:VREC Magnitude 1 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9731 |  |  |  | HR9730 (Lo-16bits)
9732 | VREC:VREC Magnitude 2 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9733 |  |  |  | HR9732 (Lo-16bits)
9734 | VREC:VREC Magnitude 3 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9735 |  |  |  | HR9734 (Lo-16bits)
9736 | VREC:VREC Magnitude 4 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9737 |  |  |  | HR9736 (Lo-16bits)
9738 | VREC:VREC Magnitude 5 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9739 |  |  |  | HR9738 (Lo-16bits)
9740 | VREC:VREC Magnitude 6 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9741 |  |  |  | HR9740 (Lo-16bits)
9742 | VREC:VREC Magnitude 7 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9743 |  |  |  | HR9742 (Lo-16bits)
9744 | VREC:VREC Magnitude 8 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9745 |  |  |  | HR9744 (Lo-16bits)
9746 | RTB:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9747 | RTB:Scale current values to primary | RW | 1 | 0=No;1=Yes
9748 | RTB:RTS to bus Magnitude 1 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9749 |  |  |  | HR9748 (Lo-16bits)
9750 | RTB:RTS to bus Magnitude 2 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9751 |  |  |  | HR9750 (Lo-16bits)
9752 | RTB:RTS to bus Magnitude 3 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9753 |  |  |  | HR9752 (Lo-16bits)
9754 | RTB:RTS to bus Magnitude 4 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9755 |  |  |  | HR9754 (Lo-16bits)
9756 | RTB:RTS to bus Magnitude 5 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9757 |  |  |  | HR9756 (Lo-16bits)
9758 | RTB:RTS to bus Magnitude 6 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9759 |  |  |  | HR9758 (Lo-16bits)
9760 | RTB:RTS to bus Magnitude 7 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9761 |  |  |  | HR9760 (Lo-16bits)
9762 | RTB:RTS to bus Magnitude 8 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9763 |  |  |  | HR9762 (Lo-16bits)
9764 | RTB:RTS to bus Magnitude 9 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9765 |  |  |  | HR9764 (Lo-16bits)
9766 | RTB:RTS to bus Magnitude 10 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9767 |  |  |  | HR9766 (Lo-16bits)
9768 | AOUT:mA In Channel 1 | R | 2 | FLOAT [0...24] (Hi-16bits)
9769 |  |  |  | HR9768 (Lo-16bits)
9770 | AOUT:mA In Channel 2 | R | 2 | FLOAT [0...24] (Hi-16bits)
9771 |  |  |  | HR9770 (Lo-16bits)
9772 | AOUT:mA Out Channel 1 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9773 |  |  |  | HR9772 (Lo-16bits)
9774 | AOUT:mA Out Channel 1 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9775 |  |  |  | HR9774 (Lo-16bits)
9776 | AOUT:mA Out Channel 2 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9777 |  |  |  | HR9776 (Lo-16bits)
9778 | AOUT:mA Out Channel 2 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9779 |  |  |  | HR9778 (Lo-16bits)
9780 | AOUT:mA Out Channel 3 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9781 |  |  |  | HR9780 (Lo-16bits)
9782 | AOUT:mA Out Channel 3 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9783 |  |  |  | HR9782 (Lo-16bits)
9784 | AOUT:mA Out Channel 4 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9785 |  |  |  | HR9784 (Lo-16bits)
9786 | AOUT:mA Out Channel 4 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9787 |  |  |  | HR9786 (Lo-16bits)
9788 | AOUT:mA Out Channel 5 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9789 |  |  |  | HR9788 (Lo-16bits)
9790 | AOUT:mA Out Channel 5 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9791 |  |  |  | HR9790 (Lo-16bits)
9792 | AOUT:mA Out Channel 6 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9793 |  |  |  | HR9792 (Lo-16bits)
9794 | AOUT:mA Out Channel 6 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9795 |  |  |  | HR9794 (Lo-16bits)
9796 | AOUT:mA Out Channel 7 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9797 |  |  |  | HR9796 (Lo-16bits)
9798 | AOUT:mA Out Channel 7 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9799 |  |  |  | HR9798 (Lo-16bits)
9800 | AOUT:mA Out Channel 8 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9801 |  |  |  | HR9800 (Lo-16bits)
9802 | AOUT:mA Out Channel 8 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9803 |  |  |  | HR9802 (Lo-16bits)
9906 | Object6 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9907 | Object7 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9908 | Object8 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9909 | Object9 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9910 | Object10 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020

## AQ-M210 & AQ-M215, v2.1.1.3-247
HR | Parameter | Access | Length | Info
1 | Modbus requests | R/W=0 | 1 | Diagnostic request counter
2 | Modbus quality | R | 1 | Diagnostic quality
3 | Modbus errors | R/W=0 | 1 | Diagnostic error counter
4 | Modbus Ctrl OK | R/W=0 | 1 | Diagnostic Control OK counter
5 | Modbus Ctrl Errors | R/W=0 | 1 | Diagnostic Control Error counter
6 | Object1 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
7 | Object2 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
8 | Object3 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9 | Object4 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
10 | Object5 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
11 | Previous Event register | R | 6 | Event code
12 | Previous Event register | R | 6 | Event timestamp (ms)
13 | Previous Event register | R | 6 | Event timestamp (sec Hi-16bits)
14 | Previous Event register | R | 6 | Event timestamp (sec Lo-16bits)
15 | Previous Event register | R | 6 | Event sequential index
16 | Previous Event register | R | 6 | RESERVED
17 | Event register | R | 6 | Event code
18 | Event register | R | 6 | Event timestamp (ms)
19 | Event register | R | 6 | Event timestamp (sec Hi-16bits)
20 | Event register | R | 6 | Event timestamp (sec Lo-16bits)
21 | Event register | R | 6 | Event sequential index
22 | Event register | R | 6 | RESERVED
23 | System time | RW | 3 | System time (ms)
24 | System time | RW | 3 | System time (sec Hi-16bits)
25 | System time | RW | 3 | System time (sec Lo-16bits)
26 | MEAS1:Pri.Pha.curr.IL1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
27 |  |  |  | HR26 (Lo-16bits)
28 | MEAS1:Pri.Pha.curr.IL2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
29 |  |  |  | HR28 (Lo-16bits)
30 | MEAS1:Pri.Pha.curr.IL3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
31 |  |  |  | HR30 (Lo-16bits)
32 | MEAS1:Pri.Res.curr.I01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
33 |  |  |  | HR32 (Lo-16bits)
34 | MEAS1:Pri.Res.curr.I02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
35 |  |  |  | HR34 (Lo-16bits)
36 | MEAS1:Pha.angle IL1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
37 |  |  |  | HR36 (Lo-16bits)
38 | MEAS1:Pha.angle IL2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
39 |  |  |  | HR38 (Lo-16bits)
40 | MEAS1:Pha.angle IL3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
41 |  |  |  | HR40 (Lo-16bits)
42 | MEAS1:Res.curr.angle I01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
43 |  |  |  | HR42 (Lo-16bits)
44 | MEAS1:Res.curr.angle I02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
45 |  |  |  | HR44 (Lo-16bits)
46 | MEAS1:Pri.calc.I0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
47 |  |  |  | HR46 (Lo-16bits)
48 | MEAS1:calc.I0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
49 |  |  |  | HR48 (Lo-16bits)
50 | MEAS1:Pha.curr.IL1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
51 |  |  |  | HR50 (Lo-16bits)
52 | MEAS1:Pha.curr.IL2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
53 |  |  |  | HR52 (Lo-16bits)
54 | MEAS1:Pha.curr.IL3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
55 |  |  |  | HR54 (Lo-16bits)
56 | MEAS1:Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
57 |  |  |  | HR56 (Lo-16bits)
58 | MEAS1:Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
59 |  |  |  | HR58 (Lo-16bits)
60 | MEAS1:Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
61 |  |  |  | HR60 (Lo-16bits)
62 | MEAS1:Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
63 |  |  |  | HR62 (Lo-16bits)
64 | MEAS1:Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
65 |  |  |  | HR64 (Lo-16bits)
66 | MEAS1:Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
67 |  |  |  | HR66 (Lo-16bits)
68 | MEAS1:Res.curr.I01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
69 |  |  |  | HR68 (Lo-16bits)
70 | MEAS1:Res.curr.I02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
71 |  |  |  | HR70 (Lo-16bits)
72 | MEAS1:Pha.L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
73 |  |  |  | HR72 (Lo-16bits)
74 | MEAS1:Pha.L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
75 |  |  |  | HR74 (Lo-16bits)
76 | MEAS1:Pha.L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
77 |  |  |  | HR76 (Lo-16bits)
78 | MEAS1:Pha.L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
79 |  |  |  | HR78 (Lo-16bits)
80 | MEAS1:Pha.L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
81 |  |  |  | HR80 (Lo-16bits)
82 | MEAS1:Pha.L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
83 |  |  |  | HR82 (Lo-16bits)
84 | MEAS1:Res.I01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
85 |  |  |  | HR84 (Lo-16bits)
86 | MEAS1:Res.I01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
87 |  |  |  | HR86 (Lo-16bits)
88 | MEAS1:Res.I02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
89 |  |  |  | HR88 (Lo-16bits)
90 | MEAS1:Res.I02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
91 |  |  |  | HR90 (Lo-16bits)
92 | MEAS1:P-P curr.IL1 | R | 2 | FLOAT [0...500] (Hi-16bits)
93 |  |  |  | HR92 (Lo-16bits)
94 | MEAS1:P-P curr.IL2 | R | 2 | FLOAT [0...500] (Hi-16bits)
95 |  |  |  | HR94 (Lo-16bits)
96 | MEAS1:P-P curr.IL3 | R | 2 | FLOAT [0...500] (Hi-16bits)
97 |  |  |  | HR96 (Lo-16bits)
98 | MEAS1:P-P curr.I01 | R | 2 | FLOAT [0...500] (Hi-16bits)
99 |  |  |  | HR98 (Lo-16bits)
100 | MEAS1:P-P curr.I02 | R | 2 | FLOAT [0...500] (Hi-16bits)
101 |  |  |  | HR100 (Lo-16bits)
102 | MEAS1:IL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
103 |  |  |  | HR102 (Lo-16bits)
104 | MEAS1:IL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
105 |  |  |  | HR104 (Lo-16bits)
106 | MEAS1:IL1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
107 |  |  |  | HR106 (Lo-16bits)
108 | MEAS1:IL1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
109 |  |  |  | HR108 (Lo-16bits)
110 | MEAS1:IL1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
111 |  |  |  | HR110 (Lo-16bits)
112 | MEAS1:IL1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
113 |  |  |  | HR112 (Lo-16bits)
114 | MEAS1:IL1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
115 |  |  |  | HR114 (Lo-16bits)
116 | MEAS1:IL1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
117 |  |  |  | HR116 (Lo-16bits)
118 | MEAS1:IL1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
119 |  |  |  | HR118 (Lo-16bits)
120 | MEAS1:IL1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
121 |  |  |  | HR120 (Lo-16bits)
122 | MEAS1:IL1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
123 |  |  |  | HR122 (Lo-16bits)
124 | MEAS1:IL1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
125 |  |  |  | HR124 (Lo-16bits)
126 | MEAS1:IL1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
127 |  |  |  | HR126 (Lo-16bits)
128 | MEAS1:IL1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
129 |  |  |  | HR128 (Lo-16bits)
130 | MEAS1:IL1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
131 |  |  |  | HR130 (Lo-16bits)
132 | MEAS1:IL1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
133 |  |  |  | HR132 (Lo-16bits)
134 | MEAS1:IL1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
135 |  |  |  | HR134 (Lo-16bits)
136 | MEAS1:IL1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
137 |  |  |  | HR136 (Lo-16bits)
138 | MEAS1:IL1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
139 |  |  |  | HR138 (Lo-16bits)
140 | MEAS1:IL1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
141 |  |  |  | HR140 (Lo-16bits)
142 | MEAS1:IL1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
143 |  |  |  | HR142 (Lo-16bits)
144 | MEAS1:IL1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
145 |  |  |  | HR144 (Lo-16bits)
146 | MEAS1:IL1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
147 |  |  |  | HR146 (Lo-16bits)
148 | MEAS1:IL1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
149 |  |  |  | HR148 (Lo-16bits)
150 | MEAS1:IL1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
151 |  |  |  | HR150 (Lo-16bits)
152 | MEAS1:IL1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
153 |  |  |  | HR152 (Lo-16bits)
154 | MEAS1:IL1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
155 |  |  |  | HR154 (Lo-16bits)
156 | MEAS1:IL1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
157 |  |  |  | HR156 (Lo-16bits)
158 | MEAS1:IL1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
159 |  |  |  | HR158 (Lo-16bits)
160 | MEAS1:IL1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
161 |  |  |  | HR160 (Lo-16bits)
162 | MEAS1:IL1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
163 |  |  |  | HR162 (Lo-16bits)
164 | MEAS1:IL1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
165 |  |  |  | HR164 (Lo-16bits)
166 | MEAS1:IL1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
167 |  |  |  | HR166 (Lo-16bits)
168 | MEAS1:IL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
169 |  |  |  | HR168 (Lo-16bits)
170 | MEAS1:IL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
171 |  |  |  | HR170 (Lo-16bits)
172 | MEAS1:IL2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
173 |  |  |  | HR172 (Lo-16bits)
174 | MEAS1:IL2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
175 |  |  |  | HR174 (Lo-16bits)
176 | MEAS1:IL2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
177 |  |  |  | HR176 (Lo-16bits)
178 | MEAS1:IL2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
179 |  |  |  | HR178 (Lo-16bits)
180 | MEAS1:IL2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
181 |  |  |  | HR180 (Lo-16bits)
182 | MEAS1:IL2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
183 |  |  |  | HR182 (Lo-16bits)
184 | MEAS1:IL2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
185 |  |  |  | HR184 (Lo-16bits)
186 | MEAS1:IL2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
187 |  |  |  | HR186 (Lo-16bits)
188 | MEAS1:IL2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
189 |  |  |  | HR188 (Lo-16bits)
190 | MEAS1:IL2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
191 |  |  |  | HR190 (Lo-16bits)
192 | MEAS1:IL2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
193 |  |  |  | HR192 (Lo-16bits)
194 | MEAS1:IL2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
195 |  |  |  | HR194 (Lo-16bits)
196 | MEAS1:IL2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
197 |  |  |  | HR196 (Lo-16bits)
198 | MEAS1:IL2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
199 |  |  |  | HR198 (Lo-16bits)
200 | MEAS1:IL2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
201 |  |  |  | HR200 (Lo-16bits)
202 | MEAS1:IL2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
203 |  |  |  | HR202 (Lo-16bits)
204 | MEAS1:IL2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
205 |  |  |  | HR204 (Lo-16bits)
206 | MEAS1:IL2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
207 |  |  |  | HR206 (Lo-16bits)
208 | MEAS1:IL2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
209 |  |  |  | HR208 (Lo-16bits)
210 | MEAS1:IL2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
211 |  |  |  | HR210 (Lo-16bits)
212 | MEAS1:IL2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
213 |  |  |  | HR212 (Lo-16bits)
214 | MEAS1:IL2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
215 |  |  |  | HR214 (Lo-16bits)
216 | MEAS1:IL2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
217 |  |  |  | HR216 (Lo-16bits)
218 | MEAS1:IL2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
219 |  |  |  | HR218 (Lo-16bits)
220 | MEAS1:IL2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
221 |  |  |  | HR220 (Lo-16bits)
222 | MEAS1:IL2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
223 |  |  |  | HR222 (Lo-16bits)
224 | MEAS1:IL2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
225 |  |  |  | HR224 (Lo-16bits)
226 | MEAS1:IL2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
227 |  |  |  | HR226 (Lo-16bits)
228 | MEAS1:IL2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
229 |  |  |  | HR228 (Lo-16bits)
230 | MEAS1:IL2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
231 |  |  |  | HR230 (Lo-16bits)
232 | MEAS1:IL2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
233 |  |  |  | HR232 (Lo-16bits)
234 | MEAS1:IL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
235 |  |  |  | HR234 (Lo-16bits)
236 | MEAS1:IL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
237 |  |  |  | HR236 (Lo-16bits)
238 | MEAS1:IL3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
239 |  |  |  | HR238 (Lo-16bits)
240 | MEAS1:IL3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
241 |  |  |  | HR240 (Lo-16bits)
242 | MEAS1:IL3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
243 |  |  |  | HR242 (Lo-16bits)
244 | MEAS1:IL3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
245 |  |  |  | HR244 (Lo-16bits)
246 | MEAS1:IL3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
247 |  |  |  | HR246 (Lo-16bits)
248 | MEAS1:IL3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
249 |  |  |  | HR248 (Lo-16bits)
250 | MEAS1:IL3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
251 |  |  |  | HR250 (Lo-16bits)
252 | MEAS1:IL3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
253 |  |  |  | HR252 (Lo-16bits)
254 | MEAS1:IL3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
255 |  |  |  | HR254 (Lo-16bits)
256 | MEAS1:IL3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
257 |  |  |  | HR256 (Lo-16bits)
258 | MEAS1:IL3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
259 |  |  |  | HR258 (Lo-16bits)
260 | MEAS1:IL3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
261 |  |  |  | HR260 (Lo-16bits)
262 | MEAS1:IL3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
263 |  |  |  | HR262 (Lo-16bits)
264 | MEAS1:IL3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
265 |  |  |  | HR264 (Lo-16bits)
266 | MEAS1:IL3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
267 |  |  |  | HR266 (Lo-16bits)
268 | MEAS1:IL3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
269 |  |  |  | HR268 (Lo-16bits)
270 | MEAS1:IL3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
271 |  |  |  | HR270 (Lo-16bits)
272 | MEAS1:IL3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
273 |  |  |  | HR272 (Lo-16bits)
274 | MEAS1:IL3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
275 |  |  |  | HR274 (Lo-16bits)
276 | MEAS1:IL3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
277 |  |  |  | HR276 (Lo-16bits)
278 | MEAS1:IL3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
279 |  |  |  | HR278 (Lo-16bits)
280 | MEAS1:IL3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
281 |  |  |  | HR280 (Lo-16bits)
282 | MEAS1:IL3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
283 |  |  |  | HR282 (Lo-16bits)
284 | MEAS1:IL3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
285 |  |  |  | HR284 (Lo-16bits)
286 | MEAS1:IL3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
287 |  |  |  | HR286 (Lo-16bits)
288 | MEAS1:IL3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
289 |  |  |  | HR288 (Lo-16bits)
290 | MEAS1:IL3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
291 |  |  |  | HR290 (Lo-16bits)
292 | MEAS1:IL3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
293 |  |  |  | HR292 (Lo-16bits)
294 | MEAS1:IL3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
295 |  |  |  | HR294 (Lo-16bits)
296 | MEAS1:IL3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
297 |  |  |  | HR296 (Lo-16bits)
298 | MEAS1:IL3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
299 |  |  |  | HR298 (Lo-16bits)
300 | MEAS1:I01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
301 |  |  |  | HR300 (Lo-16bits)
302 | MEAS1:I01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
303 |  |  |  | HR302 (Lo-16bits)
304 | MEAS1:I01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
305 |  |  |  | HR304 (Lo-16bits)
306 | MEAS1:I01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
307 |  |  |  | HR306 (Lo-16bits)
308 | MEAS1:I01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
309 |  |  |  | HR308 (Lo-16bits)
310 | MEAS1:I01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
311 |  |  |  | HR310 (Lo-16bits)
312 | MEAS1:I01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
313 |  |  |  | HR312 (Lo-16bits)
314 | MEAS1:I01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
315 |  |  |  | HR314 (Lo-16bits)
316 | MEAS1:I01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
317 |  |  |  | HR316 (Lo-16bits)
318 | MEAS1:I01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
319 |  |  |  | HR318 (Lo-16bits)
320 | MEAS1:I01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
321 |  |  |  | HR320 (Lo-16bits)
322 | MEAS1:I01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
323 |  |  |  | HR322 (Lo-16bits)
324 | MEAS1:I01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
325 |  |  |  | HR324 (Lo-16bits)
326 | MEAS1:I01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
327 |  |  |  | HR326 (Lo-16bits)
328 | MEAS1:I01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
329 |  |  |  | HR328 (Lo-16bits)
330 | MEAS1:I01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
331 |  |  |  | HR330 (Lo-16bits)
332 | MEAS1:I01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
333 |  |  |  | HR332 (Lo-16bits)
334 | MEAS1:I01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
335 |  |  |  | HR334 (Lo-16bits)
336 | MEAS1:I01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
337 |  |  |  | HR336 (Lo-16bits)
338 | MEAS1:I01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
339 |  |  |  | HR338 (Lo-16bits)
340 | MEAS1:I01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
341 |  |  |  | HR340 (Lo-16bits)
342 | MEAS1:I01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
343 |  |  |  | HR342 (Lo-16bits)
344 | MEAS1:I01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
345 |  |  |  | HR344 (Lo-16bits)
346 | MEAS1:I01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
347 |  |  |  | HR346 (Lo-16bits)
348 | MEAS1:I01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
349 |  |  |  | HR348 (Lo-16bits)
350 | MEAS1:I01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
351 |  |  |  | HR350 (Lo-16bits)
352 | MEAS1:I01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
353 |  |  |  | HR352 (Lo-16bits)
354 | MEAS1:I01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
355 |  |  |  | HR354 (Lo-16bits)
356 | MEAS1:I01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
357 |  |  |  | HR356 (Lo-16bits)
358 | MEAS1:I01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
359 |  |  |  | HR358 (Lo-16bits)
360 | MEAS1:I01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
361 |  |  |  | HR360 (Lo-16bits)
362 | MEAS1:I01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
363 |  |  |  | HR362 (Lo-16bits)
364 | MEAS1:I01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
365 |  |  |  | HR364 (Lo-16bits)
366 | MEAS1:I02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
367 |  |  |  | HR366 (Lo-16bits)
368 | MEAS1:I02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
369 |  |  |  | HR368 (Lo-16bits)
370 | MEAS1:I02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
371 |  |  |  | HR370 (Lo-16bits)
372 | MEAS1:I02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
373 |  |  |  | HR372 (Lo-16bits)
374 | MEAS1:I02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
375 |  |  |  | HR374 (Lo-16bits)
376 | MEAS1:I02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
377 |  |  |  | HR376 (Lo-16bits)
378 | MEAS1:I02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
379 |  |  |  | HR378 (Lo-16bits)
380 | MEAS1:I02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
381 |  |  |  | HR380 (Lo-16bits)
382 | MEAS1:I02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
383 |  |  |  | HR382 (Lo-16bits)
384 | MEAS1:I02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
385 |  |  |  | HR384 (Lo-16bits)
386 | MEAS1:I02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
387 |  |  |  | HR386 (Lo-16bits)
388 | MEAS1:I02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
389 |  |  |  | HR388 (Lo-16bits)
390 | MEAS1:I02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
391 |  |  |  | HR390 (Lo-16bits)
392 | MEAS1:I02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
393 |  |  |  | HR392 (Lo-16bits)
394 | MEAS1:I02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
395 |  |  |  | HR394 (Lo-16bits)
396 | MEAS1:I02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
397 |  |  |  | HR396 (Lo-16bits)
398 | MEAS1:I02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
399 |  |  |  | HR398 (Lo-16bits)
400 | MEAS1:I02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
401 |  |  |  | HR400 (Lo-16bits)
402 | MEAS1:I02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
403 |  |  |  | HR402 (Lo-16bits)
404 | MEAS1:I02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
405 |  |  |  | HR404 (Lo-16bits)
406 | MEAS1:I02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
407 |  |  |  | HR406 (Lo-16bits)
408 | MEAS1:I02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
409 |  |  |  | HR408 (Lo-16bits)
410 | MEAS1:I02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
411 |  |  |  | HR410 (Lo-16bits)
412 | MEAS1:I02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
413 |  |  |  | HR412 (Lo-16bits)
414 | MEAS1:I02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
415 |  |  |  | HR414 (Lo-16bits)
416 | MEAS1:I02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
417 |  |  |  | HR416 (Lo-16bits)
418 | MEAS1:I02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
419 |  |  |  | HR418 (Lo-16bits)
420 | MEAS1:I02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
421 |  |  |  | HR420 (Lo-16bits)
422 | MEAS1:I02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
423 |  |  |  | HR422 (Lo-16bits)
424 | MEAS1:I02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
425 |  |  |  | HR424 (Lo-16bits)
426 | MEAS1:I02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
427 |  |  |  | HR426 (Lo-16bits)
428 | MEAS1:I02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
429 |  |  |  | HR428 (Lo-16bits)
430 | MEAS1:I02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
431 |  |  |  | HR430 (Lo-16bits)
432 | MEAS1:Meas1 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
433 |  |  |  | HR432 (Lo-16bits)
434 | MEAS2:Pri.Pha.curr.I''L1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
435 |  |  |  | HR434 (Lo-16bits)
436 | MEAS2:Pri.Pha.curr.I''L2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
437 |  |  |  | HR436 (Lo-16bits)
438 | MEAS2:Pri.Pha.curr.I''L3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
439 |  |  |  | HR438 (Lo-16bits)
440 | MEAS2:Pha.angle I''L1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
441 |  |  |  | HR440 (Lo-16bits)
442 | MEAS2:Pha.angle I''L2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
443 |  |  |  | HR442 (Lo-16bits)
444 | MEAS2:Pha.angle I''L3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
445 |  |  |  | HR444 (Lo-16bits)
446 | MEAS2:Pri.Res.curr.I''01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
447 |  |  |  | HR446 (Lo-16bits)
448 | MEAS2:Res.curr.angle I''01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
449 |  |  |  | HR448 (Lo-16bits)
450 | MEAS2:Pri.Res.curr.I''02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
451 |  |  |  | HR450 (Lo-16bits)
452 | MEAS2:Res.curr.angle I''02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
453 |  |  |  | HR452 (Lo-16bits)
454 | MEAS2:Pri.calc.I''0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
455 |  |  |  | HR454 (Lo-16bits)
456 | MEAS2:calc.I''0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
457 |  |  |  | HR456 (Lo-16bits)
458 | MEAS2:Pha.curr.I''L1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
459 |  |  |  | HR458 (Lo-16bits)
460 | MEAS2:Pha.curr.I''L2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
461 |  |  |  | HR460 (Lo-16bits)
462 | MEAS2:Pha.curr.I''L3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
463 |  |  |  | HR462 (Lo-16bits)
464 | MEAS2:I'' Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
465 |  |  |  | HR464 (Lo-16bits)
466 | MEAS2:I'' Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
467 |  |  |  | HR466 (Lo-16bits)
468 | MEAS2:I'' Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
469 |  |  |  | HR468 (Lo-16bits)
470 | MEAS2:I'' Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
471 |  |  |  | HR470 (Lo-16bits)
472 | MEAS2:I'' Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
473 |  |  |  | HR472 (Lo-16bits)
474 | MEAS2:I'' Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
475 |  |  |  | HR474 (Lo-16bits)
476 | MEAS2:Res.curr.I''01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
477 |  |  |  | HR476 (Lo-16bits)
478 | MEAS2:Res.curr.I''02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
479 |  |  |  | HR478 (Lo-16bits)
480 | MEAS2:Pha.I''L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
481 |  |  |  | HR480 (Lo-16bits)
482 | MEAS2:Pha.I''L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
483 |  |  |  | HR482 (Lo-16bits)
484 | MEAS2:Pha.I''L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
485 |  |  |  | HR484 (Lo-16bits)
486 | MEAS2:Pha.I''L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
487 |  |  |  | HR486 (Lo-16bits)
488 | MEAS2:Pha.I''L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
489 |  |  |  | HR488 (Lo-16bits)
490 | MEAS2:Pha.I''L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
491 |  |  |  | HR490 (Lo-16bits)
492 | MEAS2:Res.I''01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
493 |  |  |  | HR492 (Lo-16bits)
494 | MEAS2:Res.I''01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
495 |  |  |  | HR494 (Lo-16bits)
496 | MEAS2:Res.I''02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
497 |  |  |  | HR496 (Lo-16bits)
498 | MEAS2:Res.I''02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
499 |  |  |  | HR498 (Lo-16bits)
500 | MEAS2:P-P curr.I''L1 | R | 2 | FLOAT [0...500] (Hi-16bits)
501 |  |  |  | HR500 (Lo-16bits)
502 | MEAS2:P-P curr.I''L2 | R | 2 | FLOAT [0...500] (Hi-16bits)
503 |  |  |  | HR502 (Lo-16bits)
504 | MEAS2:P-P curr.I''L3 | R | 2 | FLOAT [0...500] (Hi-16bits)
505 |  |  |  | HR504 (Lo-16bits)
506 | MEAS2:P-P curr.I''01 | R | 2 | FLOAT [0...500] (Hi-16bits)
507 |  |  |  | HR506 (Lo-16bits)
508 | MEAS2:P-P curr.I''02 | R | 2 | FLOAT [0...500] (Hi-16bits)
509 |  |  |  | HR508 (Lo-16bits)
510 | MEAS2:I''L1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
511 |  |  |  | HR510 (Lo-16bits)
512 | MEAS2:I''L1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
513 |  |  |  | HR512 (Lo-16bits)
514 | MEAS2:I''L1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
515 |  |  |  | HR514 (Lo-16bits)
516 | MEAS2:I''L1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
517 |  |  |  | HR516 (Lo-16bits)
518 | MEAS2:I''L1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
519 |  |  |  | HR518 (Lo-16bits)
520 | MEAS2:I''L1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
521 |  |  |  | HR520 (Lo-16bits)
522 | MEAS2:I''L1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
523 |  |  |  | HR522 (Lo-16bits)
524 | MEAS2:I''L1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
525 |  |  |  | HR524 (Lo-16bits)
526 | MEAS2:I''L1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
527 |  |  |  | HR526 (Lo-16bits)
528 | MEAS2:I''L1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
529 |  |  |  | HR528 (Lo-16bits)
530 | MEAS2:I''L1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
531 |  |  |  | HR530 (Lo-16bits)
532 | MEAS2:I''L1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
533 |  |  |  | HR532 (Lo-16bits)
534 | MEAS2:I''L1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
535 |  |  |  | HR534 (Lo-16bits)
536 | MEAS2:I''L1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
537 |  |  |  | HR536 (Lo-16bits)
538 | MEAS2:I''L1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
539 |  |  |  | HR538 (Lo-16bits)
540 | MEAS2:I''L1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
541 |  |  |  | HR540 (Lo-16bits)
542 | MEAS2:I''L1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
543 |  |  |  | HR542 (Lo-16bits)
544 | MEAS2:I''L1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
545 |  |  |  | HR544 (Lo-16bits)
546 | MEAS2:I''L1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
547 |  |  |  | HR546 (Lo-16bits)
548 | MEAS2:I''L1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
549 |  |  |  | HR548 (Lo-16bits)
550 | MEAS2:I''L1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
551 |  |  |  | HR550 (Lo-16bits)
552 | MEAS2:I''L1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
553 |  |  |  | HR552 (Lo-16bits)
554 | MEAS2:I''L1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
555 |  |  |  | HR554 (Lo-16bits)
556 | MEAS2:I''L1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
557 |  |  |  | HR556 (Lo-16bits)
558 | MEAS2:I''L1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
559 |  |  |  | HR558 (Lo-16bits)
560 | MEAS2:I''L1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
561 |  |  |  | HR560 (Lo-16bits)
562 | MEAS2:I''L1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
563 |  |  |  | HR562 (Lo-16bits)
564 | MEAS2:I''L1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
565 |  |  |  | HR564 (Lo-16bits)
566 | MEAS2:I''L1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
567 |  |  |  | HR566 (Lo-16bits)
568 | MEAS2:I''L1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
569 |  |  |  | HR568 (Lo-16bits)
570 | MEAS2:I''L1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
571 |  |  |  | HR570 (Lo-16bits)
572 | MEAS2:I''L1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
573 |  |  |  | HR572 (Lo-16bits)
574 | MEAS2:I''L1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
575 |  |  |  | HR574 (Lo-16bits)
576 | MEAS2:I''L2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
577 |  |  |  | HR576 (Lo-16bits)
578 | MEAS2:I''L2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
579 |  |  |  | HR578 (Lo-16bits)
580 | MEAS2:I''L2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
581 |  |  |  | HR580 (Lo-16bits)
582 | MEAS2:I''L2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
583 |  |  |  | HR582 (Lo-16bits)
584 | MEAS2:I''L2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
585 |  |  |  | HR584 (Lo-16bits)
586 | MEAS2:I''L2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
587 |  |  |  | HR586 (Lo-16bits)
588 | MEAS2:I''L2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
589 |  |  |  | HR588 (Lo-16bits)
590 | MEAS2:I''L2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
591 |  |  |  | HR590 (Lo-16bits)
592 | MEAS2:I''L2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
593 |  |  |  | HR592 (Lo-16bits)
594 | MEAS2:I''L2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
595 |  |  |  | HR594 (Lo-16bits)
596 | MEAS2:I''L2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
597 |  |  |  | HR596 (Lo-16bits)
598 | MEAS2:I''L2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
599 |  |  |  | HR598 (Lo-16bits)
600 | MEAS2:I''L2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
601 |  |  |  | HR600 (Lo-16bits)
602 | MEAS2:I''L2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
603 |  |  |  | HR602 (Lo-16bits)
604 | MEAS2:I''L2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
605 |  |  |  | HR604 (Lo-16bits)
606 | MEAS2:I''L2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
607 |  |  |  | HR606 (Lo-16bits)
608 | MEAS2:I''L2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
609 |  |  |  | HR608 (Lo-16bits)
610 | MEAS2:I''L2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
611 |  |  |  | HR610 (Lo-16bits)
612 | MEAS2:I''L2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
613 |  |  |  | HR612 (Lo-16bits)
614 | MEAS2:I''L2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
615 |  |  |  | HR614 (Lo-16bits)
616 | MEAS2:I''L2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
617 |  |  |  | HR616 (Lo-16bits)
618 | MEAS2:I''L2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
619 |  |  |  | HR618 (Lo-16bits)
620 | MEAS2:I''L2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
621 |  |  |  | HR620 (Lo-16bits)
622 | MEAS2:I''L2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
623 |  |  |  | HR622 (Lo-16bits)
624 | MEAS2:I''L2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
625 |  |  |  | HR624 (Lo-16bits)
626 | MEAS2:I''L2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
627 |  |  |  | HR626 (Lo-16bits)
628 | MEAS2:I''L2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
629 |  |  |  | HR628 (Lo-16bits)
630 | MEAS2:I''L2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
631 |  |  |  | HR630 (Lo-16bits)
632 | MEAS2:I''L2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
633 |  |  |  | HR632 (Lo-16bits)
634 | MEAS2:I''L2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
635 |  |  |  | HR634 (Lo-16bits)
636 | MEAS2:I''L2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
637 |  |  |  | HR636 (Lo-16bits)
638 | MEAS2:I''L2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
639 |  |  |  | HR638 (Lo-16bits)
640 | MEAS2:I''L2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
641 |  |  |  | HR640 (Lo-16bits)
642 | MEAS2:I''L3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
643 |  |  |  | HR642 (Lo-16bits)
644 | MEAS2:I''L3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
645 |  |  |  | HR644 (Lo-16bits)
646 | MEAS2:I''L3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
647 |  |  |  | HR646 (Lo-16bits)
648 | MEAS2:I''L3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
649 |  |  |  | HR648 (Lo-16bits)
650 | MEAS2:I''L3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
651 |  |  |  | HR650 (Lo-16bits)
652 | MEAS2:I''L3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
653 |  |  |  | HR652 (Lo-16bits)
654 | MEAS2:I''L3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
655 |  |  |  | HR654 (Lo-16bits)
656 | MEAS2:I''L3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
657 |  |  |  | HR656 (Lo-16bits)
658 | MEAS2:I''L3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
659 |  |  |  | HR658 (Lo-16bits)
660 | MEAS2:I''L3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
661 |  |  |  | HR660 (Lo-16bits)
662 | MEAS2:I''L3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
663 |  |  |  | HR662 (Lo-16bits)
664 | MEAS2:I''L3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
665 |  |  |  | HR664 (Lo-16bits)
666 | MEAS2:I''L3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
667 |  |  |  | HR666 (Lo-16bits)
668 | MEAS2:I''L3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
669 |  |  |  | HR668 (Lo-16bits)
670 | MEAS2:I''L3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
671 |  |  |  | HR670 (Lo-16bits)
672 | MEAS2:I''L3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
673 |  |  |  | HR672 (Lo-16bits)
674 | MEAS2:I''L3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
675 |  |  |  | HR674 (Lo-16bits)
676 | MEAS2:I''L3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
677 |  |  |  | HR676 (Lo-16bits)
678 | MEAS2:I''L3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
679 |  |  |  | HR678 (Lo-16bits)
680 | MEAS2:I''L3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
681 |  |  |  | HR680 (Lo-16bits)
682 | MEAS2:I''L3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
683 |  |  |  | HR682 (Lo-16bits)
684 | MEAS2:I''L3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
685 |  |  |  | HR684 (Lo-16bits)
686 | MEAS2:I''L3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
687 |  |  |  | HR686 (Lo-16bits)
688 | MEAS2:I''L3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
689 |  |  |  | HR688 (Lo-16bits)
690 | MEAS2:I''L3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
691 |  |  |  | HR690 (Lo-16bits)
692 | MEAS2:I''L3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
693 |  |  |  | HR692 (Lo-16bits)
694 | MEAS2:I''L3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
695 |  |  |  | HR694 (Lo-16bits)
696 | MEAS2:I''L3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
697 |  |  |  | HR696 (Lo-16bits)
698 | MEAS2:I''L3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
699 |  |  |  | HR698 (Lo-16bits)
700 | MEAS2:I''L3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
701 |  |  |  | HR700 (Lo-16bits)
702 | MEAS2:I''L3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
703 |  |  |  | HR702 (Lo-16bits)
704 | MEAS2:I''L3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
705 |  |  |  | HR704 (Lo-16bits)
706 | MEAS2:I''L3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
707 |  |  |  | HR706 (Lo-16bits)
708 | MEAS2:I''01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
709 |  |  |  | HR708 (Lo-16bits)
710 | MEAS2:I''01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
711 |  |  |  | HR710 (Lo-16bits)
712 | MEAS2:I''01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
713 |  |  |  | HR712 (Lo-16bits)
714 | MEAS2:I''01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
715 |  |  |  | HR714 (Lo-16bits)
716 | MEAS2:I''01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
717 |  |  |  | HR716 (Lo-16bits)
718 | MEAS2:I''01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
719 |  |  |  | HR718 (Lo-16bits)
720 | MEAS2:I''01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
721 |  |  |  | HR720 (Lo-16bits)
722 | MEAS2:I''01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
723 |  |  |  | HR722 (Lo-16bits)
724 | MEAS2:I''01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
725 |  |  |  | HR724 (Lo-16bits)
726 | MEAS2:I''01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
727 |  |  |  | HR726 (Lo-16bits)
728 | MEAS2:I''01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
729 |  |  |  | HR728 (Lo-16bits)
730 | MEAS2:I''01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
731 |  |  |  | HR730 (Lo-16bits)
732 | MEAS2:I''01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
733 |  |  |  | HR732 (Lo-16bits)
734 | MEAS2:I''01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
735 |  |  |  | HR734 (Lo-16bits)
736 | MEAS2:I''01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
737 |  |  |  | HR736 (Lo-16bits)
738 | MEAS2:I''01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
739 |  |  |  | HR738 (Lo-16bits)
740 | MEAS2:I''01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
741 |  |  |  | HR740 (Lo-16bits)
742 | MEAS2:I''01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
743 |  |  |  | HR742 (Lo-16bits)
744 | MEAS2:I''01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
745 |  |  |  | HR744 (Lo-16bits)
746 | MEAS2:I''01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
747 |  |  |  | HR746 (Lo-16bits)
748 | MEAS2:I''01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
749 |  |  |  | HR748 (Lo-16bits)
750 | MEAS2:I''01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
751 |  |  |  | HR750 (Lo-16bits)
752 | MEAS2:I''01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
753 |  |  |  | HR752 (Lo-16bits)
754 | MEAS2:I''01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
755 |  |  |  | HR754 (Lo-16bits)
756 | MEAS2:I''01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
757 |  |  |  | HR756 (Lo-16bits)
758 | MEAS2:I''01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
759 |  |  |  | HR758 (Lo-16bits)
760 | MEAS2:I''01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
761 |  |  |  | HR760 (Lo-16bits)
762 | MEAS2:I''01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
763 |  |  |  | HR762 (Lo-16bits)
764 | MEAS2:I''01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
765 |  |  |  | HR764 (Lo-16bits)
766 | MEAS2:I''01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
767 |  |  |  | HR766 (Lo-16bits)
768 | MEAS2:I''01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
769 |  |  |  | HR768 (Lo-16bits)
770 | MEAS2:I''01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
771 |  |  |  | HR770 (Lo-16bits)
772 | MEAS2:I''01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
773 |  |  |  | HR772 (Lo-16bits)
774 | MEAS2:I''02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
775 |  |  |  | HR774 (Lo-16bits)
776 | MEAS2:I''02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
777 |  |  |  | HR776 (Lo-16bits)
778 | MEAS2:I''02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
779 |  |  |  | HR778 (Lo-16bits)
780 | MEAS2:I''02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
781 |  |  |  | HR780 (Lo-16bits)
782 | MEAS2:I''02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
783 |  |  |  | HR782 (Lo-16bits)
784 | MEAS2:I''02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
785 |  |  |  | HR784 (Lo-16bits)
786 | MEAS2:I''02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
787 |  |  |  | HR786 (Lo-16bits)
788 | MEAS2:I''02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
789 |  |  |  | HR788 (Lo-16bits)
790 | MEAS2:I''02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
791 |  |  |  | HR790 (Lo-16bits)
792 | MEAS2:I''02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
793 |  |  |  | HR792 (Lo-16bits)
794 | MEAS2:I''02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
795 |  |  |  | HR794 (Lo-16bits)
796 | MEAS2:I''02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
797 |  |  |  | HR796 (Lo-16bits)
798 | MEAS2:I''02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
799 |  |  |  | HR798 (Lo-16bits)
800 | MEAS2:I''02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
801 |  |  |  | HR800 (Lo-16bits)
802 | MEAS2:I''02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
803 |  |  |  | HR802 (Lo-16bits)
804 | MEAS2:I''02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
805 |  |  |  | HR804 (Lo-16bits)
806 | MEAS2:I''02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
807 |  |  |  | HR806 (Lo-16bits)
808 | MEAS2:I''02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
809 |  |  |  | HR808 (Lo-16bits)
810 | MEAS2:I''02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
811 |  |  |  | HR810 (Lo-16bits)
812 | MEAS2:I''02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
813 |  |  |  | HR812 (Lo-16bits)
814 | MEAS2:I''02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
815 |  |  |  | HR814 (Lo-16bits)
816 | MEAS2:I''02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
817 |  |  |  | HR816 (Lo-16bits)
818 | MEAS2:I''02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
819 |  |  |  | HR818 (Lo-16bits)
820 | MEAS2:I''02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
821 |  |  |  | HR820 (Lo-16bits)
822 | MEAS2:I''02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
823 |  |  |  | HR822 (Lo-16bits)
824 | MEAS2:I''02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
825 |  |  |  | HR824 (Lo-16bits)
826 | MEAS2:I''02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
827 |  |  |  | HR826 (Lo-16bits)
828 | MEAS2:I''02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
829 |  |  |  | HR828 (Lo-16bits)
830 | MEAS2:I''02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
831 |  |  |  | HR830 (Lo-16bits)
832 | MEAS2:I''02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
833 |  |  |  | HR832 (Lo-16bits)
834 | MEAS2:I''02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
835 |  |  |  | HR834 (Lo-16bits)
836 | MEAS2:I''02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
837 |  |  |  | HR836 (Lo-16bits)
838 | MEAS2:I''02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
839 |  |  |  | HR838 (Lo-16bits)
840 | MEAS2:MEAS2 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
841 |  |  |  | HR840 (Lo-16bits)
842 | MEAS3:U1Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
843 |  |  |  | HR842 (Lo-16bits)
844 | MEAS3:U1Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
845 |  |  |  | HR844 (Lo-16bits)
846 | MEAS3:U2Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
847 |  |  |  | HR846 (Lo-16bits)
848 | MEAS3:U2Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
849 |  |  |  | HR848 (Lo-16bits)
850 | MEAS3:U3Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
851 |  |  |  | HR850 (Lo-16bits)
852 | MEAS3:U3Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
853 |  |  |  | HR852 (Lo-16bits)
854 | MEAS3:U4Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
855 |  |  |  | HR854 (Lo-16bits)
856 | MEAS3:U4Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
857 |  |  |  | HR856 (Lo-16bits)
858 | MEAS3:U1Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
859 |  |  |  | HR858 (Lo-16bits)
860 | MEAS3:U1Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
861 |  |  |  | HR860 (Lo-16bits)
862 | MEAS3:U2Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
863 |  |  |  | HR862 (Lo-16bits)
864 | MEAS3:U2Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
865 |  |  |  | HR864 (Lo-16bits)
866 | MEAS3:U3Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
867 |  |  |  | HR866 (Lo-16bits)
868 | MEAS3:U3Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
869 |  |  |  | HR868 (Lo-16bits)
870 | MEAS3:U4Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
871 |  |  |  | HR870 (Lo-16bits)
872 | MEAS3:U4Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
873 |  |  |  | HR872 (Lo-16bits)
874 | MEAS3:Pos.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
875 |  |  |  | HR874 (Lo-16bits)
876 | MEAS3:Pos.seq.Volt.sec | R | 2 | FLOAT [0...480] (Hi-16bits)
877 |  |  |  | HR876 (Lo-16bits)
878 | MEAS3:Neg.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
879 |  |  |  | HR878 (Lo-16bits)
880 | MEAS3:Neg.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
881 |  |  |  | HR880 (Lo-16bits)
882 | MEAS3:Zero.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
883 |  |  |  | HR882 (Lo-16bits)
884 | MEAS3:Zero.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
885 |  |  |  | HR884 (Lo-16bits)
886 | MEAS3:U0 Calc. pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
887 |  |  |  | HR886 (Lo-16bits)
888 | MEAS3:U0 Calc.Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
889 |  |  |  | HR888 (Lo-16bits)
890 | MEAS3:U1 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
891 |  |  |  | HR890 (Lo-16bits)
892 | MEAS3:U2 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
893 |  |  |  | HR892 (Lo-16bits)
894 | MEAS3:U3 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
895 |  |  |  | HR894 (Lo-16bits)
896 | MEAS3:U4 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
897 |  |  |  | HR896 (Lo-16bits)
898 | MEAS3:Pos.Seq volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
899 |  |  |  | HR898 (Lo-16bits)
900 | MEAS3:Neg.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
901 |  |  |  | HR900 (Lo-16bits)
902 | MEAS3:Zero.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
903 |  |  |  | HR902 (Lo-16bits)
904 | MEAS3:System volt UL12 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
905 |  |  |  | HR904 (Lo-16bits)
906 | MEAS3:System volt UL12 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
907 |  |  |  | HR906 (Lo-16bits)
908 | MEAS3:System volt UL12 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
909 |  |  |  | HR908 (Lo-16bits)
910 | MEAS3:System volt UL23 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
911 |  |  |  | HR910 (Lo-16bits)
912 | MEAS3:System volt UL23 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
913 |  |  |  | HR912 (Lo-16bits)
914 | MEAS3:System volt UL23 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
915 |  |  |  | HR914 (Lo-16bits)
916 | MEAS3:System volt UL31 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
917 |  |  |  | HR916 (Lo-16bits)
918 | MEAS3:System volt UL31 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
919 |  |  |  | HR918 (Lo-16bits)
920 | MEAS3:System volt UL31 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
921 |  |  |  | HR920 (Lo-16bits)
922 | MEAS3:System volt UL1 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
923 |  |  |  | HR922 (Lo-16bits)
924 | MEAS3:System volt UL1 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
925 |  |  |  | HR924 (Lo-16bits)
926 | MEAS3:System volt UL1 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
927 |  |  |  | HR926 (Lo-16bits)
928 | MEAS3:System volt UL2 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
929 |  |  |  | HR928 (Lo-16bits)
930 | MEAS3:System volt UL2 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
931 |  |  |  | HR930 (Lo-16bits)
932 | MEAS3:System volt UL2 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
933 |  |  |  | HR932 (Lo-16bits)
934 | MEAS3:System volt UL3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
935 |  |  |  | HR934 (Lo-16bits)
936 | MEAS3:System volt UL3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
937 |  |  |  | HR936 (Lo-16bits)
938 | MEAS3:System volt UL3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
939 |  |  |  | HR938 (Lo-16bits)
940 | MEAS3:System volt U0 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
941 |  |  |  | HR940 (Lo-16bits)
942 | MEAS3:System volt U0 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
943 |  |  |  | HR942 (Lo-16bits)
944 | MEAS3:System volt U0 mag(%) | R | 2 | FLOAT [0...120] (Hi-16bits)
945 |  |  |  | HR944 (Lo-16bits)
946 | MEAS3:System volt U0 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
947 |  |  |  | HR946 (Lo-16bits)
948 | MEAS3:System volt U3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
949 |  |  |  | HR948 (Lo-16bits)
950 | MEAS3:System volt U3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
951 |  |  |  | HR950 (Lo-16bits)
952 | MEAS3:System volt U3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
953 |  |  |  | HR952 (Lo-16bits)
954 | MEAS3:System volt U4 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
955 |  |  |  | HR954 (Lo-16bits)
956 | MEAS3:System volt U4 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
957 |  |  |  | HR956 (Lo-16bits)
958 | MEAS3:System volt U4 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
959 |  |  |  | HR958 (Lo-16bits)
960 | MEAS3:System volt UL1 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
961 |  |  |  | HR960 (Lo-16bits)
962 | MEAS3:System volt UL2 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
963 |  |  |  | HR962 (Lo-16bits)
964 | MEAS3:System volt UL3 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
965 |  |  |  | HR964 (Lo-16bits)
966 | MEAS3:UL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
967 |  |  |  | HR966 (Lo-16bits)
968 | MEAS3:UL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
969 |  |  |  | HR968 (Lo-16bits)
970 | MEAS3:UL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
971 |  |  |  | HR970 (Lo-16bits)
972 | MEAS3:UL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
973 |  |  |  | HR972 (Lo-16bits)
974 | MEAS3:UL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
975 |  |  |  | HR974 (Lo-16bits)
976 | MEAS3:UL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
977 |  |  |  | HR976 (Lo-16bits)
978 | MEAS3:U1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
979 |  |  |  | HR978 (Lo-16bits)
980 | MEAS3:U1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
981 |  |  |  | HR980 (Lo-16bits)
982 | MEAS3:U1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
983 |  |  |  | HR982 (Lo-16bits)
984 | MEAS3:U1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
985 |  |  |  | HR984 (Lo-16bits)
986 | MEAS3:U1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
987 |  |  |  | HR986 (Lo-16bits)
988 | MEAS3:U1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
989 |  |  |  | HR988 (Lo-16bits)
990 | MEAS3:U1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
991 |  |  |  | HR990 (Lo-16bits)
992 | MEAS3:U1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
993 |  |  |  | HR992 (Lo-16bits)
994 | MEAS3:U1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
995 |  |  |  | HR994 (Lo-16bits)
996 | MEAS3:U1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
997 |  |  |  | HR996 (Lo-16bits)
998 | MEAS3:U1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
999 |  |  |  | HR998 (Lo-16bits)
1000 | MEAS3:U1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1001 |  |  |  | HR1000 (Lo-16bits)
1002 | MEAS3:U1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1003 |  |  |  | HR1002 (Lo-16bits)
1004 | MEAS3:U1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1005 |  |  |  | HR1004 (Lo-16bits)
1006 | MEAS3:U1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1007 |  |  |  | HR1006 (Lo-16bits)
1008 | MEAS3:U1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1009 |  |  |  | HR1008 (Lo-16bits)
1010 | MEAS3:U1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1011 |  |  |  | HR1010 (Lo-16bits)
1012 | MEAS3:U1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1013 |  |  |  | HR1012 (Lo-16bits)
1014 | MEAS3:U1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1015 |  |  |  | HR1014 (Lo-16bits)
1016 | MEAS3:U1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1017 |  |  |  | HR1016 (Lo-16bits)
1018 | MEAS3:U1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1019 |  |  |  | HR1018 (Lo-16bits)
1020 | MEAS3:U1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1021 |  |  |  | HR1020 (Lo-16bits)
1022 | MEAS3:U1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1023 |  |  |  | HR1022 (Lo-16bits)
1024 | MEAS3:U1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1025 |  |  |  | HR1024 (Lo-16bits)
1026 | MEAS3:U1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1027 |  |  |  | HR1026 (Lo-16bits)
1028 | MEAS3:U1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1029 |  |  |  | HR1028 (Lo-16bits)
1030 | MEAS3:U1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1031 |  |  |  | HR1030 (Lo-16bits)
1032 | MEAS3:U1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1033 |  |  |  | HR1032 (Lo-16bits)
1034 | MEAS3:U1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1035 |  |  |  | HR1034 (Lo-16bits)
1036 | MEAS3:U1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1037 |  |  |  | HR1036 (Lo-16bits)
1038 | MEAS3:U1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1039 |  |  |  | HR1038 (Lo-16bits)
1040 | MEAS3:U2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1041 |  |  |  | HR1040 (Lo-16bits)
1042 | MEAS3:U2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1043 |  |  |  | HR1042 (Lo-16bits)
1044 | MEAS3:U2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1045 |  |  |  | HR1044 (Lo-16bits)
1046 | MEAS3:U2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1047 |  |  |  | HR1046 (Lo-16bits)
1048 | MEAS3:U2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1049 |  |  |  | HR1048 (Lo-16bits)
1050 | MEAS3:U2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1051 |  |  |  | HR1050 (Lo-16bits)
1052 | MEAS3:U2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1053 |  |  |  | HR1052 (Lo-16bits)
1054 | MEAS3:U2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1055 |  |  |  | HR1054 (Lo-16bits)
1056 | MEAS3:U2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1057 |  |  |  | HR1056 (Lo-16bits)
1058 | MEAS3:U2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1059 |  |  |  | HR1058 (Lo-16bits)
1060 | MEAS3:U2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1061 |  |  |  | HR1060 (Lo-16bits)
1062 | MEAS3:U2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1063 |  |  |  | HR1062 (Lo-16bits)
1064 | MEAS3:U2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1065 |  |  |  | HR1064 (Lo-16bits)
1066 | MEAS3:U2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1067 |  |  |  | HR1066 (Lo-16bits)
1068 | MEAS3:U2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1069 |  |  |  | HR1068 (Lo-16bits)
1070 | MEAS3:U2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1071 |  |  |  | HR1070 (Lo-16bits)
1072 | MEAS3:U2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1073 |  |  |  | HR1072 (Lo-16bits)
1074 | MEAS3:U2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1075 |  |  |  | HR1074 (Lo-16bits)
1076 | MEAS3:U2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1077 |  |  |  | HR1076 (Lo-16bits)
1078 | MEAS3:U2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1079 |  |  |  | HR1078 (Lo-16bits)
1080 | MEAS3:U2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1081 |  |  |  | HR1080 (Lo-16bits)
1082 | MEAS3:U2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1083 |  |  |  | HR1082 (Lo-16bits)
1084 | MEAS3:U2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1085 |  |  |  | HR1084 (Lo-16bits)
1086 | MEAS3:U2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1087 |  |  |  | HR1086 (Lo-16bits)
1088 | MEAS3:U2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1089 |  |  |  | HR1088 (Lo-16bits)
1090 | MEAS3:U2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1091 |  |  |  | HR1090 (Lo-16bits)
1092 | MEAS3:U2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1093 |  |  |  | HR1092 (Lo-16bits)
1094 | MEAS3:U2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1095 |  |  |  | HR1094 (Lo-16bits)
1096 | MEAS3:U2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1097 |  |  |  | HR1096 (Lo-16bits)
1098 | MEAS3:U2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1099 |  |  |  | HR1098 (Lo-16bits)
1100 | MEAS3:U2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1101 |  |  |  | HR1100 (Lo-16bits)
1102 | MEAS3:U3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1103 |  |  |  | HR1102 (Lo-16bits)
1104 | MEAS3:U3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1105 |  |  |  | HR1104 (Lo-16bits)
1106 | MEAS3:U3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1107 |  |  |  | HR1106 (Lo-16bits)
1108 | MEAS3:U3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1109 |  |  |  | HR1108 (Lo-16bits)
1110 | MEAS3:U3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1111 |  |  |  | HR1110 (Lo-16bits)
1112 | MEAS3:U3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1113 |  |  |  | HR1112 (Lo-16bits)
1114 | MEAS3:U3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1115 |  |  |  | HR1114 (Lo-16bits)
1116 | MEAS3:U3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1117 |  |  |  | HR1116 (Lo-16bits)
1118 | MEAS3:U3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1119 |  |  |  | HR1118 (Lo-16bits)
1120 | MEAS3:U3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1121 |  |  |  | HR1120 (Lo-16bits)
1122 | MEAS3:U3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1123 |  |  |  | HR1122 (Lo-16bits)
1124 | MEAS3:U3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1125 |  |  |  | HR1124 (Lo-16bits)
1126 | MEAS3:U3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1127 |  |  |  | HR1126 (Lo-16bits)
1128 | MEAS3:U3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1129 |  |  |  | HR1128 (Lo-16bits)
1130 | MEAS3:U3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1131 |  |  |  | HR1130 (Lo-16bits)
1132 | MEAS3:U3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1133 |  |  |  | HR1132 (Lo-16bits)
1134 | MEAS3:U3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1135 |  |  |  | HR1134 (Lo-16bits)
1136 | MEAS3:U3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1137 |  |  |  | HR1136 (Lo-16bits)
1138 | MEAS3:U3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1139 |  |  |  | HR1138 (Lo-16bits)
1140 | MEAS3:U3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1141 |  |  |  | HR1140 (Lo-16bits)
1142 | MEAS3:U3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1143 |  |  |  | HR1142 (Lo-16bits)
1144 | MEAS3:U3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1145 |  |  |  | HR1144 (Lo-16bits)
1146 | MEAS3:U3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1147 |  |  |  | HR1146 (Lo-16bits)
1148 | MEAS3:U3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1149 |  |  |  | HR1148 (Lo-16bits)
1150 | MEAS3:U3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1151 |  |  |  | HR1150 (Lo-16bits)
1152 | MEAS3:U3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1153 |  |  |  | HR1152 (Lo-16bits)
1154 | MEAS3:U3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1155 |  |  |  | HR1154 (Lo-16bits)
1156 | MEAS3:U3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1157 |  |  |  | HR1156 (Lo-16bits)
1158 | MEAS3:U3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1159 |  |  |  | HR1158 (Lo-16bits)
1160 | MEAS3:U3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1161 |  |  |  | HR1160 (Lo-16bits)
1162 | MEAS3:U3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1163 |  |  |  | HR1162 (Lo-16bits)
1164 | MEAS3:U4 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1165 |  |  |  | HR1164 (Lo-16bits)
1166 | MEAS3:U4 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1167 |  |  |  | HR1166 (Lo-16bits)
1168 | MEAS3:U4 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1169 |  |  |  | HR1168 (Lo-16bits)
1170 | MEAS3:U4 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1171 |  |  |  | HR1170 (Lo-16bits)
1172 | MEAS3:U4 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1173 |  |  |  | HR1172 (Lo-16bits)
1174 | MEAS3:U4 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1175 |  |  |  | HR1174 (Lo-16bits)
1176 | MEAS3:U4 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1177 |  |  |  | HR1176 (Lo-16bits)
1178 | MEAS3:U4 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1179 |  |  |  | HR1178 (Lo-16bits)
1180 | MEAS3:U4 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1181 |  |  |  | HR1180 (Lo-16bits)
1182 | MEAS3:U4 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1183 |  |  |  | HR1182 (Lo-16bits)
1184 | MEAS3:U4 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1185 |  |  |  | HR1184 (Lo-16bits)
1186 | MEAS3:U4 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1187 |  |  |  | HR1186 (Lo-16bits)
1188 | MEAS3:U4 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1189 |  |  |  | HR1188 (Lo-16bits)
1190 | MEAS3:U4 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1191 |  |  |  | HR1190 (Lo-16bits)
1192 | MEAS3:U4 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1193 |  |  |  | HR1192 (Lo-16bits)
1194 | MEAS3:U4 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1195 |  |  |  | HR1194 (Lo-16bits)
1196 | MEAS3:U4 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1197 |  |  |  | HR1196 (Lo-16bits)
1198 | MEAS3:U4 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1199 |  |  |  | HR1198 (Lo-16bits)
1200 | MEAS3:U4 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1201 |  |  |  | HR1200 (Lo-16bits)
1202 | MEAS3:U4 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1203 |  |  |  | HR1202 (Lo-16bits)
1204 | MEAS3:U4 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1205 |  |  |  | HR1204 (Lo-16bits)
1206 | MEAS3:U4 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1207 |  |  |  | HR1206 (Lo-16bits)
1208 | MEAS3:U4 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1209 |  |  |  | HR1208 (Lo-16bits)
1210 | MEAS3:U4 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1211 |  |  |  | HR1210 (Lo-16bits)
1212 | MEAS3:U4 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1213 |  |  |  | HR1212 (Lo-16bits)
1214 | MEAS3:U4 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1215 |  |  |  | HR1214 (Lo-16bits)
1216 | MEAS3:U4 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1217 |  |  |  | HR1216 (Lo-16bits)
1218 | MEAS3:U4 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1219 |  |  |  | HR1218 (Lo-16bits)
1220 | MEAS3:U4 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1221 |  |  |  | HR1220 (Lo-16bits)
1222 | MEAS3:U4 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1223 |  |  |  | HR1222 (Lo-16bits)
1224 | MEAS3:U4 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1225 |  |  |  | HR1224 (Lo-16bits)
1226 | IMERX:IL1 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1227 |  |  |  | HR1226 (Lo-16bits)
1228 | IMERX:IL1 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1229 |  |  |  | HR1228 (Lo-16bits)
1230 | IMERX:IL2 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1231 |  |  |  | HR1230 (Lo-16bits)
1232 | IMERX:IL2 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1233 |  |  |  | HR1232 (Lo-16bits)
1234 | IMERX:IL3 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1235 |  |  |  | HR1234 (Lo-16bits)
1236 | IMERX:IL3 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1237 |  |  |  | HR1236 (Lo-16bits)
1238 | IMERX:Pos.seq. Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1239 |  |  |  | HR1238 (Lo-16bits)
1240 | IMERX:Pos.Seq. Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1241 |  |  |  | HR1240 (Lo-16bits)
1242 | IMERX:I01 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1243 |  |  |  | HR1242 (Lo-16bits)
1244 | IMERX:I01 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1245 |  |  |  | HR1244 (Lo-16bits)
1246 | IMERX:I02 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1247 |  |  |  | HR1246 (Lo-16bits)
1248 | IMERX:I02 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1249 |  |  |  | HR1248 (Lo-16bits)
1250 | IMERX:I01 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1251 |  |  |  | HR1250 (Lo-16bits)
1252 | IMERX:I01 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1253 |  |  |  | HR1252 (Lo-16bits)
1254 | IMERX:I02 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1255 |  |  |  | HR1254 (Lo-16bits)
1256 | IMERX:I02 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1257 |  |  |  | HR1256 (Lo-16bits)
1258 | POW1:Export Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1259 |  |  |  | HR1258 (Lo-16bits)
1260 | POW1:Export Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1261 |  |  |  | HR1260 (Lo-16bits)
1262 | POW1:Import Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1263 |  |  |  | HR1262 (Lo-16bits)
1264 | POW1:Import Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1265 |  |  |  | HR1264 (Lo-16bits)
1266 | POW1:Active Energy (P) Export/Import balance MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1267 |  |  |  | HR1266 (Lo-16bits)
1268 | POW1:Active Energy (P) Export/Import balance kWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1269 |  |  |  | HR1268 (Lo-16bits)
1270 | POW1:Exported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1271 |  |  |  | HR1270 (Lo-16bits)
1272 | POW1:Exported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1273 |  |  |  | HR1272 (Lo-16bits)
1274 | POW1:Imported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1275 |  |  |  | HR1274 (Lo-16bits)
1276 | POW1:Imported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1277 |  |  |  | HR1276 (Lo-16bits)
1278 | POW1:Reactive Energy (Q) balance while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1279 |  |  |  | HR1278 (Lo-16bits)
1280 | POW1:Reactive Energy (Q) balance while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1281 |  |  |  | HR1280 (Lo-16bits)
1282 | POW1:Exported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1283 |  |  |  | HR1282 (Lo-16bits)
1284 | POW1:Exported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1285 |  |  |  | HR1284 (Lo-16bits)
1286 | POW1:Imported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1287 |  |  |  | HR1286 (Lo-16bits)
1288 | POW1:Imported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1289 |  |  |  | HR1288 (Lo-16bits)
1290 | POW1:Reactive Energy (Q) balance while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1291 |  |  |  | HR1290 (Lo-16bits)
1292 | POW1:Reactive Energy (Q) balance while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1293 |  |  |  | HR1292 (Lo-16bits)
1294 | POW1:Apparent Energy (S) while Export (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1295 |  |  |  | HR1294 (Lo-16bits)
1296 | POW1:Apparent Energy (S) while Export (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1297 |  |  |  | HR1296 (Lo-16bits)
1298 | POW1:Apparent Energy (S) while Import (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1299 |  |  |  | HR1298 (Lo-16bits)
1300 | POW1:Apparent Energy (S) while Import (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1301 |  |  |  | HR1300 (Lo-16bits)
1302 | POW1:Apparent Energy (S) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1303 |  |  |  | HR1302 (Lo-16bits)
1304 | POW1:Real Energy (P) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1305 |  |  |  | HR1304 (Lo-16bits)
1306 | POW1:Reactive Energy (Q) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1307 |  |  |  | HR1306 (Lo-16bits)
1308 | POW1:Real Energy (P) Supply (Default supply direction towards busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1309 |  |  |  | HR1308 (Lo-16bits)
1310 | POW1:Reactive Energy (Q) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1311 |  |  |  | HR1310 (Lo-16bits)
1312 | POW1:Real Energy (P) Demand (Default demand direction from busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1313 |  |  |  | HR1312 (Lo-16bits)
1314 | POW1:Reactive Energy (Q) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1315 |  |  |  | HR1314 (Lo-16bits)
1316 | POW1:Reset 3ph Energies | RW | 1 | 0=-;1=Reset
1317 | POW1:POW1 3PH Apparent power (S) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1318 |  |  |  | HR1317 (Lo-16bits)
1319 | POW1:POW1 3PH Apparent power (S MVA) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1320 |  |  |  | HR1319 (Lo-16bits)
1321 | POW1:POW1 3PH Active power (P) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1322 |  |  |  | HR1321 (Lo-16bits)
1323 | POW1:POW1 3PH Active power (P MW) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1324 |  |  |  | HR1323 (Lo-16bits)
1325 | POW1:POW1 3PH Reactive power (Q) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1326 |  |  |  | HR1325 (Lo-16bits)
1327 | POW1:POW1 3PH Reactive power (QMVar) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1328 |  |  |  | HR1327 (Lo-16bits)
1329 | POW1:POW1 3PH Tan(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1330 |  |  |  | HR1329 (Lo-16bits)
1331 | POW1:POW1 3PH Cos(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1332 |  |  |  | HR1331 (Lo-16bits)
1333 | POW1:3PH PF | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1334 |  |  |  | HR1333 (Lo-16bits)
1335 | ASC1:Curve1 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1336 |  |  |  | HR1335 (Lo-16bits)
1337 | ASC1:Curve1 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1338 |  |  |  | HR1337 (Lo-16bits)
1339 | ASC1:Curve2 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1340 |  |  |  | HR1339 (Lo-16bits)
1341 | ASC1:Curve2 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1342 |  |  |  | HR1341 (Lo-16bits)
1343 | ASC1:Curve3 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1344 |  |  |  | HR1343 (Lo-16bits)
1345 | ASC1:Curve3 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1346 |  |  |  | HR1345 (Lo-16bits)
1347 | ASC1:Curve4 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1348 |  |  |  | HR1347 (Lo-16bits)
1349 | ASC1:Curve4 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1350 |  |  |  | HR1349 (Lo-16bits)
1351 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1352 |  |  |  | HR1351 (Lo-16bits)
1353 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1354 |  |  |  | HR1353 (Lo-16bits)
1355 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1356 |  |  |  | HR1355 (Lo-16bits)
1357 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1358 |  |  |  | HR1357 (Lo-16bits)
1359 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1360 |  |  |  | HR1359 (Lo-16bits)
1361 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1362 |  |  |  | HR1361 (Lo-16bits)
1363 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1364 |  |  |  | HR1363 (Lo-16bits)
1365 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1366 |  |  |  | HR1365 (Lo-16bits)
1367 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1368 |  |  |  | HR1367 (Lo-16bits)
1369 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1370 |  |  |  | HR1369 (Lo-16bits)
1371 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1372 |  |  |  | HR1371 (Lo-16bits)
1373 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1374 |  |  |  | HR1373 (Lo-16bits)
1375 | M1CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1376 |  |  |  | HR1375 (Lo-16bits)
1377 | M1CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1378 |  |  |  | HR1377 (Lo-16bits)
1379 | M1CT2:I01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1380 |  |  |  | HR1379 (Lo-16bits)
1381 | M1CT2:I01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1382 |  |  |  | HR1381 (Lo-16bits)
1383 | M1CT3:I02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1384 |  |  |  | HR1383 (Lo-16bits)
1385 | M1CT3:I02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1386 |  |  |  | HR1385 (Lo-16bits)
1387 | M2CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1388 |  |  |  | HR1387 (Lo-16bits)
1389 | M2CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1390 |  |  |  | HR1389 (Lo-16bits)
1391 | M2CT2:I''01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1392 |  |  |  | HR1391 (Lo-16bits)
1393 | M2CT2:I''01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1394 |  |  |  | HR1393 (Lo-16bits)
1395 | M2CT3:I''02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1396 |  |  |  | HR1395 (Lo-16bits)
1397 | M2CT3:I''02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1398 |  |  |  | HR1397 (Lo-16bits)
1399 | M1VT1:VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1400 |  |  |  | HR1399 (Lo-16bits)
1401 | M1VT1:VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1402 |  |  |  | HR1401 (Lo-16bits)
1403 | M1VT1:U3 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1404 |  |  |  | HR1403 (Lo-16bits)
1405 | M1VT1:U3 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1406 |  |  |  | HR1405 (Lo-16bits)
1407 | M1VT1:U4 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1408 |  |  |  | HR1407 (Lo-16bits)
1409 | M1VT1:U4 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1410 |  |  |  | HR1409 (Lo-16bits)
1411 | FREQS:f atm. Protections (when not measurable returns to nominal) | R | 2 | FLOAT [0...75] (Hi-16bits)
1412 |  |  |  | HR1411 (Lo-16bits)
1413 | FREQS:f atm. Display (when not measurable is 0Hz) | R | 2 | FLOAT [0...75] (Hi-16bits)
1414 |  |  |  | HR1413 (Lo-16bits)
1415 | FREQS:SS1.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1416 |  |  |  | HR1415 (Lo-16bits)
1417 | FREQS:SS2.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1418 |  |  |  | HR1417 (Lo-16bits)
1419 | DIGI:DIs (cpu) | R | 2 | 0b=DI1;1b=DI2;2b=DI3; (Hi-16bits)
1420 |  |  |  | HR1419 (Lo-16bits)
1421 | DIGI:DIs (input option 1) | R | 2 | 0b=DI4;1b=DI5;2b=DI6;3b=DI7;4b=DI8;5b=DI9;6b=DI10;7b=DI11 (Hi-16bits)
1422 |  |  |  | HR1421 (Lo-16bits)
1423 | DIGI:DIs (input option 2) | R | 2 | 0b=DI12;1b=DI13;2b=DI14;3b=DI15;4b=DI16;5b=DI17;6b=DI18;7b=DI19 (Hi-16bits)
1424 |  |  |  | HR1423 (Lo-16bits)
1425 | DIGI:DIs (input option 3) | R | 2 | 0b=DI20;1b=DI21;2b=DI22;3b=DI23;4b=DI24;5b=DI25;6b=DI26;7b=DI27 (Hi-16bits)
1426 |  |  |  | HR1425 (Lo-16bits)
1427 | DIGI:DIs (input option 4) | R | 2 | 0b=D28;1b=DI29;2b=DI30;3b=DI31;4b=DI32;5b=DI33;6b=DI34;7b=DI35 (Hi-16bits)
1428 |  |  |  | HR1427 (Lo-16bits)
1429 | DIGI:DIs (input option 5) | R | 2 | 0b=DI36;1b=DI37;2b=DI38;3b=DI39;4b=DI40;5b=DI41;6b=DI42;7b=DI43 (Hi-16bits)
1430 |  |  |  | HR1429 (Lo-16bits)
1431 | DIGI:DIs (input option 6) | R | 2 | 0b=DI44;1b=DI45;2b=DI46;3b=DI47;4b=DI48;5b=DI49;6b=DI50;7b=DI51 (Hi-16bits)
1432 |  |  |  | HR1431 (Lo-16bits)
1433 | DIGI:Dis 1-32 | R | 2 | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32 (Hi-16bits)
1434 |  |  |  | HR1433 (Lo-16bits)
1435 | DIGI:Dis 33-64 | R | 2 | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51 (Hi-16bits)
1436 |  |  |  | HR1435 (Lo-16bits)
1437 | DIGI:DI1 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1438 |  |  |  | HR1437 (Lo-16bits)
1439 | DIGI:DI1 Counter Clear | RW | 1 | 0=-;1=Clear
1440 | DIGI:DI2 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1441 |  |  |  | HR1440 (Lo-16bits)
1442 | DIGI:DI2 Counter Clear | RW | 1 | 0=-;1=Clear
1443 | DIGI:DI3 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1444 |  |  |  | HR1443 (Lo-16bits)
1445 | DIGI:DI3 Counter Clear | RW | 1 | 0=-;1=Clear
1446 | DIGI:DI4 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1447 |  |  |  | HR1446 (Lo-16bits)
1448 | DIGI:DI4 Counter Clear | RW | 1 | 0=-;1=Clear
1449 | DIGI:DI5 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1450 |  |  |  | HR1449 (Lo-16bits)
1451 | DIGI:DI5 Counter Clear | RW | 1 | 0=-;1=Clear
1452 | DIGI:DI6 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1453 |  |  |  | HR1452 (Lo-16bits)
1454 | DIGI:DI6 Counter Clear | RW | 1 | 0=-;1=Clear
1455 | DIGI:DI7 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1456 |  |  |  | HR1455 (Lo-16bits)
1457 | DIGI:DI7 Counter Clear | RW | 1 | 0=-;1=Clear
1458 | DIGI:DI8 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1459 |  |  |  | HR1458 (Lo-16bits)
1460 | DIGI:DI8 Counter Clear | RW | 1 | 0=-;1=Clear
1461 | DIGI:DI9 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1462 |  |  |  | HR1461 (Lo-16bits)
1463 | DIGI:DI9 Counter Clear | RW | 1 | 0=-;1=Clear
1464 | DIGI:DI10 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1465 |  |  |  | HR1464 (Lo-16bits)
1466 | DIGI:DI10 Counter Clear | RW | 1 | 0=-;1=Clear
1467 | DIGI:DI11 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1468 |  |  |  | HR1467 (Lo-16bits)
1469 | DIGI:DI11 Counter Clear | RW | 1 | 0=-;1=Clear
1470 | DIGI:DI12 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1471 |  |  |  | HR1470 (Lo-16bits)
1472 | DIGI:DI12 Counter Clear | RW | 1 | 0=-;1=Clear
1473 | DIGI:DI13 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1474 |  |  |  | HR1473 (Lo-16bits)
1475 | DIGI:DI13 Counter Clear | RW | 1 | 0=-;1=Clear
1476 | DIGI:DI14 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1477 |  |  |  | HR1476 (Lo-16bits)
1478 | DIGI:DI14 Counter Clear | RW | 1 | 0=-;1=Clear
1479 | DIGI:DI15 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1480 |  |  |  | HR1479 (Lo-16bits)
1481 | DIGI:DI15 Counter Clear | RW | 1 | 0=-;1=Clear
1482 | DIGI:DI16 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1483 |  |  |  | HR1482 (Lo-16bits)
1484 | DIGI:DI16 Counter Clear | RW | 1 | 0=-;1=Clear
1485 | DIGI:DI17 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1486 |  |  |  | HR1485 (Lo-16bits)
1487 | DIGI:DI17 Counter Clear | RW | 1 | 0=-;1=Clear
1488 | DIGI:DI18 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1489 |  |  |  | HR1488 (Lo-16bits)
1490 | DIGI:DI18 Counter Clear | RW | 1 | 0=-;1=Clear
1491 | DIGI:DI19 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1492 |  |  |  | HR1491 (Lo-16bits)
1493 | DIGI:DI19 Counter Clear | RW | 1 | 0=-;1=Clear
1494 | DIGI:DI20 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1495 |  |  |  | HR1494 (Lo-16bits)
1496 | DIGI:DI20 Counter Clear | RW | 1 | 0=-;1=Clear
1497 | DIGI:DI21 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1498 |  |  |  | HR1497 (Lo-16bits)
1499 | DIGI:DI21 Counter Clear | RW | 1 | 0=-;1=Clear
1500 | DIGI:DI22 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1501 |  |  |  | HR1500 (Lo-16bits)
1502 | DIGI:DI22 Counter Clear | RW | 1 | 0=-;1=Clear
1503 | DIGI:DI23 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1504 |  |  |  | HR1503 (Lo-16bits)
1505 | DIGI:DI23 Counter Clear | RW | 1 | 0=-;1=Clear
1506 | DIGI:DI24 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1507 |  |  |  | HR1506 (Lo-16bits)
1508 | DIGI:DI24 Counter Clear | RW | 1 | 0=-;1=Clear
1509 | DIGI:DI25 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1510 |  |  |  | HR1509 (Lo-16bits)
1511 | DIGI:DI25 Counter Clear | RW | 1 | 0=-;1=Clear
1512 | DIGI:DI26 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1513 |  |  |  | HR1512 (Lo-16bits)
1514 | DIGI:DI26 Counter Clear | RW | 1 | 0=-;1=Clear
1515 | DIGI:DI27 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1516 |  |  |  | HR1515 (Lo-16bits)
1517 | DIGI:DI27 Counter Clear | RW | 1 | 0=-;1=Clear
1518 | DIGI:DI28 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1519 |  |  |  | HR1518 (Lo-16bits)
1520 | DIGI:DI28 Counter Clear | RW | 1 | 0=-;1=Clear
1521 | DIGI:DI29 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1522 |  |  |  | HR1521 (Lo-16bits)
1523 | DIGI:DI29 Counter Clear | RW | 1 | 0=-;1=Clear
1524 | DIGI:DI30 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1525 |  |  |  | HR1524 (Lo-16bits)
1526 | DIGI:DI30 Counter Clear | RW | 1 | 0=-;1=Clear
1527 | DIGI:DI31 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1528 |  |  |  | HR1527 (Lo-16bits)
1529 | DIGI:DI31 Counter Clear | RW | 1 | 0=-;1=Clear
1530 | DIGI:DI32 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1531 |  |  |  | HR1530 (Lo-16bits)
1532 | DIGI:DI32 Counter Clear | RW | 1 | 0=-;1=Clear
1533 | DIGI:DI33 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1534 |  |  |  | HR1533 (Lo-16bits)
1535 | DIGI:DI33 Counter Clear | RW | 1 | 0=-;1=Clear
1536 | DIGI:DI34 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1537 |  |  |  | HR1536 (Lo-16bits)
1538 | DIGI:DI34 Counter Clear | RW | 1 | 0=-;1=Clear
1539 | DIGI:DI35 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1540 |  |  |  | HR1539 (Lo-16bits)
1541 | DIGI:DI35 Counter Clear | RW | 1 | 0=-;1=Clear
1542 | DIGI:DI36 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1543 |  |  |  | HR1542 (Lo-16bits)
1544 | DIGI:DI36 Counter Clear | RW | 1 | 0=-;1=Clear
1545 | DIGI:DI37 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1546 |  |  |  | HR1545 (Lo-16bits)
1547 | DIGI:DI37 Counter Clear | RW | 1 | 0=-;1=Clear
1548 | DIGI:DI38 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1549 |  |  |  | HR1548 (Lo-16bits)
1550 | DIGI:DI38 Counter Clear | RW | 1 | 0=-;1=Clear
1551 | DIGI:DI39 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1552 |  |  |  | HR1551 (Lo-16bits)
1553 | DIGI:DI39 Counter Clear | RW | 1 | 0=-;1=Clear
1554 | DIGI:DI40 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1555 |  |  |  | HR1554 (Lo-16bits)
1556 | DIGI:DI40 Counter Clear | RW | 1 | 0=-;1=Clear
1557 | DIGI:DI41 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1558 |  |  |  | HR1557 (Lo-16bits)
1559 | DIGI:DI41 Counter Clear | RW | 1 | 0=-;1=Clear
1560 | DIGI:DI42 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1561 |  |  |  | HR1560 (Lo-16bits)
1562 | DIGI:DI42 Counter Clear | RW | 1 | 0=-;1=Clear
1563 | DIGI:DI43 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1564 |  |  |  | HR1563 (Lo-16bits)
1565 | DIGI:DI43 Counter Clear | RW | 1 | 0=-;1=Clear
1566 | DIGI:DI44 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1567 |  |  |  | HR1566 (Lo-16bits)
1568 | DIGI:DI44 Counter Clear | RW | 1 | 0=-;1=Clear
1569 | DIGI:DI45 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1570 |  |  |  | HR1569 (Lo-16bits)
1571 | DIGI:DI45 Counter Clear | RW | 1 | 0=-;1=Clear
1572 | DIGI:DI46 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1573 |  |  |  | HR1572 (Lo-16bits)
1574 | DIGI:DI46 Counter Clear | RW | 1 | 0=-;1=Clear
1575 | DIGI:DI47 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1576 |  |  |  | HR1575 (Lo-16bits)
1577 | DIGI:DI47 Counter Clear | RW | 1 | 0=-;1=Clear
1578 | DIGI:DI48 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1579 |  |  |  | HR1578 (Lo-16bits)
1580 | DIGI:DI48 Counter Clear | RW | 1 | 0=-;1=Clear
1581 | DIGI:DI49 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1582 |  |  |  | HR1581 (Lo-16bits)
1583 | DIGI:DI49 Counter Clear | RW | 1 | 0=-;1=Clear
1584 | DIGI:DI50 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1585 |  |  |  | HR1584 (Lo-16bits)
1586 | DIGI:DI50 Counter Clear | RW | 1 | 0=-;1=Clear
1587 | DIGI:DI51 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1588 |  |  |  | HR1587 (Lo-16bits)
1589 | DIGI:DI51 Counter Clear | RW | 1 | 0=-;1=Clear
1590 | RELE:Outputs status | R | 2 | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15 (Hi-16bits)
1591 |  |  |  | HR1590 (Lo-16bits)
1592 | SGS:Active setting group | R | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
1593 | SGS:Force SG | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1594 | SGS:Force SG change | RW | 1 | 0=Disabled;1=Enabled
1595 | SGS:Used setting groups | RW | 1 | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
1596 | SGS:Remote SG change | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1597 | CTRL:Local/Remote status | R | 1 | 0=Remote;1=Local
1598 | DEV:Serial number | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1599 |  |  |  | HR1598 (Lo-16bits)
1600 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1601 |  |  |  | HR1600 (Lo-16bits)
1602 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1603 |  |  |  | HR1602 (Lo-16bits)
1604 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1605 |  |  |  | HR1604 (Lo-16bits)
1606 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1607 |  |  |  | HR1606 (Lo-16bits)
1608 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1609 |  |  |  | HR1608 (Lo-16bits)
1610 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1611 |  |  |  | HR1610 (Lo-16bits)
1612 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1613 |  |  |  | HR1612 (Lo-16bits)
1614 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1615 |  |  |  | HR1614 (Lo-16bits)
1616 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1617 |  |  |  | HR1616 (Lo-16bits)
1618 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1619 |  |  |  | HR1618 (Lo-16bits)
1620 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1621 |  |  |  | HR1620 (Lo-16bits)
1622 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1623 |  |  |  | HR1622 (Lo-16bits)
1624 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1625 |  |  |  | HR1624 (Lo-16bits)
1626 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1627 |  |  |  | HR1626 (Lo-16bits)
1628 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1629 |  |  |  | HR1628 (Lo-16bits)
1630 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1631 |  |  |  | HR1630 (Lo-16bits)
1632 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1633 |  |  |  | HR1632 (Lo-16bits)
1634 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1635 |  |  |  | HR1634 (Lo-16bits)
1636 | DIAG:Configuration changed | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1637 |  |  |  | HR1636 (Lo-16bits)
1638 | MBTCP:Enable mapped setting value modification through Modbus | RW | 1 | 0=Disabled;1=Enabled
1639 | MBIO:MBIO ModA Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1640 |  |  |  | HR1639 (Lo-16bits)
1641 | MBIO:MBIO ModA Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1642 |  |  |  | HR1641 (Lo-16bits)
1643 | MBIO:MBIO ModA Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1644 |  |  |  | HR1643 (Lo-16bits)
1645 | MBIO:MBIO ModA Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1646 |  |  |  | HR1645 (Lo-16bits)
1647 | MBIO:MBIO ModA Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1648 |  |  |  | HR1647 (Lo-16bits)
1649 | MBIO:MBIO ModA Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1650 |  |  |  | HR1649 (Lo-16bits)
1651 | MBIO:MBIO ModA Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1652 |  |  |  | HR1651 (Lo-16bits)
1653 | MBIO:MBIO ModA Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1654 |  |  |  | HR1653 (Lo-16bits)
1655 | MBIO:MBIO ModB Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1656 |  |  |  | HR1655 (Lo-16bits)
1657 | MBIO:MBIO ModB Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1658 |  |  |  | HR1657 (Lo-16bits)
1659 | MBIO:MBIO ModB Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1660 |  |  |  | HR1659 (Lo-16bits)
1661 | MBIO:MBIO ModB Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1662 |  |  |  | HR1661 (Lo-16bits)
1663 | MBIO:MBIO ModB Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1664 |  |  |  | HR1663 (Lo-16bits)
1665 | MBIO:MBIO ModB Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1666 |  |  |  | HR1665 (Lo-16bits)
1667 | MBIO:MBIO ModB Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1668 |  |  |  | HR1667 (Lo-16bits)
1669 | MBIO:MBIO ModB Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1670 |  |  |  | HR1669 (Lo-16bits)
1671 | MBIO:MBIO ModC Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1672 |  |  |  | HR1671 (Lo-16bits)
1673 | MBIO:MBIO ModC Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1674 |  |  |  | HR1673 (Lo-16bits)
1675 | MBIO:MBIO ModC Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1676 |  |  |  | HR1675 (Lo-16bits)
1677 | MBIO:MBIO ModC Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1678 |  |  |  | HR1677 (Lo-16bits)
1679 | MBIO:MBIO ModC Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1680 |  |  |  | HR1679 (Lo-16bits)
1681 | MBIO:MBIO ModC Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1682 |  |  |  | HR1681 (Lo-16bits)
1683 | MBIO:MBIO ModC Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1684 |  |  |  | HR1683 (Lo-16bits)
1685 | MBIO:MBIO ModC Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1686 |  |  |  | HR1685 (Lo-16bits)
1687 | LOGIC:Reset Latches | RW | 1 | 0=-;1=Reset
1688 | LOGIC1:Logic out 1-32 | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
1689 |  |  |  | HR1688 (Lo-16bits)
1690 | NOC1:I> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1691 | NOC1:I> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1692 | NOC1:I> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1693 | NOC1:I> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1694 | NOC1:I> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1695 | NOC1:I> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1696 |  |  |  | HR1695 (Lo-16bits)
1697 | NOC1:I> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1698 |  |  |  | HR1697 (Lo-16bits)
1699 | NOC1:I> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1700 |  |  |  | HR1699 (Lo-16bits)
1701 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1702 |  |  |  | HR1701 (Lo-16bits)
1703 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1704 |  |  |  | HR1703 (Lo-16bits)
1705 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1706 |  |  |  | HR1705 (Lo-16bits)
1707 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1708 |  |  |  | HR1707 (Lo-16bits)
1709 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1710 |  |  |  | HR1709 (Lo-16bits)
1711 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1712 |  |  |  | HR1711 (Lo-16bits)
1713 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1714 |  |  |  | HR1713 (Lo-16bits)
1715 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1716 |  |  |  | HR1715 (Lo-16bits)
1717 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1718 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1719 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1720 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1721 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1722 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1723 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1724 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1725 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1726 |  |  |  | HR1725 (Lo-16bits)
1727 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1728 |  |  |  | HR1727 (Lo-16bits)
1729 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1730 |  |  |  | HR1729 (Lo-16bits)
1731 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1732 |  |  |  | HR1731 (Lo-16bits)
1733 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1734 |  |  |  | HR1733 (Lo-16bits)
1735 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1736 |  |  |  | HR1735 (Lo-16bits)
1737 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1738 |  |  |  | HR1737 (Lo-16bits)
1739 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1740 |  |  |  | HR1739 (Lo-16bits)
1741 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1742 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1743 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1744 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1745 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1746 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1747 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1748 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1749 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1750 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1751 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1752 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1753 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1754 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1755 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1756 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1757 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1758 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1759 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1760 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1761 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1762 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1763 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1764 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1765 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1766 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1767 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1768 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1769 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1770 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1771 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1772 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1773 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1774 |  |  |  | HR1773 (Lo-16bits)
1775 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1776 |  |  |  | HR1775 (Lo-16bits)
1777 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1778 |  |  |  | HR1777 (Lo-16bits)
1779 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1780 |  |  |  | HR1779 (Lo-16bits)
1781 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1782 |  |  |  | HR1781 (Lo-16bits)
1783 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1784 |  |  |  | HR1783 (Lo-16bits)
1785 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1786 |  |  |  | HR1785 (Lo-16bits)
1787 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1788 |  |  |  | HR1787 (Lo-16bits)
1789 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1790 |  |  |  | HR1789 (Lo-16bits)
1791 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1792 |  |  |  | HR1791 (Lo-16bits)
1793 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1794 |  |  |  | HR1793 (Lo-16bits)
1795 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1796 |  |  |  | HR1795 (Lo-16bits)
1797 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1798 |  |  |  | HR1797 (Lo-16bits)
1799 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1800 |  |  |  | HR1799 (Lo-16bits)
1801 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1802 |  |  |  | HR1801 (Lo-16bits)
1803 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1804 |  |  |  | HR1803 (Lo-16bits)
1805 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1806 |  |  |  | HR1805 (Lo-16bits)
1807 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1808 |  |  |  | HR1807 (Lo-16bits)
1809 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1810 |  |  |  | HR1809 (Lo-16bits)
1811 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1812 |  |  |  | HR1811 (Lo-16bits)
1813 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1814 |  |  |  | HR1813 (Lo-16bits)
1815 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1816 |  |  |  | HR1815 (Lo-16bits)
1817 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1818 |  |  |  | HR1817 (Lo-16bits)
1819 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1820 |  |  |  | HR1819 (Lo-16bits)
1821 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1822 |  |  |  | HR1821 (Lo-16bits)
1823 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1824 |  |  |  | HR1823 (Lo-16bits)
1825 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1826 |  |  |  | HR1825 (Lo-16bits)
1827 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1828 |  |  |  | HR1827 (Lo-16bits)
1829 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1830 |  |  |  | HR1829 (Lo-16bits)
1831 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1832 |  |  |  | HR1831 (Lo-16bits)
1833 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1834 |  |  |  | HR1833 (Lo-16bits)
1835 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1836 |  |  |  | HR1835 (Lo-16bits)
1837 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1838 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1839 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1840 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1841 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1842 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1843 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1844 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1845 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1846 |  |  |  | HR1845 (Lo-16bits)
1847 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1848 |  |  |  | HR1847 (Lo-16bits)
1849 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1850 |  |  |  | HR1849 (Lo-16bits)
1851 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1852 |  |  |  | HR1851 (Lo-16bits)
1853 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1854 |  |  |  | HR1853 (Lo-16bits)
1855 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1856 |  |  |  | HR1855 (Lo-16bits)
1857 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1858 |  |  |  | HR1857 (Lo-16bits)
1859 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1860 |  |  |  | HR1859 (Lo-16bits)
1861 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1862 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1863 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1864 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1865 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1866 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1867 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1868 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1869 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1870 |  |  |  | HR1869 (Lo-16bits)
1871 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1872 |  |  |  | HR1871 (Lo-16bits)
1873 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1874 |  |  |  | HR1873 (Lo-16bits)
1875 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1876 |  |  |  | HR1875 (Lo-16bits)
1877 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1878 |  |  |  | HR1877 (Lo-16bits)
1879 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1880 |  |  |  | HR1879 (Lo-16bits)
1881 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1882 |  |  |  | HR1881 (Lo-16bits)
1883 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1884 |  |  |  | HR1883 (Lo-16bits)
1885 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1886 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1887 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1888 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1889 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1890 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1891 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1892 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1893 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1894 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1895 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1896 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1897 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1898 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1899 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1900 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1901 | NOC1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
1902 |  |  |  | HR1901 (Lo-16bits)
1903 | NOC1:Delay type | RW | 1 | 0=DT;1=IDMT
1904 | NOC1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
1905 |  |  |  | HR1904 (Lo-16bits)
1906 | NOC1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
1907 | NOC1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1908 | NOC1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1909 | NOC1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
1910 | NOC1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
1911 |  |  |  | HR1910 (Lo-16bits)
1912 | NOC1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
1913 |  |  |  | HR1912 (Lo-16bits)
1914 | NOC1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
1915 |  |  |  | HR1914 (Lo-16bits)
1916 | NOC1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
1917 |  |  |  | HR1916 (Lo-16bits)
1918 | NOC1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
1919 | NOC1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
1920 | NOC2:I>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1921 | NOC2:I>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1922 | NOC2:I>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1923 | NOC2:I>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1924 | NOC2:I>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1925 | NOC2:I>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1926 |  |  |  | HR1925 (Lo-16bits)
1927 | NOC2:I>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1928 |  |  |  | HR1927 (Lo-16bits)
1929 | NOC2:I>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1930 |  |  |  | HR1929 (Lo-16bits)
1931 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1932 |  |  |  | HR1931 (Lo-16bits)
1933 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1934 |  |  |  | HR1933 (Lo-16bits)
1935 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1936 |  |  |  | HR1935 (Lo-16bits)
1937 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1938 |  |  |  | HR1937 (Lo-16bits)
1939 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1940 |  |  |  | HR1939 (Lo-16bits)
1941 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1942 |  |  |  | HR1941 (Lo-16bits)
1943 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1944 |  |  |  | HR1943 (Lo-16bits)
1945 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1946 |  |  |  | HR1945 (Lo-16bits)
1947 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1948 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1949 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1950 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1951 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1952 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1953 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1954 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
1955 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1956 |  |  |  | HR1955 (Lo-16bits)
1957 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1958 |  |  |  | HR1957 (Lo-16bits)
1959 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1960 |  |  |  | HR1959 (Lo-16bits)
1961 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1962 |  |  |  | HR1961 (Lo-16bits)
1963 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1964 |  |  |  | HR1963 (Lo-16bits)
1965 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1966 |  |  |  | HR1965 (Lo-16bits)
1967 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1968 |  |  |  | HR1967 (Lo-16bits)
1969 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1970 |  |  |  | HR1969 (Lo-16bits)
1971 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1972 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1973 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1974 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1975 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1976 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1977 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1978 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1979 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1980 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1981 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1982 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1983 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1984 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1985 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1986 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1987 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1988 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1989 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1990 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1991 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1992 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1993 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1994 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1995 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1996 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1997 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1998 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1999 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2000 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2001 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2002 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2003 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2004 |  |  |  | HR2003 (Lo-16bits)
2005 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2006 |  |  |  | HR2005 (Lo-16bits)
2007 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2008 |  |  |  | HR2007 (Lo-16bits)
2009 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2010 |  |  |  | HR2009 (Lo-16bits)
2011 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2012 |  |  |  | HR2011 (Lo-16bits)
2013 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2014 |  |  |  | HR2013 (Lo-16bits)
2015 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2016 |  |  |  | HR2015 (Lo-16bits)
2017 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2018 |  |  |  | HR2017 (Lo-16bits)
2019 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2020 |  |  |  | HR2019 (Lo-16bits)
2021 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2022 |  |  |  | HR2021 (Lo-16bits)
2023 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2024 |  |  |  | HR2023 (Lo-16bits)
2025 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2026 |  |  |  | HR2025 (Lo-16bits)
2027 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2028 |  |  |  | HR2027 (Lo-16bits)
2029 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2030 |  |  |  | HR2029 (Lo-16bits)
2031 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2032 |  |  |  | HR2031 (Lo-16bits)
2033 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2034 |  |  |  | HR2033 (Lo-16bits)
2035 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2036 |  |  |  | HR2035 (Lo-16bits)
2037 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2038 |  |  |  | HR2037 (Lo-16bits)
2039 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2040 |  |  |  | HR2039 (Lo-16bits)
2041 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2042 |  |  |  | HR2041 (Lo-16bits)
2043 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2044 |  |  |  | HR2043 (Lo-16bits)
2045 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2046 |  |  |  | HR2045 (Lo-16bits)
2047 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2048 |  |  |  | HR2047 (Lo-16bits)
2049 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2050 |  |  |  | HR2049 (Lo-16bits)
2051 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2052 |  |  |  | HR2051 (Lo-16bits)
2053 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2054 |  |  |  | HR2053 (Lo-16bits)
2055 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2056 |  |  |  | HR2055 (Lo-16bits)
2057 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2058 |  |  |  | HR2057 (Lo-16bits)
2059 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2060 |  |  |  | HR2059 (Lo-16bits)
2061 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2062 |  |  |  | HR2061 (Lo-16bits)
2063 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2064 |  |  |  | HR2063 (Lo-16bits)
2065 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2066 |  |  |  | HR2065 (Lo-16bits)
2067 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2068 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2069 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2070 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2071 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2072 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2073 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2074 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2075 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2076 |  |  |  | HR2075 (Lo-16bits)
2077 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2078 |  |  |  | HR2077 (Lo-16bits)
2079 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2080 |  |  |  | HR2079 (Lo-16bits)
2081 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2082 |  |  |  | HR2081 (Lo-16bits)
2083 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2084 |  |  |  | HR2083 (Lo-16bits)
2085 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2086 |  |  |  | HR2085 (Lo-16bits)
2087 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2088 |  |  |  | HR2087 (Lo-16bits)
2089 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2090 |  |  |  | HR2089 (Lo-16bits)
2091 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2092 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2093 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2094 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2095 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2096 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2097 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2098 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2099 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2100 |  |  |  | HR2099 (Lo-16bits)
2101 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2102 |  |  |  | HR2101 (Lo-16bits)
2103 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2104 |  |  |  | HR2103 (Lo-16bits)
2105 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2106 |  |  |  | HR2105 (Lo-16bits)
2107 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2108 |  |  |  | HR2107 (Lo-16bits)
2109 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2110 |  |  |  | HR2109 (Lo-16bits)
2111 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2112 |  |  |  | HR2111 (Lo-16bits)
2113 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2114 |  |  |  | HR2113 (Lo-16bits)
2115 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2116 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2117 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2118 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2119 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2120 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2121 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2122 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2123 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2124 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2125 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2126 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2127 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2128 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2129 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2130 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2131 | NOC2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2132 |  |  |  | HR2131 (Lo-16bits)
2133 | NOC2:Delay type | RW | 1 | 0=DT;1=IDMT
2134 | NOC2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2135 |  |  |  | HR2134 (Lo-16bits)
2136 | NOC2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2137 | NOC2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2138 | NOC2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2139 | NOC2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2140 | NOC2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2141 |  |  |  | HR2140 (Lo-16bits)
2142 | NOC2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2143 |  |  |  | HR2142 (Lo-16bits)
2144 | NOC2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2145 |  |  |  | HR2144 (Lo-16bits)
2146 | NOC2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2147 |  |  |  | HR2146 (Lo-16bits)
2148 | NOC2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2149 | NOC2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2150 | NOC3:I>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2151 | NOC3:I>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2152 | NOC3:I>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2153 | NOC3:I>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2154 | NOC3:I>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2155 | NOC3:I>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2156 |  |  |  | HR2155 (Lo-16bits)
2157 | NOC3:I>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2158 |  |  |  | HR2157 (Lo-16bits)
2159 | NOC3:I>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2160 |  |  |  | HR2159 (Lo-16bits)
2161 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2162 |  |  |  | HR2161 (Lo-16bits)
2163 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2164 |  |  |  | HR2163 (Lo-16bits)
2165 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2166 |  |  |  | HR2165 (Lo-16bits)
2167 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2168 |  |  |  | HR2167 (Lo-16bits)
2169 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2170 |  |  |  | HR2169 (Lo-16bits)
2171 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2172 |  |  |  | HR2171 (Lo-16bits)
2173 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2174 |  |  |  | HR2173 (Lo-16bits)
2175 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2176 |  |  |  | HR2175 (Lo-16bits)
2177 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2178 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2179 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2180 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2181 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2182 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2183 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2184 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2185 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2186 |  |  |  | HR2185 (Lo-16bits)
2187 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2188 |  |  |  | HR2187 (Lo-16bits)
2189 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2190 |  |  |  | HR2189 (Lo-16bits)
2191 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2192 |  |  |  | HR2191 (Lo-16bits)
2193 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2194 |  |  |  | HR2193 (Lo-16bits)
2195 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2196 |  |  |  | HR2195 (Lo-16bits)
2197 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2198 |  |  |  | HR2197 (Lo-16bits)
2199 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2200 |  |  |  | HR2199 (Lo-16bits)
2201 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2202 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2203 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2204 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2205 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2206 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2207 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2208 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2209 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2210 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2211 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2212 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2213 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2214 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2215 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2216 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2217 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2218 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2219 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2220 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2221 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2222 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2223 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2224 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2225 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2226 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2227 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2228 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2229 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2230 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2231 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2232 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2233 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2234 |  |  |  | HR2233 (Lo-16bits)
2235 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2236 |  |  |  | HR2235 (Lo-16bits)
2237 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2238 |  |  |  | HR2237 (Lo-16bits)
2239 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2240 |  |  |  | HR2239 (Lo-16bits)
2241 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2242 |  |  |  | HR2241 (Lo-16bits)
2243 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2244 |  |  |  | HR2243 (Lo-16bits)
2245 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2246 |  |  |  | HR2245 (Lo-16bits)
2247 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2248 |  |  |  | HR2247 (Lo-16bits)
2249 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2250 |  |  |  | HR2249 (Lo-16bits)
2251 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2252 |  |  |  | HR2251 (Lo-16bits)
2253 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2254 |  |  |  | HR2253 (Lo-16bits)
2255 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2256 |  |  |  | HR2255 (Lo-16bits)
2257 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2258 |  |  |  | HR2257 (Lo-16bits)
2259 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2260 |  |  |  | HR2259 (Lo-16bits)
2261 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2262 |  |  |  | HR2261 (Lo-16bits)
2263 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2264 |  |  |  | HR2263 (Lo-16bits)
2265 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2266 |  |  |  | HR2265 (Lo-16bits)
2267 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2268 |  |  |  | HR2267 (Lo-16bits)
2269 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2270 |  |  |  | HR2269 (Lo-16bits)
2271 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2272 |  |  |  | HR2271 (Lo-16bits)
2273 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2274 |  |  |  | HR2273 (Lo-16bits)
2275 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2276 |  |  |  | HR2275 (Lo-16bits)
2277 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2278 |  |  |  | HR2277 (Lo-16bits)
2279 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2280 |  |  |  | HR2279 (Lo-16bits)
2281 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2282 |  |  |  | HR2281 (Lo-16bits)
2283 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2284 |  |  |  | HR2283 (Lo-16bits)
2285 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2286 |  |  |  | HR2285 (Lo-16bits)
2287 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2288 |  |  |  | HR2287 (Lo-16bits)
2289 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2290 |  |  |  | HR2289 (Lo-16bits)
2291 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2292 |  |  |  | HR2291 (Lo-16bits)
2293 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2294 |  |  |  | HR2293 (Lo-16bits)
2295 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2296 |  |  |  | HR2295 (Lo-16bits)
2297 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2298 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2299 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2300 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2301 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2302 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2303 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2304 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2305 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2306 |  |  |  | HR2305 (Lo-16bits)
2307 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2308 |  |  |  | HR2307 (Lo-16bits)
2309 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2310 |  |  |  | HR2309 (Lo-16bits)
2311 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2312 |  |  |  | HR2311 (Lo-16bits)
2313 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2314 |  |  |  | HR2313 (Lo-16bits)
2315 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2316 |  |  |  | HR2315 (Lo-16bits)
2317 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2318 |  |  |  | HR2317 (Lo-16bits)
2319 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2320 |  |  |  | HR2319 (Lo-16bits)
2321 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2322 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2323 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2324 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2325 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2326 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2327 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2328 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2329 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2330 |  |  |  | HR2329 (Lo-16bits)
2331 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2332 |  |  |  | HR2331 (Lo-16bits)
2333 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2334 |  |  |  | HR2333 (Lo-16bits)
2335 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2336 |  |  |  | HR2335 (Lo-16bits)
2337 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2338 |  |  |  | HR2337 (Lo-16bits)
2339 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2340 |  |  |  | HR2339 (Lo-16bits)
2341 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2342 |  |  |  | HR2341 (Lo-16bits)
2343 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2344 |  |  |  | HR2343 (Lo-16bits)
2345 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2346 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2347 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2348 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2349 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2350 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2351 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2352 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2353 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2354 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2355 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2356 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2357 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2358 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2359 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2360 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2361 | NOC3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2362 |  |  |  | HR2361 (Lo-16bits)
2363 | NOC3:Delay type | RW | 1 | 0=DT;1=IDMT
2364 | NOC3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2365 |  |  |  | HR2364 (Lo-16bits)
2366 | NOC3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2367 | NOC3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2368 | NOC3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2369 | NOC3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2370 | NOC3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2371 |  |  |  | HR2370 (Lo-16bits)
2372 | NOC3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2373 |  |  |  | HR2372 (Lo-16bits)
2374 | NOC3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2375 |  |  |  | HR2374 (Lo-16bits)
2376 | NOC3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2377 |  |  |  | HR2376 (Lo-16bits)
2378 | NOC3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2379 | NOC3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2380 | NOC4:I>>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2381 | NOC4:I>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2382 | NOC4:I>>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2383 | NOC4:I>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2384 | NOC4:I>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2385 | NOC4:I>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2386 |  |  |  | HR2385 (Lo-16bits)
2387 | NOC4:I>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2388 |  |  |  | HR2387 (Lo-16bits)
2389 | NOC4:I>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2390 |  |  |  | HR2389 (Lo-16bits)
2391 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2392 |  |  |  | HR2391 (Lo-16bits)
2393 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2394 |  |  |  | HR2393 (Lo-16bits)
2395 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2396 |  |  |  | HR2395 (Lo-16bits)
2397 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2398 |  |  |  | HR2397 (Lo-16bits)
2399 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2400 |  |  |  | HR2399 (Lo-16bits)
2401 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2402 |  |  |  | HR2401 (Lo-16bits)
2403 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2404 |  |  |  | HR2403 (Lo-16bits)
2405 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2406 |  |  |  | HR2405 (Lo-16bits)
2407 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2408 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2409 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2410 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2411 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2412 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2413 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2414 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2415 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2416 |  |  |  | HR2415 (Lo-16bits)
2417 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2418 |  |  |  | HR2417 (Lo-16bits)
2419 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2420 |  |  |  | HR2419 (Lo-16bits)
2421 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2422 |  |  |  | HR2421 (Lo-16bits)
2423 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2424 |  |  |  | HR2423 (Lo-16bits)
2425 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2426 |  |  |  | HR2425 (Lo-16bits)
2427 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2428 |  |  |  | HR2427 (Lo-16bits)
2429 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2430 |  |  |  | HR2429 (Lo-16bits)
2431 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2432 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2433 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2434 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2435 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2436 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2437 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2438 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2439 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2440 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2441 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2442 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2443 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2444 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2445 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2446 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2447 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2448 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2449 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2450 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2451 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2452 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2453 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2454 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2455 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2456 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2457 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2458 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2459 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2460 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2461 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2462 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2463 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2464 |  |  |  | HR2463 (Lo-16bits)
2465 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2466 |  |  |  | HR2465 (Lo-16bits)
2467 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2468 |  |  |  | HR2467 (Lo-16bits)
2469 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2470 |  |  |  | HR2469 (Lo-16bits)
2471 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2472 |  |  |  | HR2471 (Lo-16bits)
2473 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2474 |  |  |  | HR2473 (Lo-16bits)
2475 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2476 |  |  |  | HR2475 (Lo-16bits)
2477 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2478 |  |  |  | HR2477 (Lo-16bits)
2479 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2480 |  |  |  | HR2479 (Lo-16bits)
2481 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2482 |  |  |  | HR2481 (Lo-16bits)
2483 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2484 |  |  |  | HR2483 (Lo-16bits)
2485 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2486 |  |  |  | HR2485 (Lo-16bits)
2487 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2488 |  |  |  | HR2487 (Lo-16bits)
2489 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2490 |  |  |  | HR2489 (Lo-16bits)
2491 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2492 |  |  |  | HR2491 (Lo-16bits)
2493 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2494 |  |  |  | HR2493 (Lo-16bits)
2495 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2496 |  |  |  | HR2495 (Lo-16bits)
2497 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2498 |  |  |  | HR2497 (Lo-16bits)
2499 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2500 |  |  |  | HR2499 (Lo-16bits)
2501 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2502 |  |  |  | HR2501 (Lo-16bits)
2503 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2504 |  |  |  | HR2503 (Lo-16bits)
2505 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2506 |  |  |  | HR2505 (Lo-16bits)
2507 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2508 |  |  |  | HR2507 (Lo-16bits)
2509 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2510 |  |  |  | HR2509 (Lo-16bits)
2511 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2512 |  |  |  | HR2511 (Lo-16bits)
2513 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2514 |  |  |  | HR2513 (Lo-16bits)
2515 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2516 |  |  |  | HR2515 (Lo-16bits)
2517 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2518 |  |  |  | HR2517 (Lo-16bits)
2519 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2520 |  |  |  | HR2519 (Lo-16bits)
2521 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2522 |  |  |  | HR2521 (Lo-16bits)
2523 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2524 |  |  |  | HR2523 (Lo-16bits)
2525 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2526 |  |  |  | HR2525 (Lo-16bits)
2527 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2528 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2529 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2530 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2531 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2532 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2533 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2534 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2535 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2536 |  |  |  | HR2535 (Lo-16bits)
2537 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2538 |  |  |  | HR2537 (Lo-16bits)
2539 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2540 |  |  |  | HR2539 (Lo-16bits)
2541 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2542 |  |  |  | HR2541 (Lo-16bits)
2543 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2544 |  |  |  | HR2543 (Lo-16bits)
2545 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2546 |  |  |  | HR2545 (Lo-16bits)
2547 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2548 |  |  |  | HR2547 (Lo-16bits)
2549 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2550 |  |  |  | HR2549 (Lo-16bits)
2551 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2552 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2553 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2554 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2555 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2556 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2557 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2558 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2559 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2560 |  |  |  | HR2559 (Lo-16bits)
2561 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2562 |  |  |  | HR2561 (Lo-16bits)
2563 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2564 |  |  |  | HR2563 (Lo-16bits)
2565 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2566 |  |  |  | HR2565 (Lo-16bits)
2567 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2568 |  |  |  | HR2567 (Lo-16bits)
2569 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2570 |  |  |  | HR2569 (Lo-16bits)
2571 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2572 |  |  |  | HR2571 (Lo-16bits)
2573 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2574 |  |  |  | HR2573 (Lo-16bits)
2575 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2576 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2577 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2578 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2579 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2580 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2581 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2582 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2583 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2584 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2585 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2586 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2587 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2588 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2589 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2590 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2591 | NOC4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2592 |  |  |  | HR2591 (Lo-16bits)
2593 | NOC4:Delay type | RW | 1 | 0=DT;1=IDMT
2594 | NOC4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2595 |  |  |  | HR2594 (Lo-16bits)
2596 | NOC4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2597 | NOC4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2598 | NOC4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2599 | NOC4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2600 | NOC4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2601 |  |  |  | HR2600 (Lo-16bits)
2602 | NOC4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2603 |  |  |  | HR2602 (Lo-16bits)
2604 | NOC4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2605 |  |  |  | HR2604 (Lo-16bits)
2606 | NOC4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2607 |  |  |  | HR2606 (Lo-16bits)
2608 | NOC4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2609 | NOC4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2610 | ROC1:Idrw> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2611 | ROC1:Idrw> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2612 | ROC2:Idrw>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2613 | ROC2:Idrw>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2614 | ROC3:Idrw>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2615 | ROC3:Idrw>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2616 | ROC4:Idrw>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2617 | ROC4:Idrw>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2618 | ROC5:Idrw>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2619 | ROC5:Idrw>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2620 | ROC6:Idrw>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2621 | ROC6:Idrw>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2622 | ROC7:Idrw>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2623 | ROC7:Idrw>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2624 | ROC8:Idrw>>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2625 | ROC8:Idrw>>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2626 | ROV1:Urw>/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2627 | ROV2:Urw>>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2628 | ROV3:Urw>>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2629 | ROV4:Urw>>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2630 | COL1:ICOL> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2631 | COL2:ICOL>> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2632 | CNU1:CNU> (50UB) mode | R(W) | 1 | 0=Disabled;1=Activated
2633 | UCP1:IUC> condition | R | 1 | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
2634 | DOC1:Idir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2635 | DOC1:Idir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2636 | DOC1:Idir> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2637 | DOC1:Idir> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2638 |  |  |  | HR2637 (Lo-16bits)
2639 | DOC1:Idir> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2640 |  |  |  | HR2639 (Lo-16bits)
2641 | DOC1:Idir> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2642 |  |  |  | HR2641 (Lo-16bits)
2643 | DOC1:Idir> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2644 |  |  |  | HR2643 (Lo-16bits)
2645 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2646 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2647 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2648 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2649 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2650 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2651 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2652 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2653 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2654 |  |  |  | HR2653 (Lo-16bits)
2655 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2656 |  |  |  | HR2655 (Lo-16bits)
2657 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2658 |  |  |  | HR2657 (Lo-16bits)
2659 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2660 |  |  |  | HR2659 (Lo-16bits)
2661 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2662 |  |  |  | HR2661 (Lo-16bits)
2663 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2664 |  |  |  | HR2663 (Lo-16bits)
2665 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2666 |  |  |  | HR2665 (Lo-16bits)
2667 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2668 |  |  |  | HR2667 (Lo-16bits)
2669 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2670 |  |  |  | HR2669 (Lo-16bits)
2671 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2672 |  |  |  | HR2671 (Lo-16bits)
2673 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2674 |  |  |  | HR2673 (Lo-16bits)
2675 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2676 |  |  |  | HR2675 (Lo-16bits)
2677 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2678 |  |  |  | HR2677 (Lo-16bits)
2679 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2680 |  |  |  | HR2679 (Lo-16bits)
2681 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2682 |  |  |  | HR2681 (Lo-16bits)
2683 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2684 |  |  |  | HR2683 (Lo-16bits)
2685 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2686 |  |  |  | HR2685 (Lo-16bits)
2687 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2688 |  |  |  | HR2687 (Lo-16bits)
2689 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2690 |  |  |  | HR2689 (Lo-16bits)
2691 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2692 |  |  |  | HR2691 (Lo-16bits)
2693 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2694 |  |  |  | HR2693 (Lo-16bits)
2695 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2696 |  |  |  | HR2695 (Lo-16bits)
2697 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2698 |  |  |  | HR2697 (Lo-16bits)
2699 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2700 |  |  |  | HR2699 (Lo-16bits)
2701 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2702 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2703 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2704 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2705 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2706 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2707 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2708 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2709 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2710 |  |  |  | HR2709 (Lo-16bits)
2711 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2712 |  |  |  | HR2711 (Lo-16bits)
2713 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2714 |  |  |  | HR2713 (Lo-16bits)
2715 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2716 |  |  |  | HR2715 (Lo-16bits)
2717 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2718 |  |  |  | HR2717 (Lo-16bits)
2719 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2720 |  |  |  | HR2719 (Lo-16bits)
2721 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2722 |  |  |  | HR2721 (Lo-16bits)
2723 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2724 |  |  |  | HR2723 (Lo-16bits)
2725 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2726 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2727 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2728 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2729 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2730 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2731 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2732 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2733 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2734 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2735 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2736 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2737 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2738 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2739 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2740 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2741 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2742 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2743 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2744 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2745 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2746 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2747 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2748 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2749 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2750 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2751 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2752 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2753 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2754 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2755 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2756 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2757 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2758 |  |  |  | HR2757 (Lo-16bits)
2759 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2760 |  |  |  | HR2759 (Lo-16bits)
2761 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2762 |  |  |  | HR2761 (Lo-16bits)
2763 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2764 |  |  |  | HR2763 (Lo-16bits)
2765 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2766 |  |  |  | HR2765 (Lo-16bits)
2767 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2768 |  |  |  | HR2767 (Lo-16bits)
2769 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2770 |  |  |  | HR2769 (Lo-16bits)
2771 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2772 |  |  |  | HR2771 (Lo-16bits)
2773 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2774 |  |  |  | HR2773 (Lo-16bits)
2775 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2776 |  |  |  | HR2775 (Lo-16bits)
2777 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2778 |  |  |  | HR2777 (Lo-16bits)
2779 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2780 |  |  |  | HR2779 (Lo-16bits)
2781 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2782 |  |  |  | HR2781 (Lo-16bits)
2783 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2784 |  |  |  | HR2783 (Lo-16bits)
2785 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2786 |  |  |  | HR2785 (Lo-16bits)
2787 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2788 |  |  |  | HR2787 (Lo-16bits)
2789 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2790 |  |  |  | HR2789 (Lo-16bits)
2791 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2792 |  |  |  | HR2791 (Lo-16bits)
2793 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2794 |  |  |  | HR2793 (Lo-16bits)
2795 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2796 |  |  |  | HR2795 (Lo-16bits)
2797 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2798 |  |  |  | HR2797 (Lo-16bits)
2799 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2800 |  |  |  | HR2799 (Lo-16bits)
2801 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2802 |  |  |  | HR2801 (Lo-16bits)
2803 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2804 |  |  |  | HR2803 (Lo-16bits)
2805 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2806 |  |  |  | HR2805 (Lo-16bits)
2807 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2808 |  |  |  | HR2807 (Lo-16bits)
2809 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2810 |  |  |  | HR2809 (Lo-16bits)
2811 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2812 |  |  |  | HR2811 (Lo-16bits)
2813 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2814 |  |  |  | HR2813 (Lo-16bits)
2815 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2816 |  |  |  | HR2815 (Lo-16bits)
2817 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2818 |  |  |  | HR2817 (Lo-16bits)
2819 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2820 |  |  |  | HR2819 (Lo-16bits)
2821 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2822 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2823 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2824 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2825 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2826 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2827 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2828 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2829 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2830 |  |  |  | HR2829 (Lo-16bits)
2831 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2832 |  |  |  | HR2831 (Lo-16bits)
2833 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2834 |  |  |  | HR2833 (Lo-16bits)
2835 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2836 |  |  |  | HR2835 (Lo-16bits)
2837 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2838 |  |  |  | HR2837 (Lo-16bits)
2839 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2840 |  |  |  | HR2839 (Lo-16bits)
2841 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2842 |  |  |  | HR2841 (Lo-16bits)
2843 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2844 |  |  |  | HR2843 (Lo-16bits)
2845 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2846 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2847 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2848 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2849 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2850 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2851 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2852 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2853 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2854 |  |  |  | HR2853 (Lo-16bits)
2855 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2856 |  |  |  | HR2855 (Lo-16bits)
2857 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2858 |  |  |  | HR2857 (Lo-16bits)
2859 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2860 |  |  |  | HR2859 (Lo-16bits)
2861 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2862 |  |  |  | HR2861 (Lo-16bits)
2863 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2864 |  |  |  | HR2863 (Lo-16bits)
2865 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2866 |  |  |  | HR2865 (Lo-16bits)
2867 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2868 |  |  |  | HR2867 (Lo-16bits)
2869 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2870 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2871 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2872 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2873 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2874 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2875 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2876 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2877 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2878 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2879 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2880 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2881 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2882 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2883 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2884 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2885 | DOC2:Idir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2886 | DOC2:Idir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2887 | DOC2:Idir>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2888 | DOC2:Idir>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2889 |  |  |  | HR2888 (Lo-16bits)
2890 | DOC2:Idir>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2891 |  |  |  | HR2890 (Lo-16bits)
2892 | DOC2:Idir>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2893 |  |  |  | HR2892 (Lo-16bits)
2894 | DOC2:Idir>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2895 |  |  |  | HR2894 (Lo-16bits)
2896 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2897 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2898 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2899 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2900 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2901 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2902 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2903 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2904 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2905 |  |  |  | HR2904 (Lo-16bits)
2906 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2907 |  |  |  | HR2906 (Lo-16bits)
2908 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2909 |  |  |  | HR2908 (Lo-16bits)
2910 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2911 |  |  |  | HR2910 (Lo-16bits)
2912 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2913 |  |  |  | HR2912 (Lo-16bits)
2914 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2915 |  |  |  | HR2914 (Lo-16bits)
2916 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2917 |  |  |  | HR2916 (Lo-16bits)
2918 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2919 |  |  |  | HR2918 (Lo-16bits)
2920 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2921 |  |  |  | HR2920 (Lo-16bits)
2922 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2923 |  |  |  | HR2922 (Lo-16bits)
2924 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2925 |  |  |  | HR2924 (Lo-16bits)
2926 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2927 |  |  |  | HR2926 (Lo-16bits)
2928 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2929 |  |  |  | HR2928 (Lo-16bits)
2930 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2931 |  |  |  | HR2930 (Lo-16bits)
2932 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2933 |  |  |  | HR2932 (Lo-16bits)
2934 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2935 |  |  |  | HR2934 (Lo-16bits)
2936 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2937 |  |  |  | HR2936 (Lo-16bits)
2938 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2939 |  |  |  | HR2938 (Lo-16bits)
2940 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2941 |  |  |  | HR2940 (Lo-16bits)
2942 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2943 |  |  |  | HR2942 (Lo-16bits)
2944 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2945 |  |  |  | HR2944 (Lo-16bits)
2946 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2947 |  |  |  | HR2946 (Lo-16bits)
2948 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2949 |  |  |  | HR2948 (Lo-16bits)
2950 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2951 |  |  |  | HR2950 (Lo-16bits)
2952 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2953 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2954 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2955 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2956 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2957 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2958 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2959 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2960 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2961 |  |  |  | HR2960 (Lo-16bits)
2962 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2963 |  |  |  | HR2962 (Lo-16bits)
2964 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2965 |  |  |  | HR2964 (Lo-16bits)
2966 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2967 |  |  |  | HR2966 (Lo-16bits)
2968 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2969 |  |  |  | HR2968 (Lo-16bits)
2970 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2971 |  |  |  | HR2970 (Lo-16bits)
2972 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2973 |  |  |  | HR2972 (Lo-16bits)
2974 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2975 |  |  |  | HR2974 (Lo-16bits)
2976 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2977 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2978 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2979 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2980 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2981 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2982 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2983 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2984 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2985 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2986 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2987 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2988 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2989 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2990 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2991 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2992 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2993 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2994 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2995 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2996 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2997 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2998 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2999 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3000 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3001 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3002 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3003 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3004 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3005 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3006 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3007 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3008 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3009 |  |  |  | HR3008 (Lo-16bits)
3010 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3011 |  |  |  | HR3010 (Lo-16bits)
3012 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3013 |  |  |  | HR3012 (Lo-16bits)
3014 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3015 |  |  |  | HR3014 (Lo-16bits)
3016 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3017 |  |  |  | HR3016 (Lo-16bits)
3018 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3019 |  |  |  | HR3018 (Lo-16bits)
3020 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3021 |  |  |  | HR3020 (Lo-16bits)
3022 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3023 |  |  |  | HR3022 (Lo-16bits)
3024 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3025 |  |  |  | HR3024 (Lo-16bits)
3026 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3027 |  |  |  | HR3026 (Lo-16bits)
3028 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3029 |  |  |  | HR3028 (Lo-16bits)
3030 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3031 |  |  |  | HR3030 (Lo-16bits)
3032 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3033 |  |  |  | HR3032 (Lo-16bits)
3034 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3035 |  |  |  | HR3034 (Lo-16bits)
3036 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3037 |  |  |  | HR3036 (Lo-16bits)
3038 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3039 |  |  |  | HR3038 (Lo-16bits)
3040 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3041 |  |  |  | HR3040 (Lo-16bits)
3042 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3043 |  |  |  | HR3042 (Lo-16bits)
3044 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3045 |  |  |  | HR3044 (Lo-16bits)
3046 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3047 |  |  |  | HR3046 (Lo-16bits)
3048 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3049 |  |  |  | HR3048 (Lo-16bits)
3050 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3051 |  |  |  | HR3050 (Lo-16bits)
3052 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3053 |  |  |  | HR3052 (Lo-16bits)
3054 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3055 |  |  |  | HR3054 (Lo-16bits)
3056 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3057 |  |  |  | HR3056 (Lo-16bits)
3058 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3059 |  |  |  | HR3058 (Lo-16bits)
3060 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3061 |  |  |  | HR3060 (Lo-16bits)
3062 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3063 |  |  |  | HR3062 (Lo-16bits)
3064 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3065 |  |  |  | HR3064 (Lo-16bits)
3066 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3067 |  |  |  | HR3066 (Lo-16bits)
3068 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3069 |  |  |  | HR3068 (Lo-16bits)
3070 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3071 |  |  |  | HR3070 (Lo-16bits)
3072 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3073 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3074 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3075 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3076 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3077 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3078 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3079 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3080 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3081 |  |  |  | HR3080 (Lo-16bits)
3082 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3083 |  |  |  | HR3082 (Lo-16bits)
3084 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3085 |  |  |  | HR3084 (Lo-16bits)
3086 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3087 |  |  |  | HR3086 (Lo-16bits)
3088 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3089 |  |  |  | HR3088 (Lo-16bits)
3090 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3091 |  |  |  | HR3090 (Lo-16bits)
3092 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3093 |  |  |  | HR3092 (Lo-16bits)
3094 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3095 |  |  |  | HR3094 (Lo-16bits)
3096 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3097 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3098 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3099 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3100 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3101 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3102 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3103 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3104 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3105 |  |  |  | HR3104 (Lo-16bits)
3106 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3107 |  |  |  | HR3106 (Lo-16bits)
3108 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3109 |  |  |  | HR3108 (Lo-16bits)
3110 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3111 |  |  |  | HR3110 (Lo-16bits)
3112 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3113 |  |  |  | HR3112 (Lo-16bits)
3114 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3115 |  |  |  | HR3114 (Lo-16bits)
3116 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3117 |  |  |  | HR3116 (Lo-16bits)
3118 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3119 |  |  |  | HR3118 (Lo-16bits)
3120 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3121 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3122 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3123 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3124 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3125 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3126 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3127 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3128 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3129 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3130 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3131 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3132 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3133 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3134 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3135 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3136 | DOC3:Idir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3137 | DOC3:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3138 | DOC3:Idir>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3139 | DOC3:Idir>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3140 |  |  |  | HR3139 (Lo-16bits)
3141 | DOC3:Idir>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3142 |  |  |  | HR3141 (Lo-16bits)
3143 | DOC3:Idir>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3144 |  |  |  | HR3143 (Lo-16bits)
3145 | DOC3:Idir>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3146 |  |  |  | HR3145 (Lo-16bits)
3147 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3148 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3149 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3150 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3151 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3152 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3153 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3154 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3155 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3156 |  |  |  | HR3155 (Lo-16bits)
3157 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3158 |  |  |  | HR3157 (Lo-16bits)
3159 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3160 |  |  |  | HR3159 (Lo-16bits)
3161 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3162 |  |  |  | HR3161 (Lo-16bits)
3163 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3164 |  |  |  | HR3163 (Lo-16bits)
3165 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3166 |  |  |  | HR3165 (Lo-16bits)
3167 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3168 |  |  |  | HR3167 (Lo-16bits)
3169 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3170 |  |  |  | HR3169 (Lo-16bits)
3171 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3172 |  |  |  | HR3171 (Lo-16bits)
3173 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3174 |  |  |  | HR3173 (Lo-16bits)
3175 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3176 |  |  |  | HR3175 (Lo-16bits)
3177 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3178 |  |  |  | HR3177 (Lo-16bits)
3179 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3180 |  |  |  | HR3179 (Lo-16bits)
3181 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3182 |  |  |  | HR3181 (Lo-16bits)
3183 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3184 |  |  |  | HR3183 (Lo-16bits)
3185 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3186 |  |  |  | HR3185 (Lo-16bits)
3187 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3188 |  |  |  | HR3187 (Lo-16bits)
3189 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3190 |  |  |  | HR3189 (Lo-16bits)
3191 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3192 |  |  |  | HR3191 (Lo-16bits)
3193 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3194 |  |  |  | HR3193 (Lo-16bits)
3195 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3196 |  |  |  | HR3195 (Lo-16bits)
3197 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3198 |  |  |  | HR3197 (Lo-16bits)
3199 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3200 |  |  |  | HR3199 (Lo-16bits)
3201 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3202 |  |  |  | HR3201 (Lo-16bits)
3203 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3204 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3205 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3206 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3207 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3208 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3209 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3210 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3211 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3212 |  |  |  | HR3211 (Lo-16bits)
3213 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3214 |  |  |  | HR3213 (Lo-16bits)
3215 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3216 |  |  |  | HR3215 (Lo-16bits)
3217 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3218 |  |  |  | HR3217 (Lo-16bits)
3219 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3220 |  |  |  | HR3219 (Lo-16bits)
3221 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3222 |  |  |  | HR3221 (Lo-16bits)
3223 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3224 |  |  |  | HR3223 (Lo-16bits)
3225 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3226 |  |  |  | HR3225 (Lo-16bits)
3227 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3228 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3229 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3230 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3231 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3232 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3233 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3234 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3235 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3236 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3237 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3238 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3239 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3240 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3241 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3242 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3243 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3244 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3245 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3246 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3247 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3248 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3249 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3250 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3251 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3252 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3253 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3254 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3255 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3256 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3257 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3258 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3259 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3260 |  |  |  | HR3259 (Lo-16bits)
3261 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3262 |  |  |  | HR3261 (Lo-16bits)
3263 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3264 |  |  |  | HR3263 (Lo-16bits)
3265 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3266 |  |  |  | HR3265 (Lo-16bits)
3267 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3268 |  |  |  | HR3267 (Lo-16bits)
3269 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3270 |  |  |  | HR3269 (Lo-16bits)
3271 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3272 |  |  |  | HR3271 (Lo-16bits)
3273 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3274 |  |  |  | HR3273 (Lo-16bits)
3275 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3276 |  |  |  | HR3275 (Lo-16bits)
3277 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3278 |  |  |  | HR3277 (Lo-16bits)
3279 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3280 |  |  |  | HR3279 (Lo-16bits)
3281 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3282 |  |  |  | HR3281 (Lo-16bits)
3283 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3284 |  |  |  | HR3283 (Lo-16bits)
3285 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3286 |  |  |  | HR3285 (Lo-16bits)
3287 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3288 |  |  |  | HR3287 (Lo-16bits)
3289 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3290 |  |  |  | HR3289 (Lo-16bits)
3291 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3292 |  |  |  | HR3291 (Lo-16bits)
3293 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3294 |  |  |  | HR3293 (Lo-16bits)
3295 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3296 |  |  |  | HR3295 (Lo-16bits)
3297 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3298 |  |  |  | HR3297 (Lo-16bits)
3299 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3300 |  |  |  | HR3299 (Lo-16bits)
3301 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3302 |  |  |  | HR3301 (Lo-16bits)
3303 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3304 |  |  |  | HR3303 (Lo-16bits)
3305 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3306 |  |  |  | HR3305 (Lo-16bits)
3307 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3308 |  |  |  | HR3307 (Lo-16bits)
3309 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3310 |  |  |  | HR3309 (Lo-16bits)
3311 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3312 |  |  |  | HR3311 (Lo-16bits)
3313 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3314 |  |  |  | HR3313 (Lo-16bits)
3315 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3316 |  |  |  | HR3315 (Lo-16bits)
3317 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3318 |  |  |  | HR3317 (Lo-16bits)
3319 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3320 |  |  |  | HR3319 (Lo-16bits)
3321 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3322 |  |  |  | HR3321 (Lo-16bits)
3323 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3324 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3325 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3326 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3327 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3328 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3329 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3330 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3331 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3332 |  |  |  | HR3331 (Lo-16bits)
3333 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3334 |  |  |  | HR3333 (Lo-16bits)
3335 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3336 |  |  |  | HR3335 (Lo-16bits)
3337 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3338 |  |  |  | HR3337 (Lo-16bits)
3339 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3340 |  |  |  | HR3339 (Lo-16bits)
3341 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3342 |  |  |  | HR3341 (Lo-16bits)
3343 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3344 |  |  |  | HR3343 (Lo-16bits)
3345 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3346 |  |  |  | HR3345 (Lo-16bits)
3347 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3348 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3349 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3350 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3351 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3352 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3353 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3354 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3355 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3356 |  |  |  | HR3355 (Lo-16bits)
3357 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3358 |  |  |  | HR3357 (Lo-16bits)
3359 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3360 |  |  |  | HR3359 (Lo-16bits)
3361 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3362 |  |  |  | HR3361 (Lo-16bits)
3363 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3364 |  |  |  | HR3363 (Lo-16bits)
3365 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3366 |  |  |  | HR3365 (Lo-16bits)
3367 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3368 |  |  |  | HR3367 (Lo-16bits)
3369 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3370 |  |  |  | HR3369 (Lo-16bits)
3371 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3372 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3373 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3374 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3375 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3376 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3377 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3378 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3379 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3380 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3381 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3382 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3383 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3384 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3385 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3386 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3387 | DOC4:Idir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3388 | DOC4:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3389 | DOC4:Idir>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3390 | DOC4:Idir>>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3391 |  |  |  | HR3390 (Lo-16bits)
3392 | DOC4:Idir>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3393 |  |  |  | HR3392 (Lo-16bits)
3394 | DOC4:Idir>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3395 |  |  |  | HR3394 (Lo-16bits)
3396 | DOC4:Idir>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3397 |  |  |  | HR3396 (Lo-16bits)
3398 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3399 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3400 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3401 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3402 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3403 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3404 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3405 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3406 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3407 |  |  |  | HR3406 (Lo-16bits)
3408 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3409 |  |  |  | HR3408 (Lo-16bits)
3410 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3411 |  |  |  | HR3410 (Lo-16bits)
3412 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3413 |  |  |  | HR3412 (Lo-16bits)
3414 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3415 |  |  |  | HR3414 (Lo-16bits)
3416 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3417 |  |  |  | HR3416 (Lo-16bits)
3418 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3419 |  |  |  | HR3418 (Lo-16bits)
3420 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3421 |  |  |  | HR3420 (Lo-16bits)
3422 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3423 |  |  |  | HR3422 (Lo-16bits)
3424 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3425 |  |  |  | HR3424 (Lo-16bits)
3426 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3427 |  |  |  | HR3426 (Lo-16bits)
3428 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3429 |  |  |  | HR3428 (Lo-16bits)
3430 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3431 |  |  |  | HR3430 (Lo-16bits)
3432 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3433 |  |  |  | HR3432 (Lo-16bits)
3434 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3435 |  |  |  | HR3434 (Lo-16bits)
3436 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3437 |  |  |  | HR3436 (Lo-16bits)
3438 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3439 |  |  |  | HR3438 (Lo-16bits)
3440 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3441 |  |  |  | HR3440 (Lo-16bits)
3442 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3443 |  |  |  | HR3442 (Lo-16bits)
3444 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3445 |  |  |  | HR3444 (Lo-16bits)
3446 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3447 |  |  |  | HR3446 (Lo-16bits)
3448 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3449 |  |  |  | HR3448 (Lo-16bits)
3450 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3451 |  |  |  | HR3450 (Lo-16bits)
3452 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3453 |  |  |  | HR3452 (Lo-16bits)
3454 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3455 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3456 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3457 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3458 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3459 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3460 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3461 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3462 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3463 |  |  |  | HR3462 (Lo-16bits)
3464 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3465 |  |  |  | HR3464 (Lo-16bits)
3466 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3467 |  |  |  | HR3466 (Lo-16bits)
3468 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3469 |  |  |  | HR3468 (Lo-16bits)
3470 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3471 |  |  |  | HR3470 (Lo-16bits)
3472 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3473 |  |  |  | HR3472 (Lo-16bits)
3474 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3475 |  |  |  | HR3474 (Lo-16bits)
3476 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3477 |  |  |  | HR3476 (Lo-16bits)
3478 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3479 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3480 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3481 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3482 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3483 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3484 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3485 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3486 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3487 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3488 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3489 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3490 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3491 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3492 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3493 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3494 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3495 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3496 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3497 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3498 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3499 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3500 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3501 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3502 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3503 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3504 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3505 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3506 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3507 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3508 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3509 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3510 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3511 |  |  |  | HR3510 (Lo-16bits)
3512 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3513 |  |  |  | HR3512 (Lo-16bits)
3514 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3515 |  |  |  | HR3514 (Lo-16bits)
3516 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3517 |  |  |  | HR3516 (Lo-16bits)
3518 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3519 |  |  |  | HR3518 (Lo-16bits)
3520 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3521 |  |  |  | HR3520 (Lo-16bits)
3522 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3523 |  |  |  | HR3522 (Lo-16bits)
3524 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3525 |  |  |  | HR3524 (Lo-16bits)
3526 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3527 |  |  |  | HR3526 (Lo-16bits)
3528 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3529 |  |  |  | HR3528 (Lo-16bits)
3530 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3531 |  |  |  | HR3530 (Lo-16bits)
3532 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3533 |  |  |  | HR3532 (Lo-16bits)
3534 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3535 |  |  |  | HR3534 (Lo-16bits)
3536 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3537 |  |  |  | HR3536 (Lo-16bits)
3538 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3539 |  |  |  | HR3538 (Lo-16bits)
3540 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3541 |  |  |  | HR3540 (Lo-16bits)
3542 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3543 |  |  |  | HR3542 (Lo-16bits)
3544 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3545 |  |  |  | HR3544 (Lo-16bits)
3546 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3547 |  |  |  | HR3546 (Lo-16bits)
3548 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3549 |  |  |  | HR3548 (Lo-16bits)
3550 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3551 |  |  |  | HR3550 (Lo-16bits)
3552 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3553 |  |  |  | HR3552 (Lo-16bits)
3554 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3555 |  |  |  | HR3554 (Lo-16bits)
3556 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3557 |  |  |  | HR3556 (Lo-16bits)
3558 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3559 |  |  |  | HR3558 (Lo-16bits)
3560 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3561 |  |  |  | HR3560 (Lo-16bits)
3562 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3563 |  |  |  | HR3562 (Lo-16bits)
3564 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3565 |  |  |  | HR3564 (Lo-16bits)
3566 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3567 |  |  |  | HR3566 (Lo-16bits)
3568 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3569 |  |  |  | HR3568 (Lo-16bits)
3570 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3571 |  |  |  | HR3570 (Lo-16bits)
3572 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3573 |  |  |  | HR3572 (Lo-16bits)
3574 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3575 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3576 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3577 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3578 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3579 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3580 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3581 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3582 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3583 |  |  |  | HR3582 (Lo-16bits)
3584 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3585 |  |  |  | HR3584 (Lo-16bits)
3586 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3587 |  |  |  | HR3586 (Lo-16bits)
3588 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3589 |  |  |  | HR3588 (Lo-16bits)
3590 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3591 |  |  |  | HR3590 (Lo-16bits)
3592 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3593 |  |  |  | HR3592 (Lo-16bits)
3594 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3595 |  |  |  | HR3594 (Lo-16bits)
3596 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3597 |  |  |  | HR3596 (Lo-16bits)
3598 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3599 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3600 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3601 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3602 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3603 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3604 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3605 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3606 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3607 |  |  |  | HR3606 (Lo-16bits)
3608 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3609 |  |  |  | HR3608 (Lo-16bits)
3610 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3611 |  |  |  | HR3610 (Lo-16bits)
3612 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3613 |  |  |  | HR3612 (Lo-16bits)
3614 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3615 |  |  |  | HR3614 (Lo-16bits)
3616 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3617 |  |  |  | HR3616 (Lo-16bits)
3618 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3619 |  |  |  | HR3618 (Lo-16bits)
3620 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3621 |  |  |  | HR3620 (Lo-16bits)
3622 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3623 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3624 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3625 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3626 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3627 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3628 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3629 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3630 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3631 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3632 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3633 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3634 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3635 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3636 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3637 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3638 | NEF1:I0> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3639 | NEF1:I0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3640 | NEF1:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3641 | NEF1:I0> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3642 | NEF1:I0> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3643 |  |  |  | HR3642 (Lo-16bits)
3644 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3645 |  |  |  | HR3644 (Lo-16bits)
3646 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3647 |  |  |  | HR3646 (Lo-16bits)
3648 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3649 |  |  |  | HR3648 (Lo-16bits)
3650 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3651 |  |  |  | HR3650 (Lo-16bits)
3652 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3653 |  |  |  | HR3652 (Lo-16bits)
3654 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3655 |  |  |  | HR3654 (Lo-16bits)
3656 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3657 |  |  |  | HR3656 (Lo-16bits)
3658 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3659 |  |  |  | HR3658 (Lo-16bits)
3660 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3661 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3662 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3663 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3664 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3665 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3666 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3667 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3668 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3669 |  |  |  | HR3668 (Lo-16bits)
3670 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3671 |  |  |  | HR3670 (Lo-16bits)
3672 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3673 |  |  |  | HR3672 (Lo-16bits)
3674 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3675 |  |  |  | HR3674 (Lo-16bits)
3676 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3677 |  |  |  | HR3676 (Lo-16bits)
3678 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3679 |  |  |  | HR3678 (Lo-16bits)
3680 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3681 |  |  |  | HR3680 (Lo-16bits)
3682 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3683 |  |  |  | HR3682 (Lo-16bits)
3684 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3685 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3686 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3687 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3688 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3689 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3690 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3691 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3692 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3693 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3694 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3695 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3696 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3697 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3698 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3699 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3700 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3701 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3702 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3703 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3704 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3705 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3706 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3707 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3708 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3709 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3710 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3711 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3712 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3713 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3714 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3715 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3716 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3717 |  |  |  | HR3716 (Lo-16bits)
3718 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3719 |  |  |  | HR3718 (Lo-16bits)
3720 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3721 |  |  |  | HR3720 (Lo-16bits)
3722 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3723 |  |  |  | HR3722 (Lo-16bits)
3724 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3725 |  |  |  | HR3724 (Lo-16bits)
3726 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3727 |  |  |  | HR3726 (Lo-16bits)
3728 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3729 |  |  |  | HR3728 (Lo-16bits)
3730 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3731 |  |  |  | HR3730 (Lo-16bits)
3732 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3733 |  |  |  | HR3732 (Lo-16bits)
3734 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3735 |  |  |  | HR3734 (Lo-16bits)
3736 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3737 |  |  |  | HR3736 (Lo-16bits)
3738 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3739 |  |  |  | HR3738 (Lo-16bits)
3740 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3741 |  |  |  | HR3740 (Lo-16bits)
3742 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3743 |  |  |  | HR3742 (Lo-16bits)
3744 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3745 |  |  |  | HR3744 (Lo-16bits)
3746 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3747 |  |  |  | HR3746 (Lo-16bits)
3748 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3749 |  |  |  | HR3748 (Lo-16bits)
3750 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3751 |  |  |  | HR3750 (Lo-16bits)
3752 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3753 |  |  |  | HR3752 (Lo-16bits)
3754 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3755 |  |  |  | HR3754 (Lo-16bits)
3756 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3757 |  |  |  | HR3756 (Lo-16bits)
3758 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3759 |  |  |  | HR3758 (Lo-16bits)
3760 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3761 |  |  |  | HR3760 (Lo-16bits)
3762 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3763 |  |  |  | HR3762 (Lo-16bits)
3764 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3765 |  |  |  | HR3764 (Lo-16bits)
3766 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3767 |  |  |  | HR3766 (Lo-16bits)
3768 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3769 |  |  |  | HR3768 (Lo-16bits)
3770 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3771 |  |  |  | HR3770 (Lo-16bits)
3772 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3773 |  |  |  | HR3772 (Lo-16bits)
3774 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3775 |  |  |  | HR3774 (Lo-16bits)
3776 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3777 |  |  |  | HR3776 (Lo-16bits)
3778 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3779 |  |  |  | HR3778 (Lo-16bits)
3780 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3781 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3782 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3783 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3784 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3785 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3786 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3787 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3788 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3789 |  |  |  | HR3788 (Lo-16bits)
3790 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3791 |  |  |  | HR3790 (Lo-16bits)
3792 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3793 |  |  |  | HR3792 (Lo-16bits)
3794 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3795 |  |  |  | HR3794 (Lo-16bits)
3796 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3797 |  |  |  | HR3796 (Lo-16bits)
3798 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3799 |  |  |  | HR3798 (Lo-16bits)
3800 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3801 |  |  |  | HR3800 (Lo-16bits)
3802 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3803 |  |  |  | HR3802 (Lo-16bits)
3804 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3805 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3806 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3807 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3808 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3809 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3810 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3811 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3812 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3813 |  |  |  | HR3812 (Lo-16bits)
3814 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3815 |  |  |  | HR3814 (Lo-16bits)
3816 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3817 |  |  |  | HR3816 (Lo-16bits)
3818 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3819 |  |  |  | HR3818 (Lo-16bits)
3820 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3821 |  |  |  | HR3820 (Lo-16bits)
3822 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3823 |  |  |  | HR3822 (Lo-16bits)
3824 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3825 |  |  |  | HR3824 (Lo-16bits)
3826 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3827 |  |  |  | HR3826 (Lo-16bits)
3828 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3829 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3830 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3831 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3832 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3833 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3834 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3835 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3836 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3837 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3838 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3839 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3840 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3841 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3842 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3843 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3844 | NEF1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
3845 |  |  |  | HR3844 (Lo-16bits)
3846 | NEF1:Delay type | RW | 1 | 0=DT;1=IDMT
3847 | NEF1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
3848 |  |  |  | HR3847 (Lo-16bits)
3849 | NEF1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
3850 | NEF1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3851 | NEF1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3852 | NEF1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
3853 | NEF1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
3854 |  |  |  | HR3853 (Lo-16bits)
3855 | NEF1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
3856 |  |  |  | HR3855 (Lo-16bits)
3857 | NEF1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
3858 |  |  |  | HR3857 (Lo-16bits)
3859 | NEF1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
3860 |  |  |  | HR3859 (Lo-16bits)
3861 | NEF1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
3862 | NEF1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
3863 | NEF2:I0>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3864 | NEF2:I0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3865 | NEF2:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3866 | NEF2:I0>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3867 | NEF2:I0>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3868 |  |  |  | HR3867 (Lo-16bits)
3869 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3870 |  |  |  | HR3869 (Lo-16bits)
3871 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3872 |  |  |  | HR3871 (Lo-16bits)
3873 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3874 |  |  |  | HR3873 (Lo-16bits)
3875 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3876 |  |  |  | HR3875 (Lo-16bits)
3877 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3878 |  |  |  | HR3877 (Lo-16bits)
3879 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3880 |  |  |  | HR3879 (Lo-16bits)
3881 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3882 |  |  |  | HR3881 (Lo-16bits)
3883 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3884 |  |  |  | HR3883 (Lo-16bits)
3885 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3886 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3887 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3888 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3889 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3890 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3891 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3892 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3893 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3894 |  |  |  | HR3893 (Lo-16bits)
3895 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3896 |  |  |  | HR3895 (Lo-16bits)
3897 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3898 |  |  |  | HR3897 (Lo-16bits)
3899 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3900 |  |  |  | HR3899 (Lo-16bits)
3901 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3902 |  |  |  | HR3901 (Lo-16bits)
3903 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3904 |  |  |  | HR3903 (Lo-16bits)
3905 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3906 |  |  |  | HR3905 (Lo-16bits)
3907 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3908 |  |  |  | HR3907 (Lo-16bits)
3909 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3910 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3911 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3912 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3913 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3914 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3915 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3916 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3917 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3918 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3919 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3920 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3921 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3922 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3923 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3924 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3925 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3926 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3927 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3928 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3929 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3930 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3931 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3932 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3933 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3934 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3935 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3936 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3937 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3938 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3939 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3940 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3941 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3942 |  |  |  | HR3941 (Lo-16bits)
3943 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3944 |  |  |  | HR3943 (Lo-16bits)
3945 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3946 |  |  |  | HR3945 (Lo-16bits)
3947 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3948 |  |  |  | HR3947 (Lo-16bits)
3949 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3950 |  |  |  | HR3949 (Lo-16bits)
3951 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3952 |  |  |  | HR3951 (Lo-16bits)
3953 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3954 |  |  |  | HR3953 (Lo-16bits)
3955 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3956 |  |  |  | HR3955 (Lo-16bits)
3957 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3958 |  |  |  | HR3957 (Lo-16bits)
3959 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3960 |  |  |  | HR3959 (Lo-16bits)
3961 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3962 |  |  |  | HR3961 (Lo-16bits)
3963 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3964 |  |  |  | HR3963 (Lo-16bits)
3965 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3966 |  |  |  | HR3965 (Lo-16bits)
3967 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3968 |  |  |  | HR3967 (Lo-16bits)
3969 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3970 |  |  |  | HR3969 (Lo-16bits)
3971 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3972 |  |  |  | HR3971 (Lo-16bits)
3973 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3974 |  |  |  | HR3973 (Lo-16bits)
3975 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3976 |  |  |  | HR3975 (Lo-16bits)
3977 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3978 |  |  |  | HR3977 (Lo-16bits)
3979 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3980 |  |  |  | HR3979 (Lo-16bits)
3981 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3982 |  |  |  | HR3981 (Lo-16bits)
3983 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3984 |  |  |  | HR3983 (Lo-16bits)
3985 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3986 |  |  |  | HR3985 (Lo-16bits)
3987 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3988 |  |  |  | HR3987 (Lo-16bits)
3989 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3990 |  |  |  | HR3989 (Lo-16bits)
3991 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3992 |  |  |  | HR3991 (Lo-16bits)
3993 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3994 |  |  |  | HR3993 (Lo-16bits)
3995 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3996 |  |  |  | HR3995 (Lo-16bits)
3997 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3998 |  |  |  | HR3997 (Lo-16bits)
3999 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4000 |  |  |  | HR3999 (Lo-16bits)
4001 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4002 |  |  |  | HR4001 (Lo-16bits)
4003 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4004 |  |  |  | HR4003 (Lo-16bits)
4005 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4006 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4007 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4008 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4009 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4010 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4011 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4012 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4013 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4014 |  |  |  | HR4013 (Lo-16bits)
4015 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4016 |  |  |  | HR4015 (Lo-16bits)
4017 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4018 |  |  |  | HR4017 (Lo-16bits)
4019 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4020 |  |  |  | HR4019 (Lo-16bits)
4021 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4022 |  |  |  | HR4021 (Lo-16bits)
4023 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4024 |  |  |  | HR4023 (Lo-16bits)
4025 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4026 |  |  |  | HR4025 (Lo-16bits)
4027 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4028 |  |  |  | HR4027 (Lo-16bits)
4029 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4030 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4031 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4032 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4033 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4034 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4035 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4036 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4037 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4038 |  |  |  | HR4037 (Lo-16bits)
4039 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4040 |  |  |  | HR4039 (Lo-16bits)
4041 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4042 |  |  |  | HR4041 (Lo-16bits)
4043 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4044 |  |  |  | HR4043 (Lo-16bits)
4045 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4046 |  |  |  | HR4045 (Lo-16bits)
4047 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4048 |  |  |  | HR4047 (Lo-16bits)
4049 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4050 |  |  |  | HR4049 (Lo-16bits)
4051 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4052 |  |  |  | HR4051 (Lo-16bits)
4053 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4054 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4055 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4056 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4057 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4058 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4059 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4060 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4061 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4062 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4063 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4064 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4065 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4066 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4067 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4068 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4069 | NEF2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4070 |  |  |  | HR4069 (Lo-16bits)
4071 | NEF2:Delay type | RW | 1 | 0=DT;1=IDMT
4072 | NEF2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4073 |  |  |  | HR4072 (Lo-16bits)
4074 | NEF2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4075 | NEF2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4076 | NEF2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4077 | NEF2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4078 | NEF2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4079 |  |  |  | HR4078 (Lo-16bits)
4080 | NEF2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4081 |  |  |  | HR4080 (Lo-16bits)
4082 | NEF2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4083 |  |  |  | HR4082 (Lo-16bits)
4084 | NEF2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4085 |  |  |  | HR4084 (Lo-16bits)
4086 | NEF2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4087 | NEF2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4088 | NEF3:I0>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4089 | NEF3:I0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4090 | NEF3:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4091 | NEF3:I0>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4092 | NEF3:I0>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4093 |  |  |  | HR4092 (Lo-16bits)
4094 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4095 |  |  |  | HR4094 (Lo-16bits)
4096 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4097 |  |  |  | HR4096 (Lo-16bits)
4098 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4099 |  |  |  | HR4098 (Lo-16bits)
4100 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4101 |  |  |  | HR4100 (Lo-16bits)
4102 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4103 |  |  |  | HR4102 (Lo-16bits)
4104 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4105 |  |  |  | HR4104 (Lo-16bits)
4106 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4107 |  |  |  | HR4106 (Lo-16bits)
4108 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4109 |  |  |  | HR4108 (Lo-16bits)
4110 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4111 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4112 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4113 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4114 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4115 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4116 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4117 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4118 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4119 |  |  |  | HR4118 (Lo-16bits)
4120 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4121 |  |  |  | HR4120 (Lo-16bits)
4122 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4123 |  |  |  | HR4122 (Lo-16bits)
4124 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4125 |  |  |  | HR4124 (Lo-16bits)
4126 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4127 |  |  |  | HR4126 (Lo-16bits)
4128 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4129 |  |  |  | HR4128 (Lo-16bits)
4130 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4131 |  |  |  | HR4130 (Lo-16bits)
4132 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4133 |  |  |  | HR4132 (Lo-16bits)
4134 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4135 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4136 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4137 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4138 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4139 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4140 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4141 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4142 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4143 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4144 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4145 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4146 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4147 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4148 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4149 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4150 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4151 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4152 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4153 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4154 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4155 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4156 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4157 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4158 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4159 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4160 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4161 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4162 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4163 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4164 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4165 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4166 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4167 |  |  |  | HR4166 (Lo-16bits)
4168 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4169 |  |  |  | HR4168 (Lo-16bits)
4170 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4171 |  |  |  | HR4170 (Lo-16bits)
4172 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4173 |  |  |  | HR4172 (Lo-16bits)
4174 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4175 |  |  |  | HR4174 (Lo-16bits)
4176 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4177 |  |  |  | HR4176 (Lo-16bits)
4178 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4179 |  |  |  | HR4178 (Lo-16bits)
4180 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4181 |  |  |  | HR4180 (Lo-16bits)
4182 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4183 |  |  |  | HR4182 (Lo-16bits)
4184 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4185 |  |  |  | HR4184 (Lo-16bits)
4186 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4187 |  |  |  | HR4186 (Lo-16bits)
4188 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4189 |  |  |  | HR4188 (Lo-16bits)
4190 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4191 |  |  |  | HR4190 (Lo-16bits)
4192 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4193 |  |  |  | HR4192 (Lo-16bits)
4194 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4195 |  |  |  | HR4194 (Lo-16bits)
4196 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4197 |  |  |  | HR4196 (Lo-16bits)
4198 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4199 |  |  |  | HR4198 (Lo-16bits)
4200 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4201 |  |  |  | HR4200 (Lo-16bits)
4202 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4203 |  |  |  | HR4202 (Lo-16bits)
4204 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4205 |  |  |  | HR4204 (Lo-16bits)
4206 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4207 |  |  |  | HR4206 (Lo-16bits)
4208 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4209 |  |  |  | HR4208 (Lo-16bits)
4210 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4211 |  |  |  | HR4210 (Lo-16bits)
4212 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4213 |  |  |  | HR4212 (Lo-16bits)
4214 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4215 |  |  |  | HR4214 (Lo-16bits)
4216 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4217 |  |  |  | HR4216 (Lo-16bits)
4218 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4219 |  |  |  | HR4218 (Lo-16bits)
4220 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4221 |  |  |  | HR4220 (Lo-16bits)
4222 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4223 |  |  |  | HR4222 (Lo-16bits)
4224 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4225 |  |  |  | HR4224 (Lo-16bits)
4226 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4227 |  |  |  | HR4226 (Lo-16bits)
4228 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4229 |  |  |  | HR4228 (Lo-16bits)
4230 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4231 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4232 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4233 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4234 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4235 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4236 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4237 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4238 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4239 |  |  |  | HR4238 (Lo-16bits)
4240 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4241 |  |  |  | HR4240 (Lo-16bits)
4242 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4243 |  |  |  | HR4242 (Lo-16bits)
4244 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4245 |  |  |  | HR4244 (Lo-16bits)
4246 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4247 |  |  |  | HR4246 (Lo-16bits)
4248 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4249 |  |  |  | HR4248 (Lo-16bits)
4250 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4251 |  |  |  | HR4250 (Lo-16bits)
4252 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4253 |  |  |  | HR4252 (Lo-16bits)
4254 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4255 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4256 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4257 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4258 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4259 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4260 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4261 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4262 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4263 |  |  |  | HR4262 (Lo-16bits)
4264 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4265 |  |  |  | HR4264 (Lo-16bits)
4266 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4267 |  |  |  | HR4266 (Lo-16bits)
4268 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4269 |  |  |  | HR4268 (Lo-16bits)
4270 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4271 |  |  |  | HR4270 (Lo-16bits)
4272 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4273 |  |  |  | HR4272 (Lo-16bits)
4274 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4275 |  |  |  | HR4274 (Lo-16bits)
4276 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4277 |  |  |  | HR4276 (Lo-16bits)
4278 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4279 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4280 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4281 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4282 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4283 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4284 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4285 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4286 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4287 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4288 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4289 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4290 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4291 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4292 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4293 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4294 | NEF3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4295 |  |  |  | HR4294 (Lo-16bits)
4296 | NEF3:Delay type | RW | 1 | 0=DT;1=IDMT
4297 | NEF3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4298 |  |  |  | HR4297 (Lo-16bits)
4299 | NEF3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4300 | NEF3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4301 | NEF3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4302 | NEF3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4303 | NEF3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4304 |  |  |  | HR4303 (Lo-16bits)
4305 | NEF3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4306 |  |  |  | HR4305 (Lo-16bits)
4307 | NEF3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4308 |  |  |  | HR4307 (Lo-16bits)
4309 | NEF3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4310 |  |  |  | HR4309 (Lo-16bits)
4311 | NEF3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4312 | NEF3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4313 | NEF4:I0>>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4314 | NEF4:I0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4315 | NEF4:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4316 | NEF4:I0>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4317 | NEF4:I0>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4318 |  |  |  | HR4317 (Lo-16bits)
4319 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4320 |  |  |  | HR4319 (Lo-16bits)
4321 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4322 |  |  |  | HR4321 (Lo-16bits)
4323 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4324 |  |  |  | HR4323 (Lo-16bits)
4325 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4326 |  |  |  | HR4325 (Lo-16bits)
4327 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4328 |  |  |  | HR4327 (Lo-16bits)
4329 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4330 |  |  |  | HR4329 (Lo-16bits)
4331 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4332 |  |  |  | HR4331 (Lo-16bits)
4333 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4334 |  |  |  | HR4333 (Lo-16bits)
4335 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4336 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4337 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4338 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4339 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4340 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4341 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4342 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4343 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4344 |  |  |  | HR4343 (Lo-16bits)
4345 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4346 |  |  |  | HR4345 (Lo-16bits)
4347 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4348 |  |  |  | HR4347 (Lo-16bits)
4349 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4350 |  |  |  | HR4349 (Lo-16bits)
4351 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4352 |  |  |  | HR4351 (Lo-16bits)
4353 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4354 |  |  |  | HR4353 (Lo-16bits)
4355 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4356 |  |  |  | HR4355 (Lo-16bits)
4357 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4358 |  |  |  | HR4357 (Lo-16bits)
4359 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4360 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4361 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4362 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4363 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4364 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4365 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4366 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4367 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4368 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4369 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4370 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4371 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4372 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4373 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4374 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4375 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4376 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4377 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4378 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4379 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4380 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4381 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4382 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4383 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4384 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4385 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4386 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4387 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4388 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4389 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4390 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4391 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4392 |  |  |  | HR4391 (Lo-16bits)
4393 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4394 |  |  |  | HR4393 (Lo-16bits)
4395 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4396 |  |  |  | HR4395 (Lo-16bits)
4397 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4398 |  |  |  | HR4397 (Lo-16bits)
4399 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4400 |  |  |  | HR4399 (Lo-16bits)
4401 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4402 |  |  |  | HR4401 (Lo-16bits)
4403 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4404 |  |  |  | HR4403 (Lo-16bits)
4405 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4406 |  |  |  | HR4405 (Lo-16bits)
4407 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4408 |  |  |  | HR4407 (Lo-16bits)
4409 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4410 |  |  |  | HR4409 (Lo-16bits)
4411 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4412 |  |  |  | HR4411 (Lo-16bits)
4413 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4414 |  |  |  | HR4413 (Lo-16bits)
4415 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4416 |  |  |  | HR4415 (Lo-16bits)
4417 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4418 |  |  |  | HR4417 (Lo-16bits)
4419 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4420 |  |  |  | HR4419 (Lo-16bits)
4421 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4422 |  |  |  | HR4421 (Lo-16bits)
4423 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4424 |  |  |  | HR4423 (Lo-16bits)
4425 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4426 |  |  |  | HR4425 (Lo-16bits)
4427 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4428 |  |  |  | HR4427 (Lo-16bits)
4429 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4430 |  |  |  | HR4429 (Lo-16bits)
4431 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4432 |  |  |  | HR4431 (Lo-16bits)
4433 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4434 |  |  |  | HR4433 (Lo-16bits)
4435 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4436 |  |  |  | HR4435 (Lo-16bits)
4437 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4438 |  |  |  | HR4437 (Lo-16bits)
4439 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4440 |  |  |  | HR4439 (Lo-16bits)
4441 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4442 |  |  |  | HR4441 (Lo-16bits)
4443 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4444 |  |  |  | HR4443 (Lo-16bits)
4445 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4446 |  |  |  | HR4445 (Lo-16bits)
4447 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4448 |  |  |  | HR4447 (Lo-16bits)
4449 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4450 |  |  |  | HR4449 (Lo-16bits)
4451 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4452 |  |  |  | HR4451 (Lo-16bits)
4453 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4454 |  |  |  | HR4453 (Lo-16bits)
4455 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4456 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4457 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4458 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4459 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4460 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4461 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4462 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4463 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4464 |  |  |  | HR4463 (Lo-16bits)
4465 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4466 |  |  |  | HR4465 (Lo-16bits)
4467 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4468 |  |  |  | HR4467 (Lo-16bits)
4469 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4470 |  |  |  | HR4469 (Lo-16bits)
4471 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4472 |  |  |  | HR4471 (Lo-16bits)
4473 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4474 |  |  |  | HR4473 (Lo-16bits)
4475 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4476 |  |  |  | HR4475 (Lo-16bits)
4477 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4478 |  |  |  | HR4477 (Lo-16bits)
4479 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4480 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4481 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4482 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4483 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4484 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4485 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4486 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4487 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4488 |  |  |  | HR4487 (Lo-16bits)
4489 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4490 |  |  |  | HR4489 (Lo-16bits)
4491 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4492 |  |  |  | HR4491 (Lo-16bits)
4493 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4494 |  |  |  | HR4493 (Lo-16bits)
4495 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4496 |  |  |  | HR4495 (Lo-16bits)
4497 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4498 |  |  |  | HR4497 (Lo-16bits)
4499 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4500 |  |  |  | HR4499 (Lo-16bits)
4501 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4502 |  |  |  | HR4501 (Lo-16bits)
4503 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4504 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4505 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4506 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4507 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4508 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4509 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4510 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4511 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4512 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4513 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4514 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4515 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4516 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4517 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4518 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4519 | NEF4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4520 |  |  |  | HR4519 (Lo-16bits)
4521 | NEF4:Delay type | RW | 1 | 0=DT;1=IDMT
4522 | NEF4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4523 |  |  |  | HR4522 (Lo-16bits)
4524 | NEF4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4525 | NEF4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4526 | NEF4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4527 | NEF4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4528 | NEF4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4529 |  |  |  | HR4528 (Lo-16bits)
4530 | NEF4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4531 |  |  |  | HR4530 (Lo-16bits)
4532 | NEF4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4533 |  |  |  | HR4532 (Lo-16bits)
4534 | NEF4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4535 |  |  |  | HR4534 (Lo-16bits)
4536 | NEF4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4537 | NEF4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4538 | DEF1:I0dir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4539 | DEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4540 | DEF1:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4541 | DEF1:I0dir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4542 | DEF1:I0dir> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4543 |  |  |  | HR4542 (Lo-16bits)
4544 | DEF1:I0dir> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4545 |  |  |  | HR4544 (Lo-16bits)
4546 | DEF1:I0dir> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4547 |  |  |  | HR4546 (Lo-16bits)
4548 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4549 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4550 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4551 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4552 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4553 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4554 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4555 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4556 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4557 |  |  |  | HR4556 (Lo-16bits)
4558 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4559 |  |  |  | HR4558 (Lo-16bits)
4560 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4561 |  |  |  | HR4560 (Lo-16bits)
4562 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4563 |  |  |  | HR4562 (Lo-16bits)
4564 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4565 |  |  |  | HR4564 (Lo-16bits)
4566 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4567 |  |  |  | HR4566 (Lo-16bits)
4568 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4569 |  |  |  | HR4568 (Lo-16bits)
4570 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4571 |  |  |  | HR4570 (Lo-16bits)
4572 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4573 |  |  |  | HR4572 (Lo-16bits)
4574 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4575 |  |  |  | HR4574 (Lo-16bits)
4576 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4577 |  |  |  | HR4576 (Lo-16bits)
4578 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4579 |  |  |  | HR4578 (Lo-16bits)
4580 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4581 |  |  |  | HR4580 (Lo-16bits)
4582 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4583 |  |  |  | HR4582 (Lo-16bits)
4584 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4585 |  |  |  | HR4584 (Lo-16bits)
4586 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4587 |  |  |  | HR4586 (Lo-16bits)
4588 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4589 |  |  |  | HR4588 (Lo-16bits)
4590 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4591 |  |  |  | HR4590 (Lo-16bits)
4592 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4593 |  |  |  | HR4592 (Lo-16bits)
4594 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4595 |  |  |  | HR4594 (Lo-16bits)
4596 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4597 |  |  |  | HR4596 (Lo-16bits)
4598 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4599 |  |  |  | HR4598 (Lo-16bits)
4600 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4601 |  |  |  | HR4600 (Lo-16bits)
4602 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4603 |  |  |  | HR4602 (Lo-16bits)
4604 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4605 |  |  |  | HR4604 (Lo-16bits)
4606 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4607 |  |  |  | HR4606 (Lo-16bits)
4608 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4609 |  |  |  | HR4608 (Lo-16bits)
4610 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4611 |  |  |  | HR4610 (Lo-16bits)
4612 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4613 |  |  |  | HR4612 (Lo-16bits)
4614 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4615 |  |  |  | HR4614 (Lo-16bits)
4616 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4617 |  |  |  | HR4616 (Lo-16bits)
4618 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4619 |  |  |  | HR4618 (Lo-16bits)
4620 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4621 |  |  |  | HR4620 (Lo-16bits)
4622 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4623 |  |  |  | HR4622 (Lo-16bits)
4624 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4625 |  |  |  | HR4624 (Lo-16bits)
4626 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4627 |  |  |  | HR4626 (Lo-16bits)
4628 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4629 |  |  |  | HR4628 (Lo-16bits)
4630 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4631 |  |  |  | HR4630 (Lo-16bits)
4632 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4633 |  |  |  | HR4632 (Lo-16bits)
4634 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4635 |  |  |  | HR4634 (Lo-16bits)
4636 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4637 |  |  |  | HR4636 (Lo-16bits)
4638 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4639 |  |  |  | HR4638 (Lo-16bits)
4640 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4641 |  |  |  | HR4640 (Lo-16bits)
4642 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4643 |  |  |  | HR4642 (Lo-16bits)
4644 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4645 |  |  |  | HR4644 (Lo-16bits)
4646 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4647 |  |  |  | HR4646 (Lo-16bits)
4648 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4649 |  |  |  | HR4648 (Lo-16bits)
4650 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4651 |  |  |  | HR4650 (Lo-16bits)
4652 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4653 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4654 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4655 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4656 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4657 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4658 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4659 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4660 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4661 |  |  |  | HR4660 (Lo-16bits)
4662 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4663 |  |  |  | HR4662 (Lo-16bits)
4664 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4665 |  |  |  | HR4664 (Lo-16bits)
4666 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4667 |  |  |  | HR4666 (Lo-16bits)
4668 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4669 |  |  |  | HR4668 (Lo-16bits)
4670 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4671 |  |  |  | HR4670 (Lo-16bits)
4672 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4673 |  |  |  | HR4672 (Lo-16bits)
4674 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4675 |  |  |  | HR4674 (Lo-16bits)
4676 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4677 |  |  |  | HR4676 (Lo-16bits)
4678 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4679 |  |  |  | HR4678 (Lo-16bits)
4680 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4681 |  |  |  | HR4680 (Lo-16bits)
4682 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4683 |  |  |  | HR4682 (Lo-16bits)
4684 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4685 |  |  |  | HR4684 (Lo-16bits)
4686 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4687 |  |  |  | HR4686 (Lo-16bits)
4688 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4689 |  |  |  | HR4688 (Lo-16bits)
4690 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4691 |  |  |  | HR4690 (Lo-16bits)
4692 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4693 |  |  |  | HR4692 (Lo-16bits)
4694 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4695 |  |  |  | HR4694 (Lo-16bits)
4696 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4697 |  |  |  | HR4696 (Lo-16bits)
4698 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4699 |  |  |  | HR4698 (Lo-16bits)
4700 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4701 |  |  |  | HR4700 (Lo-16bits)
4702 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4703 |  |  |  | HR4702 (Lo-16bits)
4704 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4705 |  |  |  | HR4704 (Lo-16bits)
4706 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4707 |  |  |  | HR4706 (Lo-16bits)
4708 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4709 |  |  |  | HR4708 (Lo-16bits)
4710 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4711 |  |  |  | HR4710 (Lo-16bits)
4712 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4713 |  |  |  | HR4712 (Lo-16bits)
4714 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4715 |  |  |  | HR4714 (Lo-16bits)
4716 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4717 |  |  |  | HR4716 (Lo-16bits)
4718 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4719 |  |  |  | HR4718 (Lo-16bits)
4720 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4721 |  |  |  | HR4720 (Lo-16bits)
4722 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4723 |  |  |  | HR4722 (Lo-16bits)
4724 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4725 |  |  |  | HR4724 (Lo-16bits)
4726 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4727 |  |  |  | HR4726 (Lo-16bits)
4728 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4729 |  |  |  | HR4728 (Lo-16bits)
4730 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4731 |  |  |  | HR4730 (Lo-16bits)
4732 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4733 |  |  |  | HR4732 (Lo-16bits)
4734 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4735 |  |  |  | HR4734 (Lo-16bits)
4736 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4737 |  |  |  | HR4736 (Lo-16bits)
4738 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4739 |  |  |  | HR4738 (Lo-16bits)
4740 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4741 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4742 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4743 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4744 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4745 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4746 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4747 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4748 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4749 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4750 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4751 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4752 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4753 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4754 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4755 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4756 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4757 |  |  |  | HR4756 (Lo-16bits)
4758 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4759 |  |  |  | HR4758 (Lo-16bits)
4760 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4761 |  |  |  | HR4760 (Lo-16bits)
4762 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4763 |  |  |  | HR4762 (Lo-16bits)
4764 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4765 |  |  |  | HR4764 (Lo-16bits)
4766 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4767 |  |  |  | HR4766 (Lo-16bits)
4768 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4769 |  |  |  | HR4768 (Lo-16bits)
4770 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4771 |  |  |  | HR4770 (Lo-16bits)
4772 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4773 |  |  |  | HR4772 (Lo-16bits)
4774 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4775 |  |  |  | HR4774 (Lo-16bits)
4776 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4777 |  |  |  | HR4776 (Lo-16bits)
4778 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4779 |  |  |  | HR4778 (Lo-16bits)
4780 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4781 |  |  |  | HR4780 (Lo-16bits)
4782 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4783 |  |  |  | HR4782 (Lo-16bits)
4784 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4785 |  |  |  | HR4784 (Lo-16bits)
4786 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4787 |  |  |  | HR4786 (Lo-16bits)
4788 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4789 |  |  |  | HR4788 (Lo-16bits)
4790 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4791 |  |  |  | HR4790 (Lo-16bits)
4792 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4793 |  |  |  | HR4792 (Lo-16bits)
4794 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4795 |  |  |  | HR4794 (Lo-16bits)
4796 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4797 |  |  |  | HR4796 (Lo-16bits)
4798 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4799 |  |  |  | HR4798 (Lo-16bits)
4800 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4801 |  |  |  | HR4800 (Lo-16bits)
4802 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4803 |  |  |  | HR4802 (Lo-16bits)
4804 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4805 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4806 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4807 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4808 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4809 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4810 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4811 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4812 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4813 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4814 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4815 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4816 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4817 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4818 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4819 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4820 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4821 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4822 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4823 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4824 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4825 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4826 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4827 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4828 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4829 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4830 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4831 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4832 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4833 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4834 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4835 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4836 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4837 |  |  |  | HR4836 (Lo-16bits)
4838 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4839 |  |  |  | HR4838 (Lo-16bits)
4840 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4841 |  |  |  | HR4840 (Lo-16bits)
4842 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4843 |  |  |  | HR4842 (Lo-16bits)
4844 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4845 |  |  |  | HR4844 (Lo-16bits)
4846 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4847 |  |  |  | HR4846 (Lo-16bits)
4848 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4849 |  |  |  | HR4848 (Lo-16bits)
4850 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4851 |  |  |  | HR4850 (Lo-16bits)
4852 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4853 |  |  |  | HR4852 (Lo-16bits)
4854 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4855 |  |  |  | HR4854 (Lo-16bits)
4856 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4857 |  |  |  | HR4856 (Lo-16bits)
4858 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4859 |  |  |  | HR4858 (Lo-16bits)
4860 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4861 |  |  |  | HR4860 (Lo-16bits)
4862 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4863 |  |  |  | HR4862 (Lo-16bits)
4864 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4865 |  |  |  | HR4864 (Lo-16bits)
4866 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4867 |  |  |  | HR4866 (Lo-16bits)
4868 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4869 |  |  |  | HR4868 (Lo-16bits)
4870 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4871 |  |  |  | HR4870 (Lo-16bits)
4872 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4873 |  |  |  | HR4872 (Lo-16bits)
4874 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4875 |  |  |  | HR4874 (Lo-16bits)
4876 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4877 |  |  |  | HR4876 (Lo-16bits)
4878 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4879 |  |  |  | HR4878 (Lo-16bits)
4880 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4881 |  |  |  | HR4880 (Lo-16bits)
4882 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4883 |  |  |  | HR4882 (Lo-16bits)
4884 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4885 |  |  |  | HR4884 (Lo-16bits)
4886 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4887 |  |  |  | HR4886 (Lo-16bits)
4888 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4889 |  |  |  | HR4888 (Lo-16bits)
4890 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4891 |  |  |  | HR4890 (Lo-16bits)
4892 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4893 |  |  |  | HR4892 (Lo-16bits)
4894 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4895 |  |  |  | HR4894 (Lo-16bits)
4896 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4897 |  |  |  | HR4896 (Lo-16bits)
4898 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4899 |  |  |  | HR4898 (Lo-16bits)
4900 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4901 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4902 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4903 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4904 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4905 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4906 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4907 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4908 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4909 |  |  |  | HR4908 (Lo-16bits)
4910 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4911 |  |  |  | HR4910 (Lo-16bits)
4912 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4913 |  |  |  | HR4912 (Lo-16bits)
4914 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4915 |  |  |  | HR4914 (Lo-16bits)
4916 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4917 |  |  |  | HR4916 (Lo-16bits)
4918 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4919 |  |  |  | HR4918 (Lo-16bits)
4920 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4921 |  |  |  | HR4920 (Lo-16bits)
4922 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4923 |  |  |  | HR4922 (Lo-16bits)
4924 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4925 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4926 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4927 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4928 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4929 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4930 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4931 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4932 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4933 |  |  |  | HR4932 (Lo-16bits)
4934 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4935 |  |  |  | HR4934 (Lo-16bits)
4936 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4937 |  |  |  | HR4936 (Lo-16bits)
4938 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4939 |  |  |  | HR4938 (Lo-16bits)
4940 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4941 |  |  |  | HR4940 (Lo-16bits)
4942 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4943 |  |  |  | HR4942 (Lo-16bits)
4944 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4945 |  |  |  | HR4944 (Lo-16bits)
4946 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4947 |  |  |  | HR4946 (Lo-16bits)
4948 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4949 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4950 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4951 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4952 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4953 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4954 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4955 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4956 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4957 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4958 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4959 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4960 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4961 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4962 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4963 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4964 | DEF2:I0dir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4965 | DEF2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4966 | DEF2:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4967 | DEF2:I0dir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4968 | DEF2:I0dir>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4969 |  |  |  | HR4968 (Lo-16bits)
4970 | DEF2:I0dir>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4971 |  |  |  | HR4970 (Lo-16bits)
4972 | DEF2:I0dir>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4973 |  |  |  | HR4972 (Lo-16bits)
4974 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4975 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4976 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4977 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4978 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4979 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4980 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4981 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4982 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4983 |  |  |  | HR4982 (Lo-16bits)
4984 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4985 |  |  |  | HR4984 (Lo-16bits)
4986 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4987 |  |  |  | HR4986 (Lo-16bits)
4988 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4989 |  |  |  | HR4988 (Lo-16bits)
4990 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4991 |  |  |  | HR4990 (Lo-16bits)
4992 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4993 |  |  |  | HR4992 (Lo-16bits)
4994 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4995 |  |  |  | HR4994 (Lo-16bits)
4996 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4997 |  |  |  | HR4996 (Lo-16bits)
4998 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4999 |  |  |  | HR4998 (Lo-16bits)
5000 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5001 |  |  |  | HR5000 (Lo-16bits)
5002 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5003 |  |  |  | HR5002 (Lo-16bits)
5004 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5005 |  |  |  | HR5004 (Lo-16bits)
5006 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5007 |  |  |  | HR5006 (Lo-16bits)
5008 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5009 |  |  |  | HR5008 (Lo-16bits)
5010 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5011 |  |  |  | HR5010 (Lo-16bits)
5012 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5013 |  |  |  | HR5012 (Lo-16bits)
5014 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5015 |  |  |  | HR5014 (Lo-16bits)
5016 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5017 |  |  |  | HR5016 (Lo-16bits)
5018 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5019 |  |  |  | HR5018 (Lo-16bits)
5020 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5021 |  |  |  | HR5020 (Lo-16bits)
5022 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5023 |  |  |  | HR5022 (Lo-16bits)
5024 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5025 |  |  |  | HR5024 (Lo-16bits)
5026 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5027 |  |  |  | HR5026 (Lo-16bits)
5028 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5029 |  |  |  | HR5028 (Lo-16bits)
5030 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5031 |  |  |  | HR5030 (Lo-16bits)
5032 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5033 |  |  |  | HR5032 (Lo-16bits)
5034 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5035 |  |  |  | HR5034 (Lo-16bits)
5036 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5037 |  |  |  | HR5036 (Lo-16bits)
5038 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5039 |  |  |  | HR5038 (Lo-16bits)
5040 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5041 |  |  |  | HR5040 (Lo-16bits)
5042 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5043 |  |  |  | HR5042 (Lo-16bits)
5044 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5045 |  |  |  | HR5044 (Lo-16bits)
5046 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5047 |  |  |  | HR5046 (Lo-16bits)
5048 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5049 |  |  |  | HR5048 (Lo-16bits)
5050 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5051 |  |  |  | HR5050 (Lo-16bits)
5052 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5053 |  |  |  | HR5052 (Lo-16bits)
5054 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5055 |  |  |  | HR5054 (Lo-16bits)
5056 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5057 |  |  |  | HR5056 (Lo-16bits)
5058 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5059 |  |  |  | HR5058 (Lo-16bits)
5060 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5061 |  |  |  | HR5060 (Lo-16bits)
5062 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5063 |  |  |  | HR5062 (Lo-16bits)
5064 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5065 |  |  |  | HR5064 (Lo-16bits)
5066 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5067 |  |  |  | HR5066 (Lo-16bits)
5068 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5069 |  |  |  | HR5068 (Lo-16bits)
5070 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5071 |  |  |  | HR5070 (Lo-16bits)
5072 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5073 |  |  |  | HR5072 (Lo-16bits)
5074 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5075 |  |  |  | HR5074 (Lo-16bits)
5076 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5077 |  |  |  | HR5076 (Lo-16bits)
5078 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5079 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5080 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5081 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5082 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5083 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5084 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5085 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5086 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5087 |  |  |  | HR5086 (Lo-16bits)
5088 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5089 |  |  |  | HR5088 (Lo-16bits)
5090 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5091 |  |  |  | HR5090 (Lo-16bits)
5092 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5093 |  |  |  | HR5092 (Lo-16bits)
5094 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5095 |  |  |  | HR5094 (Lo-16bits)
5096 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5097 |  |  |  | HR5096 (Lo-16bits)
5098 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5099 |  |  |  | HR5098 (Lo-16bits)
5100 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5101 |  |  |  | HR5100 (Lo-16bits)
5102 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5103 |  |  |  | HR5102 (Lo-16bits)
5104 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5105 |  |  |  | HR5104 (Lo-16bits)
5106 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5107 |  |  |  | HR5106 (Lo-16bits)
5108 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5109 |  |  |  | HR5108 (Lo-16bits)
5110 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5111 |  |  |  | HR5110 (Lo-16bits)
5112 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5113 |  |  |  | HR5112 (Lo-16bits)
5114 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5115 |  |  |  | HR5114 (Lo-16bits)
5116 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5117 |  |  |  | HR5116 (Lo-16bits)
5118 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5119 |  |  |  | HR5118 (Lo-16bits)
5120 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5121 |  |  |  | HR5120 (Lo-16bits)
5122 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5123 |  |  |  | HR5122 (Lo-16bits)
5124 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5125 |  |  |  | HR5124 (Lo-16bits)
5126 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5127 |  |  |  | HR5126 (Lo-16bits)
5128 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5129 |  |  |  | HR5128 (Lo-16bits)
5130 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5131 |  |  |  | HR5130 (Lo-16bits)
5132 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5133 |  |  |  | HR5132 (Lo-16bits)
5134 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5135 |  |  |  | HR5134 (Lo-16bits)
5136 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5137 |  |  |  | HR5136 (Lo-16bits)
5138 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5139 |  |  |  | HR5138 (Lo-16bits)
5140 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5141 |  |  |  | HR5140 (Lo-16bits)
5142 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5143 |  |  |  | HR5142 (Lo-16bits)
5144 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5145 |  |  |  | HR5144 (Lo-16bits)
5146 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5147 |  |  |  | HR5146 (Lo-16bits)
5148 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5149 |  |  |  | HR5148 (Lo-16bits)
5150 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5151 |  |  |  | HR5150 (Lo-16bits)
5152 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5153 |  |  |  | HR5152 (Lo-16bits)
5154 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5155 |  |  |  | HR5154 (Lo-16bits)
5156 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5157 |  |  |  | HR5156 (Lo-16bits)
5158 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5159 |  |  |  | HR5158 (Lo-16bits)
5160 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5161 |  |  |  | HR5160 (Lo-16bits)
5162 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5163 |  |  |  | HR5162 (Lo-16bits)
5164 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5165 |  |  |  | HR5164 (Lo-16bits)
5166 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5167 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5168 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5169 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5170 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5171 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5172 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5173 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5174 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5175 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5176 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5177 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5178 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5179 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5180 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5181 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5182 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5183 |  |  |  | HR5182 (Lo-16bits)
5184 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5185 |  |  |  | HR5184 (Lo-16bits)
5186 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5187 |  |  |  | HR5186 (Lo-16bits)
5188 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5189 |  |  |  | HR5188 (Lo-16bits)
5190 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5191 |  |  |  | HR5190 (Lo-16bits)
5192 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5193 |  |  |  | HR5192 (Lo-16bits)
5194 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5195 |  |  |  | HR5194 (Lo-16bits)
5196 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5197 |  |  |  | HR5196 (Lo-16bits)
5198 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5199 |  |  |  | HR5198 (Lo-16bits)
5200 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5201 |  |  |  | HR5200 (Lo-16bits)
5202 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5203 |  |  |  | HR5202 (Lo-16bits)
5204 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5205 |  |  |  | HR5204 (Lo-16bits)
5206 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5207 |  |  |  | HR5206 (Lo-16bits)
5208 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5209 |  |  |  | HR5208 (Lo-16bits)
5210 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5211 |  |  |  | HR5210 (Lo-16bits)
5212 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5213 |  |  |  | HR5212 (Lo-16bits)
5214 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5215 |  |  |  | HR5214 (Lo-16bits)
5216 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5217 |  |  |  | HR5216 (Lo-16bits)
5218 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5219 |  |  |  | HR5218 (Lo-16bits)
5220 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5221 |  |  |  | HR5220 (Lo-16bits)
5222 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5223 |  |  |  | HR5222 (Lo-16bits)
5224 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5225 |  |  |  | HR5224 (Lo-16bits)
5226 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5227 |  |  |  | HR5226 (Lo-16bits)
5228 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5229 |  |  |  | HR5228 (Lo-16bits)
5230 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5231 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5232 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5233 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5234 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5235 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5236 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5237 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5238 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5239 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5240 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5241 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5242 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5243 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5244 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5245 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5246 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5247 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5248 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5249 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5250 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5251 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5252 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5253 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5254 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5255 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5256 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5257 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5258 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5259 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5260 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5261 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5262 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5263 |  |  |  | HR5262 (Lo-16bits)
5264 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5265 |  |  |  | HR5264 (Lo-16bits)
5266 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5267 |  |  |  | HR5266 (Lo-16bits)
5268 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5269 |  |  |  | HR5268 (Lo-16bits)
5270 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5271 |  |  |  | HR5270 (Lo-16bits)
5272 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5273 |  |  |  | HR5272 (Lo-16bits)
5274 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5275 |  |  |  | HR5274 (Lo-16bits)
5276 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5277 |  |  |  | HR5276 (Lo-16bits)
5278 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5279 |  |  |  | HR5278 (Lo-16bits)
5280 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5281 |  |  |  | HR5280 (Lo-16bits)
5282 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5283 |  |  |  | HR5282 (Lo-16bits)
5284 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5285 |  |  |  | HR5284 (Lo-16bits)
5286 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5287 |  |  |  | HR5286 (Lo-16bits)
5288 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5289 |  |  |  | HR5288 (Lo-16bits)
5290 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5291 |  |  |  | HR5290 (Lo-16bits)
5292 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5293 |  |  |  | HR5292 (Lo-16bits)
5294 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5295 |  |  |  | HR5294 (Lo-16bits)
5296 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5297 |  |  |  | HR5296 (Lo-16bits)
5298 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5299 |  |  |  | HR5298 (Lo-16bits)
5300 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5301 |  |  |  | HR5300 (Lo-16bits)
5302 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5303 |  |  |  | HR5302 (Lo-16bits)
5304 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5305 |  |  |  | HR5304 (Lo-16bits)
5306 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5307 |  |  |  | HR5306 (Lo-16bits)
5308 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5309 |  |  |  | HR5308 (Lo-16bits)
5310 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5311 |  |  |  | HR5310 (Lo-16bits)
5312 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5313 |  |  |  | HR5312 (Lo-16bits)
5314 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5315 |  |  |  | HR5314 (Lo-16bits)
5316 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5317 |  |  |  | HR5316 (Lo-16bits)
5318 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5319 |  |  |  | HR5318 (Lo-16bits)
5320 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5321 |  |  |  | HR5320 (Lo-16bits)
5322 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5323 |  |  |  | HR5322 (Lo-16bits)
5324 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5325 |  |  |  | HR5324 (Lo-16bits)
5326 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5327 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5328 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5329 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5330 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5331 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5332 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5333 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5334 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5335 |  |  |  | HR5334 (Lo-16bits)
5336 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5337 |  |  |  | HR5336 (Lo-16bits)
5338 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5339 |  |  |  | HR5338 (Lo-16bits)
5340 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5341 |  |  |  | HR5340 (Lo-16bits)
5342 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5343 |  |  |  | HR5342 (Lo-16bits)
5344 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5345 |  |  |  | HR5344 (Lo-16bits)
5346 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5347 |  |  |  | HR5346 (Lo-16bits)
5348 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5349 |  |  |  | HR5348 (Lo-16bits)
5350 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5351 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5352 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5353 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5354 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5355 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5356 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5357 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5358 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5359 |  |  |  | HR5358 (Lo-16bits)
5360 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5361 |  |  |  | HR5360 (Lo-16bits)
5362 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5363 |  |  |  | HR5362 (Lo-16bits)
5364 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5365 |  |  |  | HR5364 (Lo-16bits)
5366 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5367 |  |  |  | HR5366 (Lo-16bits)
5368 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5369 |  |  |  | HR5368 (Lo-16bits)
5370 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5371 |  |  |  | HR5370 (Lo-16bits)
5372 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5373 |  |  |  | HR5372 (Lo-16bits)
5374 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5375 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5376 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5377 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5378 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5379 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5380 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5381 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5382 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5383 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5384 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5385 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5386 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5387 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5388 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5389 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5390 | DEF3:I0dir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5391 | DEF3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5392 | DEF3:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5393 | DEF3:I0dir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5394 | DEF3:I0dir>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5395 |  |  |  | HR5394 (Lo-16bits)
5396 | DEF3:I0dir>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5397 |  |  |  | HR5396 (Lo-16bits)
5398 | DEF3:I0dir>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5399 |  |  |  | HR5398 (Lo-16bits)
5400 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5401 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5402 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5403 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5404 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5405 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5406 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5407 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5408 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5409 |  |  |  | HR5408 (Lo-16bits)
5410 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5411 |  |  |  | HR5410 (Lo-16bits)
5412 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5413 |  |  |  | HR5412 (Lo-16bits)
5414 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5415 |  |  |  | HR5414 (Lo-16bits)
5416 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5417 |  |  |  | HR5416 (Lo-16bits)
5418 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5419 |  |  |  | HR5418 (Lo-16bits)
5420 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5421 |  |  |  | HR5420 (Lo-16bits)
5422 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5423 |  |  |  | HR5422 (Lo-16bits)
5424 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5425 |  |  |  | HR5424 (Lo-16bits)
5426 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5427 |  |  |  | HR5426 (Lo-16bits)
5428 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5429 |  |  |  | HR5428 (Lo-16bits)
5430 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5431 |  |  |  | HR5430 (Lo-16bits)
5432 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5433 |  |  |  | HR5432 (Lo-16bits)
5434 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5435 |  |  |  | HR5434 (Lo-16bits)
5436 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5437 |  |  |  | HR5436 (Lo-16bits)
5438 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5439 |  |  |  | HR5438 (Lo-16bits)
5440 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5441 |  |  |  | HR5440 (Lo-16bits)
5442 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5443 |  |  |  | HR5442 (Lo-16bits)
5444 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5445 |  |  |  | HR5444 (Lo-16bits)
5446 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5447 |  |  |  | HR5446 (Lo-16bits)
5448 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5449 |  |  |  | HR5448 (Lo-16bits)
5450 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5451 |  |  |  | HR5450 (Lo-16bits)
5452 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5453 |  |  |  | HR5452 (Lo-16bits)
5454 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5455 |  |  |  | HR5454 (Lo-16bits)
5456 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5457 |  |  |  | HR5456 (Lo-16bits)
5458 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5459 |  |  |  | HR5458 (Lo-16bits)
5460 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5461 |  |  |  | HR5460 (Lo-16bits)
5462 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5463 |  |  |  | HR5462 (Lo-16bits)
5464 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5465 |  |  |  | HR5464 (Lo-16bits)
5466 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5467 |  |  |  | HR5466 (Lo-16bits)
5468 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5469 |  |  |  | HR5468 (Lo-16bits)
5470 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5471 |  |  |  | HR5470 (Lo-16bits)
5472 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5473 |  |  |  | HR5472 (Lo-16bits)
5474 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5475 |  |  |  | HR5474 (Lo-16bits)
5476 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5477 |  |  |  | HR5476 (Lo-16bits)
5478 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5479 |  |  |  | HR5478 (Lo-16bits)
5480 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5481 |  |  |  | HR5480 (Lo-16bits)
5482 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5483 |  |  |  | HR5482 (Lo-16bits)
5484 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5485 |  |  |  | HR5484 (Lo-16bits)
5486 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5487 |  |  |  | HR5486 (Lo-16bits)
5488 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5489 |  |  |  | HR5488 (Lo-16bits)
5490 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5491 |  |  |  | HR5490 (Lo-16bits)
5492 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5493 |  |  |  | HR5492 (Lo-16bits)
5494 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5495 |  |  |  | HR5494 (Lo-16bits)
5496 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5497 |  |  |  | HR5496 (Lo-16bits)
5498 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5499 |  |  |  | HR5498 (Lo-16bits)
5500 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5501 |  |  |  | HR5500 (Lo-16bits)
5502 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5503 |  |  |  | HR5502 (Lo-16bits)
5504 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5505 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5506 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5507 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5508 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5509 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5510 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5511 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5512 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5513 |  |  |  | HR5512 (Lo-16bits)
5514 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5515 |  |  |  | HR5514 (Lo-16bits)
5516 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5517 |  |  |  | HR5516 (Lo-16bits)
5518 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5519 |  |  |  | HR5518 (Lo-16bits)
5520 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5521 |  |  |  | HR5520 (Lo-16bits)
5522 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5523 |  |  |  | HR5522 (Lo-16bits)
5524 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5525 |  |  |  | HR5524 (Lo-16bits)
5526 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5527 |  |  |  | HR5526 (Lo-16bits)
5528 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5529 |  |  |  | HR5528 (Lo-16bits)
5530 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5531 |  |  |  | HR5530 (Lo-16bits)
5532 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5533 |  |  |  | HR5532 (Lo-16bits)
5534 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5535 |  |  |  | HR5534 (Lo-16bits)
5536 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5537 |  |  |  | HR5536 (Lo-16bits)
5538 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5539 |  |  |  | HR5538 (Lo-16bits)
5540 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5541 |  |  |  | HR5540 (Lo-16bits)
5542 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5543 |  |  |  | HR5542 (Lo-16bits)
5544 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5545 |  |  |  | HR5544 (Lo-16bits)
5546 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5547 |  |  |  | HR5546 (Lo-16bits)
5548 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5549 |  |  |  | HR5548 (Lo-16bits)
5550 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5551 |  |  |  | HR5550 (Lo-16bits)
5552 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5553 |  |  |  | HR5552 (Lo-16bits)
5554 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5555 |  |  |  | HR5554 (Lo-16bits)
5556 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5557 |  |  |  | HR5556 (Lo-16bits)
5558 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5559 |  |  |  | HR5558 (Lo-16bits)
5560 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5561 |  |  |  | HR5560 (Lo-16bits)
5562 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5563 |  |  |  | HR5562 (Lo-16bits)
5564 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5565 |  |  |  | HR5564 (Lo-16bits)
5566 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5567 |  |  |  | HR5566 (Lo-16bits)
5568 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5569 |  |  |  | HR5568 (Lo-16bits)
5570 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5571 |  |  |  | HR5570 (Lo-16bits)
5572 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5573 |  |  |  | HR5572 (Lo-16bits)
5574 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5575 |  |  |  | HR5574 (Lo-16bits)
5576 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5577 |  |  |  | HR5576 (Lo-16bits)
5578 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5579 |  |  |  | HR5578 (Lo-16bits)
5580 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5581 |  |  |  | HR5580 (Lo-16bits)
5582 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5583 |  |  |  | HR5582 (Lo-16bits)
5584 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5585 |  |  |  | HR5584 (Lo-16bits)
5586 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5587 |  |  |  | HR5586 (Lo-16bits)
5588 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5589 |  |  |  | HR5588 (Lo-16bits)
5590 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5591 |  |  |  | HR5590 (Lo-16bits)
5592 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5593 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5594 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5595 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5596 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5597 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5598 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5599 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5600 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5601 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5602 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5603 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5604 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5605 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5606 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5607 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5608 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5609 |  |  |  | HR5608 (Lo-16bits)
5610 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5611 |  |  |  | HR5610 (Lo-16bits)
5612 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5613 |  |  |  | HR5612 (Lo-16bits)
5614 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5615 |  |  |  | HR5614 (Lo-16bits)
5616 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5617 |  |  |  | HR5616 (Lo-16bits)
5618 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5619 |  |  |  | HR5618 (Lo-16bits)
5620 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5621 |  |  |  | HR5620 (Lo-16bits)
5622 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5623 |  |  |  | HR5622 (Lo-16bits)
5624 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5625 |  |  |  | HR5624 (Lo-16bits)
5626 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5627 |  |  |  | HR5626 (Lo-16bits)
5628 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5629 |  |  |  | HR5628 (Lo-16bits)
5630 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5631 |  |  |  | HR5630 (Lo-16bits)
5632 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5633 |  |  |  | HR5632 (Lo-16bits)
5634 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5635 |  |  |  | HR5634 (Lo-16bits)
5636 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5637 |  |  |  | HR5636 (Lo-16bits)
5638 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5639 |  |  |  | HR5638 (Lo-16bits)
5640 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5641 |  |  |  | HR5640 (Lo-16bits)
5642 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5643 |  |  |  | HR5642 (Lo-16bits)
5644 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5645 |  |  |  | HR5644 (Lo-16bits)
5646 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5647 |  |  |  | HR5646 (Lo-16bits)
5648 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5649 |  |  |  | HR5648 (Lo-16bits)
5650 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5651 |  |  |  | HR5650 (Lo-16bits)
5652 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5653 |  |  |  | HR5652 (Lo-16bits)
5654 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5655 |  |  |  | HR5654 (Lo-16bits)
5656 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5657 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5658 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5659 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5660 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5661 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5662 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5663 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5664 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5665 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5666 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5667 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5668 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5669 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5670 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5671 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5672 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5673 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5674 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5675 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5676 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5677 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5678 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5679 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5680 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5681 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5682 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5683 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5684 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5685 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5686 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5687 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5688 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5689 |  |  |  | HR5688 (Lo-16bits)
5690 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5691 |  |  |  | HR5690 (Lo-16bits)
5692 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5693 |  |  |  | HR5692 (Lo-16bits)
5694 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5695 |  |  |  | HR5694 (Lo-16bits)
5696 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5697 |  |  |  | HR5696 (Lo-16bits)
5698 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5699 |  |  |  | HR5698 (Lo-16bits)
5700 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5701 |  |  |  | HR5700 (Lo-16bits)
5702 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5703 |  |  |  | HR5702 (Lo-16bits)
5704 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5705 |  |  |  | HR5704 (Lo-16bits)
5706 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5707 |  |  |  | HR5706 (Lo-16bits)
5708 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5709 |  |  |  | HR5708 (Lo-16bits)
5710 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5711 |  |  |  | HR5710 (Lo-16bits)
5712 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5713 |  |  |  | HR5712 (Lo-16bits)
5714 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5715 |  |  |  | HR5714 (Lo-16bits)
5716 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5717 |  |  |  | HR5716 (Lo-16bits)
5718 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5719 |  |  |  | HR5718 (Lo-16bits)
5720 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5721 |  |  |  | HR5720 (Lo-16bits)
5722 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5723 |  |  |  | HR5722 (Lo-16bits)
5724 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5725 |  |  |  | HR5724 (Lo-16bits)
5726 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5727 |  |  |  | HR5726 (Lo-16bits)
5728 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5729 |  |  |  | HR5728 (Lo-16bits)
5730 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5731 |  |  |  | HR5730 (Lo-16bits)
5732 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5733 |  |  |  | HR5732 (Lo-16bits)
5734 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5735 |  |  |  | HR5734 (Lo-16bits)
5736 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5737 |  |  |  | HR5736 (Lo-16bits)
5738 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5739 |  |  |  | HR5738 (Lo-16bits)
5740 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5741 |  |  |  | HR5740 (Lo-16bits)
5742 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5743 |  |  |  | HR5742 (Lo-16bits)
5744 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5745 |  |  |  | HR5744 (Lo-16bits)
5746 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5747 |  |  |  | HR5746 (Lo-16bits)
5748 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5749 |  |  |  | HR5748 (Lo-16bits)
5750 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5751 |  |  |  | HR5750 (Lo-16bits)
5752 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5753 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5754 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5755 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5756 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5757 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5758 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5759 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5760 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5761 |  |  |  | HR5760 (Lo-16bits)
5762 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5763 |  |  |  | HR5762 (Lo-16bits)
5764 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5765 |  |  |  | HR5764 (Lo-16bits)
5766 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5767 |  |  |  | HR5766 (Lo-16bits)
5768 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5769 |  |  |  | HR5768 (Lo-16bits)
5770 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5771 |  |  |  | HR5770 (Lo-16bits)
5772 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5773 |  |  |  | HR5772 (Lo-16bits)
5774 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5775 |  |  |  | HR5774 (Lo-16bits)
5776 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5777 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5778 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5779 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5780 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5781 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5782 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5783 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5784 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5785 |  |  |  | HR5784 (Lo-16bits)
5786 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5787 |  |  |  | HR5786 (Lo-16bits)
5788 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5789 |  |  |  | HR5788 (Lo-16bits)
5790 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5791 |  |  |  | HR5790 (Lo-16bits)
5792 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5793 |  |  |  | HR5792 (Lo-16bits)
5794 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5795 |  |  |  | HR5794 (Lo-16bits)
5796 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5797 |  |  |  | HR5796 (Lo-16bits)
5798 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5799 |  |  |  | HR5798 (Lo-16bits)
5800 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5801 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5802 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5803 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5804 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5805 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5806 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5807 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5808 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5809 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5810 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5811 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5812 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5813 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5814 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5815 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5816 | DEF4:I0dir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5817 | DEF4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5818 | DEF4:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5819 | DEF4:I0dir>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5820 | DEF4:I0dir>>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5821 |  |  |  | HR5820 (Lo-16bits)
5822 | DEF4:I0dir>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5823 |  |  |  | HR5822 (Lo-16bits)
5824 | DEF4:I0dir>>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5825 |  |  |  | HR5824 (Lo-16bits)
5826 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5827 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5828 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5829 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5830 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5831 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5832 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5833 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5834 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5835 |  |  |  | HR5834 (Lo-16bits)
5836 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5837 |  |  |  | HR5836 (Lo-16bits)
5838 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5839 |  |  |  | HR5838 (Lo-16bits)
5840 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5841 |  |  |  | HR5840 (Lo-16bits)
5842 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5843 |  |  |  | HR5842 (Lo-16bits)
5844 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5845 |  |  |  | HR5844 (Lo-16bits)
5846 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5847 |  |  |  | HR5846 (Lo-16bits)
5848 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5849 |  |  |  | HR5848 (Lo-16bits)
5850 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5851 |  |  |  | HR5850 (Lo-16bits)
5852 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5853 |  |  |  | HR5852 (Lo-16bits)
5854 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5855 |  |  |  | HR5854 (Lo-16bits)
5856 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5857 |  |  |  | HR5856 (Lo-16bits)
5858 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5859 |  |  |  | HR5858 (Lo-16bits)
5860 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5861 |  |  |  | HR5860 (Lo-16bits)
5862 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5863 |  |  |  | HR5862 (Lo-16bits)
5864 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5865 |  |  |  | HR5864 (Lo-16bits)
5866 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5867 |  |  |  | HR5866 (Lo-16bits)
5868 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5869 |  |  |  | HR5868 (Lo-16bits)
5870 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5871 |  |  |  | HR5870 (Lo-16bits)
5872 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5873 |  |  |  | HR5872 (Lo-16bits)
5874 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5875 |  |  |  | HR5874 (Lo-16bits)
5876 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5877 |  |  |  | HR5876 (Lo-16bits)
5878 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5879 |  |  |  | HR5878 (Lo-16bits)
5880 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5881 |  |  |  | HR5880 (Lo-16bits)
5882 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5883 |  |  |  | HR5882 (Lo-16bits)
5884 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5885 |  |  |  | HR5884 (Lo-16bits)
5886 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5887 |  |  |  | HR5886 (Lo-16bits)
5888 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5889 |  |  |  | HR5888 (Lo-16bits)
5890 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5891 |  |  |  | HR5890 (Lo-16bits)
5892 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5893 |  |  |  | HR5892 (Lo-16bits)
5894 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5895 |  |  |  | HR5894 (Lo-16bits)
5896 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5897 |  |  |  | HR5896 (Lo-16bits)
5898 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5899 |  |  |  | HR5898 (Lo-16bits)
5900 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5901 |  |  |  | HR5900 (Lo-16bits)
5902 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5903 |  |  |  | HR5902 (Lo-16bits)
5904 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5905 |  |  |  | HR5904 (Lo-16bits)
5906 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5907 |  |  |  | HR5906 (Lo-16bits)
5908 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5909 |  |  |  | HR5908 (Lo-16bits)
5910 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5911 |  |  |  | HR5910 (Lo-16bits)
5912 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5913 |  |  |  | HR5912 (Lo-16bits)
5914 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5915 |  |  |  | HR5914 (Lo-16bits)
5916 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5917 |  |  |  | HR5916 (Lo-16bits)
5918 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5919 |  |  |  | HR5918 (Lo-16bits)
5920 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5921 |  |  |  | HR5920 (Lo-16bits)
5922 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5923 |  |  |  | HR5922 (Lo-16bits)
5924 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5925 |  |  |  | HR5924 (Lo-16bits)
5926 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5927 |  |  |  | HR5926 (Lo-16bits)
5928 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5929 |  |  |  | HR5928 (Lo-16bits)
5930 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5931 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5932 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5933 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5934 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5935 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5936 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5937 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5938 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5939 |  |  |  | HR5938 (Lo-16bits)
5940 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5941 |  |  |  | HR5940 (Lo-16bits)
5942 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5943 |  |  |  | HR5942 (Lo-16bits)
5944 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5945 |  |  |  | HR5944 (Lo-16bits)
5946 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5947 |  |  |  | HR5946 (Lo-16bits)
5948 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5949 |  |  |  | HR5948 (Lo-16bits)
5950 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5951 |  |  |  | HR5950 (Lo-16bits)
5952 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5953 |  |  |  | HR5952 (Lo-16bits)
5954 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5955 |  |  |  | HR5954 (Lo-16bits)
5956 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5957 |  |  |  | HR5956 (Lo-16bits)
5958 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5959 |  |  |  | HR5958 (Lo-16bits)
5960 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5961 |  |  |  | HR5960 (Lo-16bits)
5962 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5963 |  |  |  | HR5962 (Lo-16bits)
5964 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5965 |  |  |  | HR5964 (Lo-16bits)
5966 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5967 |  |  |  | HR5966 (Lo-16bits)
5968 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5969 |  |  |  | HR5968 (Lo-16bits)
5970 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5971 |  |  |  | HR5970 (Lo-16bits)
5972 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5973 |  |  |  | HR5972 (Lo-16bits)
5974 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5975 |  |  |  | HR5974 (Lo-16bits)
5976 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5977 |  |  |  | HR5976 (Lo-16bits)
5978 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5979 |  |  |  | HR5978 (Lo-16bits)
5980 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5981 |  |  |  | HR5980 (Lo-16bits)
5982 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5983 |  |  |  | HR5982 (Lo-16bits)
5984 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5985 |  |  |  | HR5984 (Lo-16bits)
5986 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5987 |  |  |  | HR5986 (Lo-16bits)
5988 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5989 |  |  |  | HR5988 (Lo-16bits)
5990 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5991 |  |  |  | HR5990 (Lo-16bits)
5992 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5993 |  |  |  | HR5992 (Lo-16bits)
5994 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5995 |  |  |  | HR5994 (Lo-16bits)
5996 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5997 |  |  |  | HR5996 (Lo-16bits)
5998 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5999 |  |  |  | HR5998 (Lo-16bits)
6000 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6001 |  |  |  | HR6000 (Lo-16bits)
6002 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6003 |  |  |  | HR6002 (Lo-16bits)
6004 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6005 |  |  |  | HR6004 (Lo-16bits)
6006 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6007 |  |  |  | HR6006 (Lo-16bits)
6008 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6009 |  |  |  | HR6008 (Lo-16bits)
6010 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6011 |  |  |  | HR6010 (Lo-16bits)
6012 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6013 |  |  |  | HR6012 (Lo-16bits)
6014 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6015 |  |  |  | HR6014 (Lo-16bits)
6016 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6017 |  |  |  | HR6016 (Lo-16bits)
6018 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6019 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6020 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6021 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6022 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6023 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6024 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6025 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6026 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6027 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6028 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6029 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6030 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6031 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6032 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6033 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6034 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6035 |  |  |  | HR6034 (Lo-16bits)
6036 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6037 |  |  |  | HR6036 (Lo-16bits)
6038 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6039 |  |  |  | HR6038 (Lo-16bits)
6040 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6041 |  |  |  | HR6040 (Lo-16bits)
6042 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6043 |  |  |  | HR6042 (Lo-16bits)
6044 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6045 |  |  |  | HR6044 (Lo-16bits)
6046 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6047 |  |  |  | HR6046 (Lo-16bits)
6048 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6049 |  |  |  | HR6048 (Lo-16bits)
6050 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6051 |  |  |  | HR6050 (Lo-16bits)
6052 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6053 |  |  |  | HR6052 (Lo-16bits)
6054 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6055 |  |  |  | HR6054 (Lo-16bits)
6056 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6057 |  |  |  | HR6056 (Lo-16bits)
6058 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6059 |  |  |  | HR6058 (Lo-16bits)
6060 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6061 |  |  |  | HR6060 (Lo-16bits)
6062 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6063 |  |  |  | HR6062 (Lo-16bits)
6064 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6065 |  |  |  | HR6064 (Lo-16bits)
6066 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6067 |  |  |  | HR6066 (Lo-16bits)
6068 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6069 |  |  |  | HR6068 (Lo-16bits)
6070 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6071 |  |  |  | HR6070 (Lo-16bits)
6072 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6073 |  |  |  | HR6072 (Lo-16bits)
6074 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6075 |  |  |  | HR6074 (Lo-16bits)
6076 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6077 |  |  |  | HR6076 (Lo-16bits)
6078 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6079 |  |  |  | HR6078 (Lo-16bits)
6080 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6081 |  |  |  | HR6080 (Lo-16bits)
6082 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6083 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6084 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6085 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6086 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6087 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6088 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6089 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6090 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6091 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6092 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6093 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6094 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6095 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6096 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6097 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6098 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6099 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6100 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6101 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6102 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6103 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6104 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6105 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6106 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6107 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6108 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6109 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6110 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6111 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6112 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6113 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6114 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6115 |  |  |  | HR6114 (Lo-16bits)
6116 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6117 |  |  |  | HR6116 (Lo-16bits)
6118 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6119 |  |  |  | HR6118 (Lo-16bits)
6120 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6121 |  |  |  | HR6120 (Lo-16bits)
6122 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6123 |  |  |  | HR6122 (Lo-16bits)
6124 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6125 |  |  |  | HR6124 (Lo-16bits)
6126 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6127 |  |  |  | HR6126 (Lo-16bits)
6128 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6129 |  |  |  | HR6128 (Lo-16bits)
6130 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6131 |  |  |  | HR6130 (Lo-16bits)
6132 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6133 |  |  |  | HR6132 (Lo-16bits)
6134 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6135 |  |  |  | HR6134 (Lo-16bits)
6136 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6137 |  |  |  | HR6136 (Lo-16bits)
6138 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6139 |  |  |  | HR6138 (Lo-16bits)
6140 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6141 |  |  |  | HR6140 (Lo-16bits)
6142 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6143 |  |  |  | HR6142 (Lo-16bits)
6144 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6145 |  |  |  | HR6144 (Lo-16bits)
6146 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6147 |  |  |  | HR6146 (Lo-16bits)
6148 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6149 |  |  |  | HR6148 (Lo-16bits)
6150 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6151 |  |  |  | HR6150 (Lo-16bits)
6152 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6153 |  |  |  | HR6152 (Lo-16bits)
6154 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6155 |  |  |  | HR6154 (Lo-16bits)
6156 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6157 |  |  |  | HR6156 (Lo-16bits)
6158 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6159 |  |  |  | HR6158 (Lo-16bits)
6160 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6161 |  |  |  | HR6160 (Lo-16bits)
6162 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6163 |  |  |  | HR6162 (Lo-16bits)
6164 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6165 |  |  |  | HR6164 (Lo-16bits)
6166 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6167 |  |  |  | HR6166 (Lo-16bits)
6168 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6169 |  |  |  | HR6168 (Lo-16bits)
6170 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6171 |  |  |  | HR6170 (Lo-16bits)
6172 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6173 |  |  |  | HR6172 (Lo-16bits)
6174 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6175 |  |  |  | HR6174 (Lo-16bits)
6176 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6177 |  |  |  | HR6176 (Lo-16bits)
6178 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6179 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6180 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6181 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6182 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6183 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6184 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6185 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6186 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6187 |  |  |  | HR6186 (Lo-16bits)
6188 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6189 |  |  |  | HR6188 (Lo-16bits)
6190 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6191 |  |  |  | HR6190 (Lo-16bits)
6192 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6193 |  |  |  | HR6192 (Lo-16bits)
6194 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6195 |  |  |  | HR6194 (Lo-16bits)
6196 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6197 |  |  |  | HR6196 (Lo-16bits)
6198 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6199 |  |  |  | HR6198 (Lo-16bits)
6200 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6201 |  |  |  | HR6200 (Lo-16bits)
6202 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6203 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6204 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6205 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6206 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6207 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6208 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6209 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6210 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6211 |  |  |  | HR6210 (Lo-16bits)
6212 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6213 |  |  |  | HR6212 (Lo-16bits)
6214 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6215 |  |  |  | HR6214 (Lo-16bits)
6216 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6217 |  |  |  | HR6216 (Lo-16bits)
6218 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6219 |  |  |  | HR6218 (Lo-16bits)
6220 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6221 |  |  |  | HR6220 (Lo-16bits)
6222 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6223 |  |  |  | HR6222 (Lo-16bits)
6224 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6225 |  |  |  | HR6224 (Lo-16bits)
6226 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6227 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6228 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6229 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6230 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6231 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6232 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6233 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6234 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6235 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6236 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6237 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6238 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6239 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6240 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6241 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6242 | IEF1:I0Int> condition | R | 1 | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
6243 | IEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
6244 | CUB1:I2> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6245 | CUB1:I2> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6246 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6247 |  |  |  | HR6246 (Lo-16bits)
6248 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6249 |  |  |  | HR6248 (Lo-16bits)
6250 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6251 |  |  |  | HR6250 (Lo-16bits)
6252 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6253 |  |  |  | HR6252 (Lo-16bits)
6254 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6255 |  |  |  | HR6254 (Lo-16bits)
6256 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6257 |  |  |  | HR6256 (Lo-16bits)
6258 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6259 |  |  |  | HR6258 (Lo-16bits)
6260 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6261 |  |  |  | HR6260 (Lo-16bits)
6262 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6263 |  |  |  | HR6262 (Lo-16bits)
6264 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6265 |  |  |  | HR6264 (Lo-16bits)
6266 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6267 |  |  |  | HR6266 (Lo-16bits)
6268 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6269 |  |  |  | HR6268 (Lo-16bits)
6270 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6271 |  |  |  | HR6270 (Lo-16bits)
6272 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6273 |  |  |  | HR6272 (Lo-16bits)
6274 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6275 |  |  |  | HR6274 (Lo-16bits)
6276 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6277 |  |  |  | HR6276 (Lo-16bits)
6278 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6279 |  |  |  | HR6278 (Lo-16bits)
6280 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6281 |  |  |  | HR6280 (Lo-16bits)
6282 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6283 |  |  |  | HR6282 (Lo-16bits)
6284 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6285 |  |  |  | HR6284 (Lo-16bits)
6286 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6287 |  |  |  | HR6286 (Lo-16bits)
6288 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6289 |  |  |  | HR6288 (Lo-16bits)
6290 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6291 |  |  |  | HR6290 (Lo-16bits)
6292 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6293 |  |  |  | HR6292 (Lo-16bits)
6294 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6295 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6296 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6297 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6298 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6299 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6300 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6301 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6302 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6303 |  |  |  | HR6302 (Lo-16bits)
6304 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6305 |  |  |  | HR6304 (Lo-16bits)
6306 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6307 |  |  |  | HR6306 (Lo-16bits)
6308 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6309 |  |  |  | HR6308 (Lo-16bits)
6310 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6311 |  |  |  | HR6310 (Lo-16bits)
6312 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6313 |  |  |  | HR6312 (Lo-16bits)
6314 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6315 |  |  |  | HR6314 (Lo-16bits)
6316 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6317 |  |  |  | HR6316 (Lo-16bits)
6318 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6319 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6320 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6321 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6322 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6323 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6324 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6325 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6326 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6327 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6328 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6329 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6330 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6331 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6332 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6333 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6334 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6335 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6336 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6337 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6338 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6339 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6340 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6341 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6342 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6343 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6344 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6345 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6346 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6347 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6348 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6349 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6350 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6351 |  |  |  | HR6350 (Lo-16bits)
6352 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6353 |  |  |  | HR6352 (Lo-16bits)
6354 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6355 |  |  |  | HR6354 (Lo-16bits)
6356 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6357 |  |  |  | HR6356 (Lo-16bits)
6358 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6359 |  |  |  | HR6358 (Lo-16bits)
6360 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6361 |  |  |  | HR6360 (Lo-16bits)
6362 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6363 |  |  |  | HR6362 (Lo-16bits)
6364 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6365 |  |  |  | HR6364 (Lo-16bits)
6366 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6367 |  |  |  | HR6366 (Lo-16bits)
6368 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6369 |  |  |  | HR6368 (Lo-16bits)
6370 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6371 |  |  |  | HR6370 (Lo-16bits)
6372 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6373 |  |  |  | HR6372 (Lo-16bits)
6374 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6375 |  |  |  | HR6374 (Lo-16bits)
6376 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6377 |  |  |  | HR6376 (Lo-16bits)
6378 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6379 |  |  |  | HR6378 (Lo-16bits)
6380 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6381 |  |  |  | HR6380 (Lo-16bits)
6382 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6383 |  |  |  | HR6382 (Lo-16bits)
6384 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6385 |  |  |  | HR6384 (Lo-16bits)
6386 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6387 |  |  |  | HR6386 (Lo-16bits)
6388 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6389 |  |  |  | HR6388 (Lo-16bits)
6390 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6391 |  |  |  | HR6390 (Lo-16bits)
6392 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6393 |  |  |  | HR6392 (Lo-16bits)
6394 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6395 |  |  |  | HR6394 (Lo-16bits)
6396 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6397 |  |  |  | HR6396 (Lo-16bits)
6398 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6399 |  |  |  | HR6398 (Lo-16bits)
6400 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6401 |  |  |  | HR6400 (Lo-16bits)
6402 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6403 |  |  |  | HR6402 (Lo-16bits)
6404 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6405 |  |  |  | HR6404 (Lo-16bits)
6406 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6407 |  |  |  | HR6406 (Lo-16bits)
6408 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6409 |  |  |  | HR6408 (Lo-16bits)
6410 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6411 |  |  |  | HR6410 (Lo-16bits)
6412 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6413 |  |  |  | HR6412 (Lo-16bits)
6414 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6415 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6416 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6417 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6418 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6419 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6420 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6421 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6422 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6423 |  |  |  | HR6422 (Lo-16bits)
6424 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6425 |  |  |  | HR6424 (Lo-16bits)
6426 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6427 |  |  |  | HR6426 (Lo-16bits)
6428 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6429 |  |  |  | HR6428 (Lo-16bits)
6430 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6431 |  |  |  | HR6430 (Lo-16bits)
6432 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6433 |  |  |  | HR6432 (Lo-16bits)
6434 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6435 |  |  |  | HR6434 (Lo-16bits)
6436 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6437 |  |  |  | HR6436 (Lo-16bits)
6438 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6439 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6440 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6441 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6442 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6443 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6444 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6445 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6446 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6447 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6448 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6449 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6450 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6451 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6452 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6453 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6454 | CUB2:I2>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6455 | CUB2:I2>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6456 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6457 |  |  |  | HR6456 (Lo-16bits)
6458 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6459 |  |  |  | HR6458 (Lo-16bits)
6460 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6461 |  |  |  | HR6460 (Lo-16bits)
6462 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6463 |  |  |  | HR6462 (Lo-16bits)
6464 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6465 |  |  |  | HR6464 (Lo-16bits)
6466 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6467 |  |  |  | HR6466 (Lo-16bits)
6468 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6469 |  |  |  | HR6468 (Lo-16bits)
6470 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6471 |  |  |  | HR6470 (Lo-16bits)
6472 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6473 |  |  |  | HR6472 (Lo-16bits)
6474 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6475 |  |  |  | HR6474 (Lo-16bits)
6476 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6477 |  |  |  | HR6476 (Lo-16bits)
6478 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6479 |  |  |  | HR6478 (Lo-16bits)
6480 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6481 |  |  |  | HR6480 (Lo-16bits)
6482 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6483 |  |  |  | HR6482 (Lo-16bits)
6484 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6485 |  |  |  | HR6484 (Lo-16bits)
6486 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6487 |  |  |  | HR6486 (Lo-16bits)
6488 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6489 |  |  |  | HR6488 (Lo-16bits)
6490 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6491 |  |  |  | HR6490 (Lo-16bits)
6492 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6493 |  |  |  | HR6492 (Lo-16bits)
6494 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6495 |  |  |  | HR6494 (Lo-16bits)
6496 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6497 |  |  |  | HR6496 (Lo-16bits)
6498 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6499 |  |  |  | HR6498 (Lo-16bits)
6500 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6501 |  |  |  | HR6500 (Lo-16bits)
6502 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6503 |  |  |  | HR6502 (Lo-16bits)
6504 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6505 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6506 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6507 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6508 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6509 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6510 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6511 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6512 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6513 |  |  |  | HR6512 (Lo-16bits)
6514 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6515 |  |  |  | HR6514 (Lo-16bits)
6516 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6517 |  |  |  | HR6516 (Lo-16bits)
6518 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6519 |  |  |  | HR6518 (Lo-16bits)
6520 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6521 |  |  |  | HR6520 (Lo-16bits)
6522 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6523 |  |  |  | HR6522 (Lo-16bits)
6524 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6525 |  |  |  | HR6524 (Lo-16bits)
6526 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6527 |  |  |  | HR6526 (Lo-16bits)
6528 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6529 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6530 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6531 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6532 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6533 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6534 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6535 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6536 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6537 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6538 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6539 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6540 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6541 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6542 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6543 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6544 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6545 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6546 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6547 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6548 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6549 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6550 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6551 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6552 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6553 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6554 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6555 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6556 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6557 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6558 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6559 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6560 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6561 |  |  |  | HR6560 (Lo-16bits)
6562 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6563 |  |  |  | HR6562 (Lo-16bits)
6564 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6565 |  |  |  | HR6564 (Lo-16bits)
6566 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6567 |  |  |  | HR6566 (Lo-16bits)
6568 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6569 |  |  |  | HR6568 (Lo-16bits)
6570 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6571 |  |  |  | HR6570 (Lo-16bits)
6572 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6573 |  |  |  | HR6572 (Lo-16bits)
6574 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6575 |  |  |  | HR6574 (Lo-16bits)
6576 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6577 |  |  |  | HR6576 (Lo-16bits)
6578 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6579 |  |  |  | HR6578 (Lo-16bits)
6580 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6581 |  |  |  | HR6580 (Lo-16bits)
6582 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6583 |  |  |  | HR6582 (Lo-16bits)
6584 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6585 |  |  |  | HR6584 (Lo-16bits)
6586 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6587 |  |  |  | HR6586 (Lo-16bits)
6588 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6589 |  |  |  | HR6588 (Lo-16bits)
6590 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6591 |  |  |  | HR6590 (Lo-16bits)
6592 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6593 |  |  |  | HR6592 (Lo-16bits)
6594 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6595 |  |  |  | HR6594 (Lo-16bits)
6596 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6597 |  |  |  | HR6596 (Lo-16bits)
6598 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6599 |  |  |  | HR6598 (Lo-16bits)
6600 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6601 |  |  |  | HR6600 (Lo-16bits)
6602 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6603 |  |  |  | HR6602 (Lo-16bits)
6604 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6605 |  |  |  | HR6604 (Lo-16bits)
6606 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6607 |  |  |  | HR6606 (Lo-16bits)
6608 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6609 |  |  |  | HR6608 (Lo-16bits)
6610 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6611 |  |  |  | HR6610 (Lo-16bits)
6612 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6613 |  |  |  | HR6612 (Lo-16bits)
6614 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6615 |  |  |  | HR6614 (Lo-16bits)
6616 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6617 |  |  |  | HR6616 (Lo-16bits)
6618 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6619 |  |  |  | HR6618 (Lo-16bits)
6620 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6621 |  |  |  | HR6620 (Lo-16bits)
6622 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6623 |  |  |  | HR6622 (Lo-16bits)
6624 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6625 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6626 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6627 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6628 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6629 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6630 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6631 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6632 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6633 |  |  |  | HR6632 (Lo-16bits)
6634 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6635 |  |  |  | HR6634 (Lo-16bits)
6636 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6637 |  |  |  | HR6636 (Lo-16bits)
6638 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6639 |  |  |  | HR6638 (Lo-16bits)
6640 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6641 |  |  |  | HR6640 (Lo-16bits)
6642 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6643 |  |  |  | HR6642 (Lo-16bits)
6644 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6645 |  |  |  | HR6644 (Lo-16bits)
6646 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6647 |  |  |  | HR6646 (Lo-16bits)
6648 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6649 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6650 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6651 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6652 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6653 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6654 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6655 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6656 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6657 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6658 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6659 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6660 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6661 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6662 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6663 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6664 | CUB3:I2>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6665 | CUB3:I2>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6666 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6667 |  |  |  | HR6666 (Lo-16bits)
6668 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6669 |  |  |  | HR6668 (Lo-16bits)
6670 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6671 |  |  |  | HR6670 (Lo-16bits)
6672 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6673 |  |  |  | HR6672 (Lo-16bits)
6674 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6675 |  |  |  | HR6674 (Lo-16bits)
6676 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6677 |  |  |  | HR6676 (Lo-16bits)
6678 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6679 |  |  |  | HR6678 (Lo-16bits)
6680 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6681 |  |  |  | HR6680 (Lo-16bits)
6682 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6683 |  |  |  | HR6682 (Lo-16bits)
6684 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6685 |  |  |  | HR6684 (Lo-16bits)
6686 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6687 |  |  |  | HR6686 (Lo-16bits)
6688 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6689 |  |  |  | HR6688 (Lo-16bits)
6690 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6691 |  |  |  | HR6690 (Lo-16bits)
6692 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6693 |  |  |  | HR6692 (Lo-16bits)
6694 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6695 |  |  |  | HR6694 (Lo-16bits)
6696 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6697 |  |  |  | HR6696 (Lo-16bits)
6698 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6699 |  |  |  | HR6698 (Lo-16bits)
6700 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6701 |  |  |  | HR6700 (Lo-16bits)
6702 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6703 |  |  |  | HR6702 (Lo-16bits)
6704 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6705 |  |  |  | HR6704 (Lo-16bits)
6706 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6707 |  |  |  | HR6706 (Lo-16bits)
6708 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6709 |  |  |  | HR6708 (Lo-16bits)
6710 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6711 |  |  |  | HR6710 (Lo-16bits)
6712 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6713 |  |  |  | HR6712 (Lo-16bits)
6714 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6715 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6716 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6717 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6718 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6719 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6720 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6721 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6722 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6723 |  |  |  | HR6722 (Lo-16bits)
6724 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6725 |  |  |  | HR6724 (Lo-16bits)
6726 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6727 |  |  |  | HR6726 (Lo-16bits)
6728 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6729 |  |  |  | HR6728 (Lo-16bits)
6730 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6731 |  |  |  | HR6730 (Lo-16bits)
6732 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6733 |  |  |  | HR6732 (Lo-16bits)
6734 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6735 |  |  |  | HR6734 (Lo-16bits)
6736 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6737 |  |  |  | HR6736 (Lo-16bits)
6738 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6739 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6740 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6741 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6742 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6743 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6744 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6745 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6746 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6747 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6748 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6749 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6750 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6751 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6752 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6753 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6754 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6755 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6756 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6757 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6758 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6759 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6760 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6761 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6762 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6763 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6764 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6765 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6766 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6767 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6768 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6769 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6770 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6771 |  |  |  | HR6770 (Lo-16bits)
6772 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6773 |  |  |  | HR6772 (Lo-16bits)
6774 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6775 |  |  |  | HR6774 (Lo-16bits)
6776 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6777 |  |  |  | HR6776 (Lo-16bits)
6778 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6779 |  |  |  | HR6778 (Lo-16bits)
6780 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6781 |  |  |  | HR6780 (Lo-16bits)
6782 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6783 |  |  |  | HR6782 (Lo-16bits)
6784 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6785 |  |  |  | HR6784 (Lo-16bits)
6786 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6787 |  |  |  | HR6786 (Lo-16bits)
6788 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6789 |  |  |  | HR6788 (Lo-16bits)
6790 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6791 |  |  |  | HR6790 (Lo-16bits)
6792 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6793 |  |  |  | HR6792 (Lo-16bits)
6794 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6795 |  |  |  | HR6794 (Lo-16bits)
6796 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6797 |  |  |  | HR6796 (Lo-16bits)
6798 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6799 |  |  |  | HR6798 (Lo-16bits)
6800 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6801 |  |  |  | HR6800 (Lo-16bits)
6802 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6803 |  |  |  | HR6802 (Lo-16bits)
6804 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6805 |  |  |  | HR6804 (Lo-16bits)
6806 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6807 |  |  |  | HR6806 (Lo-16bits)
6808 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6809 |  |  |  | HR6808 (Lo-16bits)
6810 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6811 |  |  |  | HR6810 (Lo-16bits)
6812 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6813 |  |  |  | HR6812 (Lo-16bits)
6814 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6815 |  |  |  | HR6814 (Lo-16bits)
6816 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6817 |  |  |  | HR6816 (Lo-16bits)
6818 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6819 |  |  |  | HR6818 (Lo-16bits)
6820 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6821 |  |  |  | HR6820 (Lo-16bits)
6822 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6823 |  |  |  | HR6822 (Lo-16bits)
6824 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6825 |  |  |  | HR6824 (Lo-16bits)
6826 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6827 |  |  |  | HR6826 (Lo-16bits)
6828 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6829 |  |  |  | HR6828 (Lo-16bits)
6830 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6831 |  |  |  | HR6830 (Lo-16bits)
6832 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6833 |  |  |  | HR6832 (Lo-16bits)
6834 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6835 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6836 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6837 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6838 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6839 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6840 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6841 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6842 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6843 |  |  |  | HR6842 (Lo-16bits)
6844 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6845 |  |  |  | HR6844 (Lo-16bits)
6846 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6847 |  |  |  | HR6846 (Lo-16bits)
6848 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6849 |  |  |  | HR6848 (Lo-16bits)
6850 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6851 |  |  |  | HR6850 (Lo-16bits)
6852 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6853 |  |  |  | HR6852 (Lo-16bits)
6854 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6855 |  |  |  | HR6854 (Lo-16bits)
6856 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6857 |  |  |  | HR6856 (Lo-16bits)
6858 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6859 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6860 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6861 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6862 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6863 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6864 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6865 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6866 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6867 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6868 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6869 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6870 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6871 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6872 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6873 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6874 | CUB4:I2>>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6875 | CUB4:I2>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6876 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6877 |  |  |  | HR6876 (Lo-16bits)
6878 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6879 |  |  |  | HR6878 (Lo-16bits)
6880 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6881 |  |  |  | HR6880 (Lo-16bits)
6882 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6883 |  |  |  | HR6882 (Lo-16bits)
6884 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6885 |  |  |  | HR6884 (Lo-16bits)
6886 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6887 |  |  |  | HR6886 (Lo-16bits)
6888 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6889 |  |  |  | HR6888 (Lo-16bits)
6890 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6891 |  |  |  | HR6890 (Lo-16bits)
6892 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6893 |  |  |  | HR6892 (Lo-16bits)
6894 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6895 |  |  |  | HR6894 (Lo-16bits)
6896 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6897 |  |  |  | HR6896 (Lo-16bits)
6898 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6899 |  |  |  | HR6898 (Lo-16bits)
6900 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6901 |  |  |  | HR6900 (Lo-16bits)
6902 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6903 |  |  |  | HR6902 (Lo-16bits)
6904 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6905 |  |  |  | HR6904 (Lo-16bits)
6906 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6907 |  |  |  | HR6906 (Lo-16bits)
6908 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6909 |  |  |  | HR6908 (Lo-16bits)
6910 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6911 |  |  |  | HR6910 (Lo-16bits)
6912 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6913 |  |  |  | HR6912 (Lo-16bits)
6914 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6915 |  |  |  | HR6914 (Lo-16bits)
6916 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6917 |  |  |  | HR6916 (Lo-16bits)
6918 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6919 |  |  |  | HR6918 (Lo-16bits)
6920 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6921 |  |  |  | HR6920 (Lo-16bits)
6922 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6923 |  |  |  | HR6922 (Lo-16bits)
6924 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6925 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6926 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6927 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6928 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6929 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6930 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6931 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6932 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6933 |  |  |  | HR6932 (Lo-16bits)
6934 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6935 |  |  |  | HR6934 (Lo-16bits)
6936 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6937 |  |  |  | HR6936 (Lo-16bits)
6938 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6939 |  |  |  | HR6938 (Lo-16bits)
6940 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6941 |  |  |  | HR6940 (Lo-16bits)
6942 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6943 |  |  |  | HR6942 (Lo-16bits)
6944 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6945 |  |  |  | HR6944 (Lo-16bits)
6946 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6947 |  |  |  | HR6946 (Lo-16bits)
6948 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6949 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6950 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6951 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6952 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6953 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6954 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6955 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6956 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6957 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6958 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6959 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6960 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6961 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6962 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6963 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6964 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6965 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6966 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6967 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6968 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6969 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6970 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6971 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6972 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6973 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6974 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6975 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6976 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6977 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6978 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6979 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6980 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6981 |  |  |  | HR6980 (Lo-16bits)
6982 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6983 |  |  |  | HR6982 (Lo-16bits)
6984 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6985 |  |  |  | HR6984 (Lo-16bits)
6986 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6987 |  |  |  | HR6986 (Lo-16bits)
6988 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6989 |  |  |  | HR6988 (Lo-16bits)
6990 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6991 |  |  |  | HR6990 (Lo-16bits)
6992 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6993 |  |  |  | HR6992 (Lo-16bits)
6994 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6995 |  |  |  | HR6994 (Lo-16bits)
6996 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6997 |  |  |  | HR6996 (Lo-16bits)
6998 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6999 |  |  |  | HR6998 (Lo-16bits)
7000 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7001 |  |  |  | HR7000 (Lo-16bits)
7002 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7003 |  |  |  | HR7002 (Lo-16bits)
7004 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7005 |  |  |  | HR7004 (Lo-16bits)
7006 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7007 |  |  |  | HR7006 (Lo-16bits)
7008 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7009 |  |  |  | HR7008 (Lo-16bits)
7010 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7011 |  |  |  | HR7010 (Lo-16bits)
7012 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7013 |  |  |  | HR7012 (Lo-16bits)
7014 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7015 |  |  |  | HR7014 (Lo-16bits)
7016 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7017 |  |  |  | HR7016 (Lo-16bits)
7018 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7019 |  |  |  | HR7018 (Lo-16bits)
7020 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7021 |  |  |  | HR7020 (Lo-16bits)
7022 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7023 |  |  |  | HR7022 (Lo-16bits)
7024 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7025 |  |  |  | HR7024 (Lo-16bits)
7026 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7027 |  |  |  | HR7026 (Lo-16bits)
7028 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7029 |  |  |  | HR7028 (Lo-16bits)
7030 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7031 |  |  |  | HR7030 (Lo-16bits)
7032 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7033 |  |  |  | HR7032 (Lo-16bits)
7034 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7035 |  |  |  | HR7034 (Lo-16bits)
7036 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7037 |  |  |  | HR7036 (Lo-16bits)
7038 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7039 |  |  |  | HR7038 (Lo-16bits)
7040 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7041 |  |  |  | HR7040 (Lo-16bits)
7042 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7043 |  |  |  | HR7042 (Lo-16bits)
7044 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7045 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7046 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7047 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7048 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7049 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7050 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7051 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7052 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7053 |  |  |  | HR7052 (Lo-16bits)
7054 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7055 |  |  |  | HR7054 (Lo-16bits)
7056 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7057 |  |  |  | HR7056 (Lo-16bits)
7058 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7059 |  |  |  | HR7058 (Lo-16bits)
7060 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7061 |  |  |  | HR7060 (Lo-16bits)
7062 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7063 |  |  |  | HR7062 (Lo-16bits)
7064 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7065 |  |  |  | HR7064 (Lo-16bits)
7066 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7067 |  |  |  | HR7066 (Lo-16bits)
7068 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7069 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7070 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7071 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7072 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7073 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7074 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7075 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7076 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7077 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7078 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7079 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7080 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7081 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7082 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7083 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7084 | HOC1:Ih> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7085 | HOC1:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7086 |  |  |  | HR7085 (Lo-16bits)
7087 | HOC1:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7088 |  |  |  | HR7087 (Lo-16bits)
7089 | HOC1:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7090 |  |  |  | HR7089 (Lo-16bits)
7091 | HOC1:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7092 |  |  |  | HR7091 (Lo-16bits)
7093 | HOC1:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7094 |  |  |  | HR7093 (Lo-16bits)
7095 | HOC1:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7096 |  |  |  | HR7095 (Lo-16bits)
7097 | HOC1:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7098 |  |  |  | HR7097 (Lo-16bits)
7099 | HOC1:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7100 |  |  |  | HR7099 (Lo-16bits)
7101 | HOC1:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7102 |  |  |  | HR7101 (Lo-16bits)
7103 | HOC1:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7104 |  |  |  | HR7103 (Lo-16bits)
7105 | HOC2:Ih>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7106 | HOC2:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7107 |  |  |  | HR7106 (Lo-16bits)
7108 | HOC2:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7109 |  |  |  | HR7108 (Lo-16bits)
7110 | HOC2:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7111 |  |  |  | HR7110 (Lo-16bits)
7112 | HOC2:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7113 |  |  |  | HR7112 (Lo-16bits)
7114 | HOC2:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7115 |  |  |  | HR7114 (Lo-16bits)
7116 | HOC2:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7117 |  |  |  | HR7116 (Lo-16bits)
7118 | HOC2:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7119 |  |  |  | HR7118 (Lo-16bits)
7120 | HOC2:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7121 |  |  |  | HR7120 (Lo-16bits)
7122 | HOC2:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7123 |  |  |  | HR7122 (Lo-16bits)
7124 | HOC2:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7125 |  |  |  | HR7124 (Lo-16bits)
7126 | HOC3:Ih>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7127 | HOC3:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7128 |  |  |  | HR7127 (Lo-16bits)
7129 | HOC3:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7130 |  |  |  | HR7129 (Lo-16bits)
7131 | HOC3:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7132 |  |  |  | HR7131 (Lo-16bits)
7133 | HOC3:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7134 |  |  |  | HR7133 (Lo-16bits)
7135 | HOC3:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7136 |  |  |  | HR7135 (Lo-16bits)
7137 | HOC3:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7138 |  |  |  | HR7137 (Lo-16bits)
7139 | HOC3:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7140 |  |  |  | HR7139 (Lo-16bits)
7141 | HOC3:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7142 |  |  |  | HR7141 (Lo-16bits)
7143 | HOC3:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7144 |  |  |  | HR7143 (Lo-16bits)
7145 | HOC3:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7146 |  |  |  | HR7145 (Lo-16bits)
7147 | HOC4:Ih>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7148 | HOC4:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7149 |  |  |  | HR7148 (Lo-16bits)
7150 | HOC4:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7151 |  |  |  | HR7150 (Lo-16bits)
7152 | HOC4:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7153 |  |  |  | HR7152 (Lo-16bits)
7154 | HOC4:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7155 |  |  |  | HR7154 (Lo-16bits)
7156 | HOC4:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7157 |  |  |  | HR7156 (Lo-16bits)
7158 | HOC4:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7159 |  |  |  | HR7158 (Lo-16bits)
7160 | HOC4:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7161 |  |  |  | HR7160 (Lo-16bits)
7162 | HOC4:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7163 |  |  |  | HR7162 (Lo-16bits)
7164 | HOC4:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7165 |  |  |  | HR7164 (Lo-16bits)
7166 | HOC4:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7167 |  |  |  | HR7166 (Lo-16bits)
7168 | CLP1:CLP condition | R | 1 | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
7169 | CBF1:CBFP condition | R | 1 | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
7170 | MST1:Motor is now | R | 1 | 0=Stopped;1=Starting;2=Running;3=Stalled
7171 | TRF1:Transformer is now | R | 1 | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
7172 | DIF1:Idx> condition | R | 2 | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On (Hi-16bits)
7173 |  |  |  | HR7172 (Lo-16bits)
7174 | DIF1:REFHV> condition | R | 2 | 0b=HV REF Blocked;1b=HV REF Trip (Hi-16bits)
7175 |  |  |  | HR7174 (Lo-16bits)
7176 | DIF1:REFLV> condition | R | 2 | 0b=LV REF Blocked;1b=LV REF Trip (Hi-16bits)
7177 |  |  |  | HR7176 (Lo-16bits)
7178 | DIF1:L1 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7179 | DIF1:L2 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7180 | DIF1:L3 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7181 | REF1:I0d> condition | R | 1 | 0=Normal;1=Trip;2=Blocked
7182 | TOLT1:TT> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7183 | TOLT1:TT> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7184 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7185 | TOLT1:TT> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7186 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7187 | TOLT1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7188 | TOLT1:Temp C or F deg | RW | 1 | 0=C;1=F
7189 | TOLT1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7190 | TOLT1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7191 | TOLT1:TT> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7192 |  |  |  | HR7191 (Lo-16bits)
7193 | TOLF1:TF> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7194 | TOLF1:TF> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7195 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7196 | TOLF1:TF> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7197 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7198 | TOLF1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7199 | TOLF1:Temp C or F deg | RW | 1 | 0=C;1=F
7200 | TOLF1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7201 | TOLF1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7202 | TOLF1:Set or Estimate tau (t const) | RW | 1 | 0=Set;1=Estimate
7203 | TOLF1:TF> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7204 |  |  |  | HR7203 (Lo-16bits)
7205 | TOLM1:TM> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7206 | TOLM1:TM> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7207 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7208 | TOLM1:TM> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7209 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7210 | TOLM1:Motor status | R | 1 | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
7211 | TOLM1:Temp C or F deg | RW | 1 | 0=C;1=F
7212 | TOLM1:NPS Biasing in use | RW | 1 | 0=No NPS biasing;1=NPS Biasing in use
7213 | TOLM1:Time constants | RW | 1 | 0=Single;1=Multiple
7214 | TOLM1:Estimate Short TC and timings | RW | 1 | 0=Set manually;1=Estimate (on-line)
7215 | TOLM1:T const dyn. balancing | RW | 1 | 0=Fixed;1=Dynamic
7216 | TOLM1:Dev.Temp (tmax) | RW | 1 | 0=A;1=B;2=F;3=H;4=Manual set
7217 | TOLM1:Amb. T Selection | RW | 1 | 0=Manual set;1=RTD
7218 | TOLM1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7219 | TOLM1:TM> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7220 |  |  |  | HR7219 (Lo-16bits)
7221 | LCR1:ISt> condition | R | 1 | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
7222 | FSP1:N> condition | R | 1 | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
7223 | NUC1:I< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7224 | MJP1:Im> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7225 | OV1:U> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7226 | OV1:U> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7227 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7228 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7229 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7230 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7231 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7232 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7233 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7234 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7235 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7236 |  |  |  | HR7235 (Lo-16bits)
7237 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7238 |  |  |  | HR7237 (Lo-16bits)
7239 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7240 |  |  |  | HR7239 (Lo-16bits)
7241 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7242 |  |  |  | HR7241 (Lo-16bits)
7243 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7244 |  |  |  | HR7243 (Lo-16bits)
7245 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7246 |  |  |  | HR7245 (Lo-16bits)
7247 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7248 |  |  |  | HR7247 (Lo-16bits)
7249 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7250 |  |  |  | HR7249 (Lo-16bits)
7251 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7252 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7253 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7254 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7255 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7256 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7257 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7258 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7259 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7260 |  |  |  | HR7259 (Lo-16bits)
7261 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7262 |  |  |  | HR7261 (Lo-16bits)
7263 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7264 |  |  |  | HR7263 (Lo-16bits)
7265 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7266 |  |  |  | HR7265 (Lo-16bits)
7267 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7268 |  |  |  | HR7267 (Lo-16bits)
7269 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7270 |  |  |  | HR7269 (Lo-16bits)
7271 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7272 |  |  |  | HR7271 (Lo-16bits)
7273 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7274 |  |  |  | HR7273 (Lo-16bits)
7275 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7276 |  |  |  | HR7275 (Lo-16bits)
7277 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7278 |  |  |  | HR7277 (Lo-16bits)
7279 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7280 |  |  |  | HR7279 (Lo-16bits)
7281 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7282 |  |  |  | HR7281 (Lo-16bits)
7283 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7284 |  |  |  | HR7283 (Lo-16bits)
7285 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7286 |  |  |  | HR7285 (Lo-16bits)
7287 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7288 |  |  |  | HR7287 (Lo-16bits)
7289 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7290 |  |  |  | HR7289 (Lo-16bits)
7291 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7292 |  |  |  | HR7291 (Lo-16bits)
7293 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7294 |  |  |  | HR7293 (Lo-16bits)
7295 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7296 |  |  |  | HR7295 (Lo-16bits)
7297 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7298 |  |  |  | HR7297 (Lo-16bits)
7299 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7300 |  |  |  | HR7299 (Lo-16bits)
7301 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7302 |  |  |  | HR7301 (Lo-16bits)
7303 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7304 |  |  |  | HR7303 (Lo-16bits)
7305 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7306 |  |  |  | HR7305 (Lo-16bits)
7307 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7308 |  |  |  | HR7307 (Lo-16bits)
7309 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7310 |  |  |  | HR7309 (Lo-16bits)
7311 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7312 |  |  |  | HR7311 (Lo-16bits)
7313 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7314 |  |  |  | HR7313 (Lo-16bits)
7315 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7316 |  |  |  | HR7315 (Lo-16bits)
7317 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7318 |  |  |  | HR7317 (Lo-16bits)
7319 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7320 |  |  |  | HR7319 (Lo-16bits)
7321 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7322 |  |  |  | HR7321 (Lo-16bits)
7323 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7324 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7325 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7326 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7327 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7328 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7329 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7330 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7331 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7332 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7333 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7334 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7335 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7336 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7337 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7338 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7339 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7340 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7341 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7342 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7343 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7344 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7345 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7346 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7347 | OV2:U>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7348 | OV2:U>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7349 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7350 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7351 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7352 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7353 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7354 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7355 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7356 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7357 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7358 |  |  |  | HR7357 (Lo-16bits)
7359 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7360 |  |  |  | HR7359 (Lo-16bits)
7361 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7362 |  |  |  | HR7361 (Lo-16bits)
7363 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7364 |  |  |  | HR7363 (Lo-16bits)
7365 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7366 |  |  |  | HR7365 (Lo-16bits)
7367 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7368 |  |  |  | HR7367 (Lo-16bits)
7369 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7370 |  |  |  | HR7369 (Lo-16bits)
7371 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7372 |  |  |  | HR7371 (Lo-16bits)
7373 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7374 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7375 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7376 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7377 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7378 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7379 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7380 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7381 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7382 |  |  |  | HR7381 (Lo-16bits)
7383 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7384 |  |  |  | HR7383 (Lo-16bits)
7385 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7386 |  |  |  | HR7385 (Lo-16bits)
7387 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7388 |  |  |  | HR7387 (Lo-16bits)
7389 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7390 |  |  |  | HR7389 (Lo-16bits)
7391 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7392 |  |  |  | HR7391 (Lo-16bits)
7393 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7394 |  |  |  | HR7393 (Lo-16bits)
7395 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7396 |  |  |  | HR7395 (Lo-16bits)
7397 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7398 |  |  |  | HR7397 (Lo-16bits)
7399 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7400 |  |  |  | HR7399 (Lo-16bits)
7401 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7402 |  |  |  | HR7401 (Lo-16bits)
7403 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7404 |  |  |  | HR7403 (Lo-16bits)
7405 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7406 |  |  |  | HR7405 (Lo-16bits)
7407 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7408 |  |  |  | HR7407 (Lo-16bits)
7409 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7410 |  |  |  | HR7409 (Lo-16bits)
7411 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7412 |  |  |  | HR7411 (Lo-16bits)
7413 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7414 |  |  |  | HR7413 (Lo-16bits)
7415 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7416 |  |  |  | HR7415 (Lo-16bits)
7417 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7418 |  |  |  | HR7417 (Lo-16bits)
7419 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7420 |  |  |  | HR7419 (Lo-16bits)
7421 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7422 |  |  |  | HR7421 (Lo-16bits)
7423 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7424 |  |  |  | HR7423 (Lo-16bits)
7425 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7426 |  |  |  | HR7425 (Lo-16bits)
7427 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7428 |  |  |  | HR7427 (Lo-16bits)
7429 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7430 |  |  |  | HR7429 (Lo-16bits)
7431 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7432 |  |  |  | HR7431 (Lo-16bits)
7433 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7434 |  |  |  | HR7433 (Lo-16bits)
7435 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7436 |  |  |  | HR7435 (Lo-16bits)
7437 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7438 |  |  |  | HR7437 (Lo-16bits)
7439 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7440 |  |  |  | HR7439 (Lo-16bits)
7441 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7442 |  |  |  | HR7441 (Lo-16bits)
7443 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7444 |  |  |  | HR7443 (Lo-16bits)
7445 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7446 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7447 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7448 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7449 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7450 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7451 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7452 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7453 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7454 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7455 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7456 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7457 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7458 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7459 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7460 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7461 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7462 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7463 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7464 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7465 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7466 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7467 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7468 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7469 | OV3:U>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7470 | OV3:U>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7471 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7472 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7473 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7474 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7475 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7476 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7477 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7478 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7479 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7480 |  |  |  | HR7479 (Lo-16bits)
7481 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7482 |  |  |  | HR7481 (Lo-16bits)
7483 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7484 |  |  |  | HR7483 (Lo-16bits)
7485 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7486 |  |  |  | HR7485 (Lo-16bits)
7487 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7488 |  |  |  | HR7487 (Lo-16bits)
7489 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7490 |  |  |  | HR7489 (Lo-16bits)
7491 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7492 |  |  |  | HR7491 (Lo-16bits)
7493 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7494 |  |  |  | HR7493 (Lo-16bits)
7495 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7496 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7497 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7498 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7499 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7500 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7501 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7502 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7503 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7504 |  |  |  | HR7503 (Lo-16bits)
7505 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7506 |  |  |  | HR7505 (Lo-16bits)
7507 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7508 |  |  |  | HR7507 (Lo-16bits)
7509 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7510 |  |  |  | HR7509 (Lo-16bits)
7511 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7512 |  |  |  | HR7511 (Lo-16bits)
7513 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7514 |  |  |  | HR7513 (Lo-16bits)
7515 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7516 |  |  |  | HR7515 (Lo-16bits)
7517 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7518 |  |  |  | HR7517 (Lo-16bits)
7519 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7520 |  |  |  | HR7519 (Lo-16bits)
7521 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7522 |  |  |  | HR7521 (Lo-16bits)
7523 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7524 |  |  |  | HR7523 (Lo-16bits)
7525 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7526 |  |  |  | HR7525 (Lo-16bits)
7527 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7528 |  |  |  | HR7527 (Lo-16bits)
7529 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7530 |  |  |  | HR7529 (Lo-16bits)
7531 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7532 |  |  |  | HR7531 (Lo-16bits)
7533 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7534 |  |  |  | HR7533 (Lo-16bits)
7535 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7536 |  |  |  | HR7535 (Lo-16bits)
7537 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7538 |  |  |  | HR7537 (Lo-16bits)
7539 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7540 |  |  |  | HR7539 (Lo-16bits)
7541 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7542 |  |  |  | HR7541 (Lo-16bits)
7543 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7544 |  |  |  | HR7543 (Lo-16bits)
7545 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7546 |  |  |  | HR7545 (Lo-16bits)
7547 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7548 |  |  |  | HR7547 (Lo-16bits)
7549 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7550 |  |  |  | HR7549 (Lo-16bits)
7551 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7552 |  |  |  | HR7551 (Lo-16bits)
7553 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7554 |  |  |  | HR7553 (Lo-16bits)
7555 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7556 |  |  |  | HR7555 (Lo-16bits)
7557 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7558 |  |  |  | HR7557 (Lo-16bits)
7559 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7560 |  |  |  | HR7559 (Lo-16bits)
7561 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7562 |  |  |  | HR7561 (Lo-16bits)
7563 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7564 |  |  |  | HR7563 (Lo-16bits)
7565 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7566 |  |  |  | HR7565 (Lo-16bits)
7567 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7568 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7569 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7570 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7571 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7572 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7573 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7574 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7575 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7576 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7577 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7578 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7579 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7580 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7581 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7582 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7583 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7584 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7585 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7586 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7587 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7588 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7589 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7590 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7591 | OV4:U>>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7592 | OV4:U>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7593 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7594 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7595 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7596 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7597 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7598 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7599 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7600 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7601 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7602 |  |  |  | HR7601 (Lo-16bits)
7603 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7604 |  |  |  | HR7603 (Lo-16bits)
7605 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7606 |  |  |  | HR7605 (Lo-16bits)
7607 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7608 |  |  |  | HR7607 (Lo-16bits)
7609 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7610 |  |  |  | HR7609 (Lo-16bits)
7611 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7612 |  |  |  | HR7611 (Lo-16bits)
7613 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7614 |  |  |  | HR7613 (Lo-16bits)
7615 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7616 |  |  |  | HR7615 (Lo-16bits)
7617 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7618 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7619 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7620 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7621 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7622 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7623 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7624 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7625 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7626 |  |  |  | HR7625 (Lo-16bits)
7627 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7628 |  |  |  | HR7627 (Lo-16bits)
7629 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7630 |  |  |  | HR7629 (Lo-16bits)
7631 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7632 |  |  |  | HR7631 (Lo-16bits)
7633 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7634 |  |  |  | HR7633 (Lo-16bits)
7635 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7636 |  |  |  | HR7635 (Lo-16bits)
7637 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7638 |  |  |  | HR7637 (Lo-16bits)
7639 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7640 |  |  |  | HR7639 (Lo-16bits)
7641 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7642 |  |  |  | HR7641 (Lo-16bits)
7643 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7644 |  |  |  | HR7643 (Lo-16bits)
7645 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7646 |  |  |  | HR7645 (Lo-16bits)
7647 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7648 |  |  |  | HR7647 (Lo-16bits)
7649 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7650 |  |  |  | HR7649 (Lo-16bits)
7651 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7652 |  |  |  | HR7651 (Lo-16bits)
7653 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7654 |  |  |  | HR7653 (Lo-16bits)
7655 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7656 |  |  |  | HR7655 (Lo-16bits)
7657 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7658 |  |  |  | HR7657 (Lo-16bits)
7659 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7660 |  |  |  | HR7659 (Lo-16bits)
7661 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7662 |  |  |  | HR7661 (Lo-16bits)
7663 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7664 |  |  |  | HR7663 (Lo-16bits)
7665 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7666 |  |  |  | HR7665 (Lo-16bits)
7667 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7668 |  |  |  | HR7667 (Lo-16bits)
7669 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7670 |  |  |  | HR7669 (Lo-16bits)
7671 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7672 |  |  |  | HR7671 (Lo-16bits)
7673 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7674 |  |  |  | HR7673 (Lo-16bits)
7675 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7676 |  |  |  | HR7675 (Lo-16bits)
7677 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7678 |  |  |  | HR7677 (Lo-16bits)
7679 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7680 |  |  |  | HR7679 (Lo-16bits)
7681 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7682 |  |  |  | HR7681 (Lo-16bits)
7683 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7684 |  |  |  | HR7683 (Lo-16bits)
7685 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7686 |  |  |  | HR7685 (Lo-16bits)
7687 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7688 |  |  |  | HR7687 (Lo-16bits)
7689 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7690 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7691 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7692 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7693 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7694 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7695 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7696 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7697 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7698 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7699 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7700 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7701 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7702 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7703 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7704 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7705 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7706 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7707 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7708 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7709 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7710 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7711 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7712 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7713 | UV1:U< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7714 | UV1:U< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7715 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7716 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7717 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7718 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7719 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7720 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7721 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7722 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7723 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7724 |  |  |  | HR7723 (Lo-16bits)
7725 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7726 |  |  |  | HR7725 (Lo-16bits)
7727 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7728 |  |  |  | HR7727 (Lo-16bits)
7729 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7730 |  |  |  | HR7729 (Lo-16bits)
7731 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7732 |  |  |  | HR7731 (Lo-16bits)
7733 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7734 |  |  |  | HR7733 (Lo-16bits)
7735 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7736 |  |  |  | HR7735 (Lo-16bits)
7737 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7738 |  |  |  | HR7737 (Lo-16bits)
7739 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7740 |  |  |  | HR7739 (Lo-16bits)
7741 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7742 |  |  |  | HR7741 (Lo-16bits)
7743 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7744 |  |  |  | HR7743 (Lo-16bits)
7745 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7746 |  |  |  | HR7745 (Lo-16bits)
7747 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7748 |  |  |  | HR7747 (Lo-16bits)
7749 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7750 |  |  |  | HR7749 (Lo-16bits)
7751 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7752 |  |  |  | HR7751 (Lo-16bits)
7753 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7754 |  |  |  | HR7753 (Lo-16bits)
7755 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7756 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7757 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7758 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7759 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7760 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7761 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7762 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7763 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7764 |  |  |  | HR7763 (Lo-16bits)
7765 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7766 |  |  |  | HR7765 (Lo-16bits)
7767 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7768 |  |  |  | HR7767 (Lo-16bits)
7769 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7770 |  |  |  | HR7769 (Lo-16bits)
7771 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7772 |  |  |  | HR7771 (Lo-16bits)
7773 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7774 |  |  |  | HR7773 (Lo-16bits)
7775 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7776 |  |  |  | HR7775 (Lo-16bits)
7777 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7778 |  |  |  | HR7777 (Lo-16bits)
7779 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7780 |  |  |  | HR7779 (Lo-16bits)
7781 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7782 |  |  |  | HR7781 (Lo-16bits)
7783 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7784 |  |  |  | HR7783 (Lo-16bits)
7785 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7786 |  |  |  | HR7785 (Lo-16bits)
7787 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7788 |  |  |  | HR7787 (Lo-16bits)
7789 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7790 |  |  |  | HR7789 (Lo-16bits)
7791 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7792 |  |  |  | HR7791 (Lo-16bits)
7793 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7794 |  |  |  | HR7793 (Lo-16bits)
7795 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7796 |  |  |  | HR7795 (Lo-16bits)
7797 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7798 |  |  |  | HR7797 (Lo-16bits)
7799 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7800 |  |  |  | HR7799 (Lo-16bits)
7801 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7802 |  |  |  | HR7801 (Lo-16bits)
7803 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7804 |  |  |  | HR7803 (Lo-16bits)
7805 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7806 |  |  |  | HR7805 (Lo-16bits)
7807 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7808 |  |  |  | HR7807 (Lo-16bits)
7809 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7810 |  |  |  | HR7809 (Lo-16bits)
7811 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7812 |  |  |  | HR7811 (Lo-16bits)
7813 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7814 |  |  |  | HR7813 (Lo-16bits)
7815 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7816 |  |  |  | HR7815 (Lo-16bits)
7817 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7818 |  |  |  | HR7817 (Lo-16bits)
7819 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7820 |  |  |  | HR7819 (Lo-16bits)
7821 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7822 |  |  |  | HR7821 (Lo-16bits)
7823 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7824 |  |  |  | HR7823 (Lo-16bits)
7825 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7826 |  |  |  | HR7825 (Lo-16bits)
7827 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7828 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7829 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7830 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7831 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7832 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7833 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7834 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7835 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7836 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7837 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7838 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7839 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7840 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7841 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7842 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7843 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7844 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7845 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7846 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7847 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7848 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7849 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7850 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7851 | UV2:U<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7852 | UV2:U<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7853 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7854 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7855 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7856 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7857 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7858 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7859 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7860 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7861 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7862 |  |  |  | HR7861 (Lo-16bits)
7863 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7864 |  |  |  | HR7863 (Lo-16bits)
7865 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7866 |  |  |  | HR7865 (Lo-16bits)
7867 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7868 |  |  |  | HR7867 (Lo-16bits)
7869 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7870 |  |  |  | HR7869 (Lo-16bits)
7871 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7872 |  |  |  | HR7871 (Lo-16bits)
7873 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7874 |  |  |  | HR7873 (Lo-16bits)
7875 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7876 |  |  |  | HR7875 (Lo-16bits)
7877 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7878 |  |  |  | HR7877 (Lo-16bits)
7879 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7880 |  |  |  | HR7879 (Lo-16bits)
7881 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7882 |  |  |  | HR7881 (Lo-16bits)
7883 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7884 |  |  |  | HR7883 (Lo-16bits)
7885 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7886 |  |  |  | HR7885 (Lo-16bits)
7887 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7888 |  |  |  | HR7887 (Lo-16bits)
7889 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7890 |  |  |  | HR7889 (Lo-16bits)
7891 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7892 |  |  |  | HR7891 (Lo-16bits)
7893 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7894 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7895 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7896 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7897 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7898 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7899 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7900 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7901 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7902 |  |  |  | HR7901 (Lo-16bits)
7903 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7904 |  |  |  | HR7903 (Lo-16bits)
7905 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7906 |  |  |  | HR7905 (Lo-16bits)
7907 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7908 |  |  |  | HR7907 (Lo-16bits)
7909 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7910 |  |  |  | HR7909 (Lo-16bits)
7911 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7912 |  |  |  | HR7911 (Lo-16bits)
7913 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7914 |  |  |  | HR7913 (Lo-16bits)
7915 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7916 |  |  |  | HR7915 (Lo-16bits)
7917 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7918 |  |  |  | HR7917 (Lo-16bits)
7919 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7920 |  |  |  | HR7919 (Lo-16bits)
7921 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7922 |  |  |  | HR7921 (Lo-16bits)
7923 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7924 |  |  |  | HR7923 (Lo-16bits)
7925 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7926 |  |  |  | HR7925 (Lo-16bits)
7927 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7928 |  |  |  | HR7927 (Lo-16bits)
7929 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7930 |  |  |  | HR7929 (Lo-16bits)
7931 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7932 |  |  |  | HR7931 (Lo-16bits)
7933 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7934 |  |  |  | HR7933 (Lo-16bits)
7935 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7936 |  |  |  | HR7935 (Lo-16bits)
7937 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7938 |  |  |  | HR7937 (Lo-16bits)
7939 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7940 |  |  |  | HR7939 (Lo-16bits)
7941 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7942 |  |  |  | HR7941 (Lo-16bits)
7943 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7944 |  |  |  | HR7943 (Lo-16bits)
7945 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7946 |  |  |  | HR7945 (Lo-16bits)
7947 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7948 |  |  |  | HR7947 (Lo-16bits)
7949 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7950 |  |  |  | HR7949 (Lo-16bits)
7951 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7952 |  |  |  | HR7951 (Lo-16bits)
7953 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7954 |  |  |  | HR7953 (Lo-16bits)
7955 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7956 |  |  |  | HR7955 (Lo-16bits)
7957 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7958 |  |  |  | HR7957 (Lo-16bits)
7959 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7960 |  |  |  | HR7959 (Lo-16bits)
7961 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7962 |  |  |  | HR7961 (Lo-16bits)
7963 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7964 |  |  |  | HR7963 (Lo-16bits)
7965 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7966 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7967 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7968 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7969 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7970 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7971 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7972 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7973 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7974 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7975 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7976 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7977 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7978 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7979 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7980 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7981 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7982 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7983 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7984 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7985 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7986 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7987 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7988 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7989 | UV3:U<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7990 | UV3:U<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7991 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7992 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7993 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7994 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7995 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7996 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7997 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7998 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7999 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8000 |  |  |  | HR7999 (Lo-16bits)
8001 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8002 |  |  |  | HR8001 (Lo-16bits)
8003 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8004 |  |  |  | HR8003 (Lo-16bits)
8005 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8006 |  |  |  | HR8005 (Lo-16bits)
8007 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8008 |  |  |  | HR8007 (Lo-16bits)
8009 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8010 |  |  |  | HR8009 (Lo-16bits)
8011 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8012 |  |  |  | HR8011 (Lo-16bits)
8013 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8014 |  |  |  | HR8013 (Lo-16bits)
8015 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8016 |  |  |  | HR8015 (Lo-16bits)
8017 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8018 |  |  |  | HR8017 (Lo-16bits)
8019 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8020 |  |  |  | HR8019 (Lo-16bits)
8021 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8022 |  |  |  | HR8021 (Lo-16bits)
8023 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8024 |  |  |  | HR8023 (Lo-16bits)
8025 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8026 |  |  |  | HR8025 (Lo-16bits)
8027 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8028 |  |  |  | HR8027 (Lo-16bits)
8029 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8030 |  |  |  | HR8029 (Lo-16bits)
8031 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8032 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8033 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8034 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8035 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8036 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8037 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8038 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8039 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8040 |  |  |  | HR8039 (Lo-16bits)
8041 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8042 |  |  |  | HR8041 (Lo-16bits)
8043 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8044 |  |  |  | HR8043 (Lo-16bits)
8045 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8046 |  |  |  | HR8045 (Lo-16bits)
8047 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8048 |  |  |  | HR8047 (Lo-16bits)
8049 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8050 |  |  |  | HR8049 (Lo-16bits)
8051 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8052 |  |  |  | HR8051 (Lo-16bits)
8053 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8054 |  |  |  | HR8053 (Lo-16bits)
8055 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8056 |  |  |  | HR8055 (Lo-16bits)
8057 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8058 |  |  |  | HR8057 (Lo-16bits)
8059 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8060 |  |  |  | HR8059 (Lo-16bits)
8061 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8062 |  |  |  | HR8061 (Lo-16bits)
8063 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8064 |  |  |  | HR8063 (Lo-16bits)
8065 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8066 |  |  |  | HR8065 (Lo-16bits)
8067 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8068 |  |  |  | HR8067 (Lo-16bits)
8069 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8070 |  |  |  | HR8069 (Lo-16bits)
8071 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8072 |  |  |  | HR8071 (Lo-16bits)
8073 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8074 |  |  |  | HR8073 (Lo-16bits)
8075 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8076 |  |  |  | HR8075 (Lo-16bits)
8077 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8078 |  |  |  | HR8077 (Lo-16bits)
8079 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8080 |  |  |  | HR8079 (Lo-16bits)
8081 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8082 |  |  |  | HR8081 (Lo-16bits)
8083 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8084 |  |  |  | HR8083 (Lo-16bits)
8085 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8086 |  |  |  | HR8085 (Lo-16bits)
8087 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8088 |  |  |  | HR8087 (Lo-16bits)
8089 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8090 |  |  |  | HR8089 (Lo-16bits)
8091 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8092 |  |  |  | HR8091 (Lo-16bits)
8093 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8094 |  |  |  | HR8093 (Lo-16bits)
8095 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8096 |  |  |  | HR8095 (Lo-16bits)
8097 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8098 |  |  |  | HR8097 (Lo-16bits)
8099 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8100 |  |  |  | HR8099 (Lo-16bits)
8101 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8102 |  |  |  | HR8101 (Lo-16bits)
8103 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8104 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8105 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8106 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8107 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8108 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8109 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8110 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8111 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8112 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8113 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8114 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8115 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8116 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8117 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8118 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8119 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8120 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8121 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8122 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8123 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8124 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8125 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8126 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8127 | UV4:U<<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
8128 | UV4:U<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
8129 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8130 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8131 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8132 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8133 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8134 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8135 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8136 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8137 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8138 |  |  |  | HR8137 (Lo-16bits)
8139 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8140 |  |  |  | HR8139 (Lo-16bits)
8141 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8142 |  |  |  | HR8141 (Lo-16bits)
8143 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8144 |  |  |  | HR8143 (Lo-16bits)
8145 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8146 |  |  |  | HR8145 (Lo-16bits)
8147 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8148 |  |  |  | HR8147 (Lo-16bits)
8149 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8150 |  |  |  | HR8149 (Lo-16bits)
8151 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8152 |  |  |  | HR8151 (Lo-16bits)
8153 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8154 |  |  |  | HR8153 (Lo-16bits)
8155 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8156 |  |  |  | HR8155 (Lo-16bits)
8157 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8158 |  |  |  | HR8157 (Lo-16bits)
8159 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8160 |  |  |  | HR8159 (Lo-16bits)
8161 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8162 |  |  |  | HR8161 (Lo-16bits)
8163 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8164 |  |  |  | HR8163 (Lo-16bits)
8165 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8166 |  |  |  | HR8165 (Lo-16bits)
8167 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8168 |  |  |  | HR8167 (Lo-16bits)
8169 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8170 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8171 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8172 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8173 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8174 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8175 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8176 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8177 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8178 |  |  |  | HR8177 (Lo-16bits)
8179 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8180 |  |  |  | HR8179 (Lo-16bits)
8181 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8182 |  |  |  | HR8181 (Lo-16bits)
8183 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8184 |  |  |  | HR8183 (Lo-16bits)
8185 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8186 |  |  |  | HR8185 (Lo-16bits)
8187 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8188 |  |  |  | HR8187 (Lo-16bits)
8189 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8190 |  |  |  | HR8189 (Lo-16bits)
8191 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8192 |  |  |  | HR8191 (Lo-16bits)
8193 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8194 |  |  |  | HR8193 (Lo-16bits)
8195 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8196 |  |  |  | HR8195 (Lo-16bits)
8197 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8198 |  |  |  | HR8197 (Lo-16bits)
8199 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8200 |  |  |  | HR8199 (Lo-16bits)
8201 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8202 |  |  |  | HR8201 (Lo-16bits)
8203 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8204 |  |  |  | HR8203 (Lo-16bits)
8205 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8206 |  |  |  | HR8205 (Lo-16bits)
8207 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8208 |  |  |  | HR8207 (Lo-16bits)
8209 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8210 |  |  |  | HR8209 (Lo-16bits)
8211 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8212 |  |  |  | HR8211 (Lo-16bits)
8213 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8214 |  |  |  | HR8213 (Lo-16bits)
8215 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8216 |  |  |  | HR8215 (Lo-16bits)
8217 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8218 |  |  |  | HR8217 (Lo-16bits)
8219 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8220 |  |  |  | HR8219 (Lo-16bits)
8221 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8222 |  |  |  | HR8221 (Lo-16bits)
8223 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8224 |  |  |  | HR8223 (Lo-16bits)
8225 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8226 |  |  |  | HR8225 (Lo-16bits)
8227 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8228 |  |  |  | HR8227 (Lo-16bits)
8229 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8230 |  |  |  | HR8229 (Lo-16bits)
8231 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8232 |  |  |  | HR8231 (Lo-16bits)
8233 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8234 |  |  |  | HR8233 (Lo-16bits)
8235 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8236 |  |  |  | HR8235 (Lo-16bits)
8237 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8238 |  |  |  | HR8237 (Lo-16bits)
8239 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8240 |  |  |  | HR8239 (Lo-16bits)
8241 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8242 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8243 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8244 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8245 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8246 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8247 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8248 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8249 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8250 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8251 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8252 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8253 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8254 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8255 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8256 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8257 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8258 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8259 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8260 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8261 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8262 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8263 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8264 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8265 | NOV1:U0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8266 | NOV1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8267 | NOV2:U0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8268 | NOV2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8269 | NOV3:U0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8270 | NOV3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8271 | NOV4:U0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8272 | NOV4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8273 | VUB1:U1/2 >/< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8274 | VUB1:U1/2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8275 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8276 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8277 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8278 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8279 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8280 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8281 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8282 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8283 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8284 |  |  |  | HR8283 (Lo-16bits)
8285 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8286 |  |  |  | HR8285 (Lo-16bits)
8287 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8288 |  |  |  | HR8287 (Lo-16bits)
8289 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8290 |  |  |  | HR8289 (Lo-16bits)
8291 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8292 |  |  |  | HR8291 (Lo-16bits)
8293 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8294 |  |  |  | HR8293 (Lo-16bits)
8295 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8296 |  |  |  | HR8295 (Lo-16bits)
8297 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8298 |  |  |  | HR8297 (Lo-16bits)
8299 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8300 |  |  |  | HR8299 (Lo-16bits)
8301 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8302 |  |  |  | HR8301 (Lo-16bits)
8303 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8304 |  |  |  | HR8303 (Lo-16bits)
8305 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8306 |  |  |  | HR8305 (Lo-16bits)
8307 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8308 |  |  |  | HR8307 (Lo-16bits)
8309 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8310 |  |  |  | HR8309 (Lo-16bits)
8311 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8312 |  |  |  | HR8311 (Lo-16bits)
8313 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8314 |  |  |  | HR8313 (Lo-16bits)
8315 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8316 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8317 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8318 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8319 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8320 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8321 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8322 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8323 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8324 |  |  |  | HR8323 (Lo-16bits)
8325 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8326 |  |  |  | HR8325 (Lo-16bits)
8327 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8328 |  |  |  | HR8327 (Lo-16bits)
8329 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8330 |  |  |  | HR8329 (Lo-16bits)
8331 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8332 |  |  |  | HR8331 (Lo-16bits)
8333 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8334 |  |  |  | HR8333 (Lo-16bits)
8335 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8336 |  |  |  | HR8335 (Lo-16bits)
8337 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8338 |  |  |  | HR8337 (Lo-16bits)
8339 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8340 |  |  |  | HR8339 (Lo-16bits)
8341 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8342 |  |  |  | HR8341 (Lo-16bits)
8343 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8344 |  |  |  | HR8343 (Lo-16bits)
8345 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8346 |  |  |  | HR8345 (Lo-16bits)
8347 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8348 |  |  |  | HR8347 (Lo-16bits)
8349 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8350 |  |  |  | HR8349 (Lo-16bits)
8351 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8352 |  |  |  | HR8351 (Lo-16bits)
8353 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8354 |  |  |  | HR8353 (Lo-16bits)
8355 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8356 |  |  |  | HR8355 (Lo-16bits)
8357 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8358 |  |  |  | HR8357 (Lo-16bits)
8359 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8360 |  |  |  | HR8359 (Lo-16bits)
8361 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8362 |  |  |  | HR8361 (Lo-16bits)
8363 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8364 |  |  |  | HR8363 (Lo-16bits)
8365 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8366 |  |  |  | HR8365 (Lo-16bits)
8367 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8368 |  |  |  | HR8367 (Lo-16bits)
8369 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8370 |  |  |  | HR8369 (Lo-16bits)
8371 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8372 |  |  |  | HR8371 (Lo-16bits)
8373 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8374 |  |  |  | HR8373 (Lo-16bits)
8375 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8376 |  |  |  | HR8375 (Lo-16bits)
8377 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8378 |  |  |  | HR8377 (Lo-16bits)
8379 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8380 |  |  |  | HR8379 (Lo-16bits)
8381 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8382 |  |  |  | HR8381 (Lo-16bits)
8383 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8384 |  |  |  | HR8383 (Lo-16bits)
8385 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8386 |  |  |  | HR8385 (Lo-16bits)
8387 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8388 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8389 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8390 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8391 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8392 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8393 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8394 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8395 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8396 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8397 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8398 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8399 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8400 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8401 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8402 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8403 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8404 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8405 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8406 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8407 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8408 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8409 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8410 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8411 | VUB2:U1/2 >>/<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8412 | VUB2:U1/2 >>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8413 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8414 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8415 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8416 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8417 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8418 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8419 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8420 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8421 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8422 |  |  |  | HR8421 (Lo-16bits)
8423 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8424 |  |  |  | HR8423 (Lo-16bits)
8425 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8426 |  |  |  | HR8425 (Lo-16bits)
8427 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8428 |  |  |  | HR8427 (Lo-16bits)
8429 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8430 |  |  |  | HR8429 (Lo-16bits)
8431 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8432 |  |  |  | HR8431 (Lo-16bits)
8433 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8434 |  |  |  | HR8433 (Lo-16bits)
8435 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8436 |  |  |  | HR8435 (Lo-16bits)
8437 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8438 |  |  |  | HR8437 (Lo-16bits)
8439 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8440 |  |  |  | HR8439 (Lo-16bits)
8441 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8442 |  |  |  | HR8441 (Lo-16bits)
8443 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8444 |  |  |  | HR8443 (Lo-16bits)
8445 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8446 |  |  |  | HR8445 (Lo-16bits)
8447 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8448 |  |  |  | HR8447 (Lo-16bits)
8449 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8450 |  |  |  | HR8449 (Lo-16bits)
8451 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8452 |  |  |  | HR8451 (Lo-16bits)
8453 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8454 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8455 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8456 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8457 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8458 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8459 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8460 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8461 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8462 |  |  |  | HR8461 (Lo-16bits)
8463 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8464 |  |  |  | HR8463 (Lo-16bits)
8465 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8466 |  |  |  | HR8465 (Lo-16bits)
8467 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8468 |  |  |  | HR8467 (Lo-16bits)
8469 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8470 |  |  |  | HR8469 (Lo-16bits)
8471 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8472 |  |  |  | HR8471 (Lo-16bits)
8473 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8474 |  |  |  | HR8473 (Lo-16bits)
8475 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8476 |  |  |  | HR8475 (Lo-16bits)
8477 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8478 |  |  |  | HR8477 (Lo-16bits)
8479 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8480 |  |  |  | HR8479 (Lo-16bits)
8481 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8482 |  |  |  | HR8481 (Lo-16bits)
8483 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8484 |  |  |  | HR8483 (Lo-16bits)
8485 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8486 |  |  |  | HR8485 (Lo-16bits)
8487 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8488 |  |  |  | HR8487 (Lo-16bits)
8489 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8490 |  |  |  | HR8489 (Lo-16bits)
8491 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8492 |  |  |  | HR8491 (Lo-16bits)
8493 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8494 |  |  |  | HR8493 (Lo-16bits)
8495 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8496 |  |  |  | HR8495 (Lo-16bits)
8497 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8498 |  |  |  | HR8497 (Lo-16bits)
8499 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8500 |  |  |  | HR8499 (Lo-16bits)
8501 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8502 |  |  |  | HR8501 (Lo-16bits)
8503 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8504 |  |  |  | HR8503 (Lo-16bits)
8505 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8506 |  |  |  | HR8505 (Lo-16bits)
8507 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8508 |  |  |  | HR8507 (Lo-16bits)
8509 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8510 |  |  |  | HR8509 (Lo-16bits)
8511 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8512 |  |  |  | HR8511 (Lo-16bits)
8513 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8514 |  |  |  | HR8513 (Lo-16bits)
8515 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8516 |  |  |  | HR8515 (Lo-16bits)
8517 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8518 |  |  |  | HR8517 (Lo-16bits)
8519 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8520 |  |  |  | HR8519 (Lo-16bits)
8521 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8522 |  |  |  | HR8521 (Lo-16bits)
8523 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8524 |  |  |  | HR8523 (Lo-16bits)
8525 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8526 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8527 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8528 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8529 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8530 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8531 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8532 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8533 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8534 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8535 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8536 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8537 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8538 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8539 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8540 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8541 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8542 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8543 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8544 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8545 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8546 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8547 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8548 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8549 | VUB3:U1/2 >>>/<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8550 | VUB3:U1/2 >>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8551 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8552 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8553 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8554 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8555 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8556 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8557 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8558 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8559 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8560 |  |  |  | HR8559 (Lo-16bits)
8561 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8562 |  |  |  | HR8561 (Lo-16bits)
8563 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8564 |  |  |  | HR8563 (Lo-16bits)
8565 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8566 |  |  |  | HR8565 (Lo-16bits)
8567 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8568 |  |  |  | HR8567 (Lo-16bits)
8569 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8570 |  |  |  | HR8569 (Lo-16bits)
8571 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8572 |  |  |  | HR8571 (Lo-16bits)
8573 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8574 |  |  |  | HR8573 (Lo-16bits)
8575 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8576 |  |  |  | HR8575 (Lo-16bits)
8577 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8578 |  |  |  | HR8577 (Lo-16bits)
8579 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8580 |  |  |  | HR8579 (Lo-16bits)
8581 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8582 |  |  |  | HR8581 (Lo-16bits)
8583 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8584 |  |  |  | HR8583 (Lo-16bits)
8585 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8586 |  |  |  | HR8585 (Lo-16bits)
8587 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8588 |  |  |  | HR8587 (Lo-16bits)
8589 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8590 |  |  |  | HR8589 (Lo-16bits)
8591 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8592 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8593 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8594 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8595 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8596 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8597 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8598 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8599 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8600 |  |  |  | HR8599 (Lo-16bits)
8601 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8602 |  |  |  | HR8601 (Lo-16bits)
8603 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8604 |  |  |  | HR8603 (Lo-16bits)
8605 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8606 |  |  |  | HR8605 (Lo-16bits)
8607 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8608 |  |  |  | HR8607 (Lo-16bits)
8609 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8610 |  |  |  | HR8609 (Lo-16bits)
8611 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8612 |  |  |  | HR8611 (Lo-16bits)
8613 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8614 |  |  |  | HR8613 (Lo-16bits)
8615 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8616 |  |  |  | HR8615 (Lo-16bits)
8617 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8618 |  |  |  | HR8617 (Lo-16bits)
8619 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8620 |  |  |  | HR8619 (Lo-16bits)
8621 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8622 |  |  |  | HR8621 (Lo-16bits)
8623 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8624 |  |  |  | HR8623 (Lo-16bits)
8625 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8626 |  |  |  | HR8625 (Lo-16bits)
8627 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8628 |  |  |  | HR8627 (Lo-16bits)
8629 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8630 |  |  |  | HR8629 (Lo-16bits)
8631 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8632 |  |  |  | HR8631 (Lo-16bits)
8633 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8634 |  |  |  | HR8633 (Lo-16bits)
8635 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8636 |  |  |  | HR8635 (Lo-16bits)
8637 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8638 |  |  |  | HR8637 (Lo-16bits)
8639 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8640 |  |  |  | HR8639 (Lo-16bits)
8641 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8642 |  |  |  | HR8641 (Lo-16bits)
8643 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8644 |  |  |  | HR8643 (Lo-16bits)
8645 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8646 |  |  |  | HR8645 (Lo-16bits)
8647 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8648 |  |  |  | HR8647 (Lo-16bits)
8649 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8650 |  |  |  | HR8649 (Lo-16bits)
8651 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8652 |  |  |  | HR8651 (Lo-16bits)
8653 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8654 |  |  |  | HR8653 (Lo-16bits)
8655 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8656 |  |  |  | HR8655 (Lo-16bits)
8657 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8658 |  |  |  | HR8657 (Lo-16bits)
8659 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8660 |  |  |  | HR8659 (Lo-16bits)
8661 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8662 |  |  |  | HR8661 (Lo-16bits)
8663 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8664 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8665 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8666 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8667 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8668 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8669 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8670 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8671 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8672 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8673 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8674 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8675 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8676 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8677 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8678 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8679 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8680 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8681 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8682 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8683 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8684 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8685 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8686 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8687 | VUB4:U1/2 >>>>/<<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8688 | VUB4:U1/2 >>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8689 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8690 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8691 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8692 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8693 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8694 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8695 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8696 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8697 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8698 |  |  |  | HR8697 (Lo-16bits)
8699 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8700 |  |  |  | HR8699 (Lo-16bits)
8701 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8702 |  |  |  | HR8701 (Lo-16bits)
8703 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8704 |  |  |  | HR8703 (Lo-16bits)
8705 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8706 |  |  |  | HR8705 (Lo-16bits)
8707 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8708 |  |  |  | HR8707 (Lo-16bits)
8709 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8710 |  |  |  | HR8709 (Lo-16bits)
8711 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8712 |  |  |  | HR8711 (Lo-16bits)
8713 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8714 |  |  |  | HR8713 (Lo-16bits)
8715 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8716 |  |  |  | HR8715 (Lo-16bits)
8717 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8718 |  |  |  | HR8717 (Lo-16bits)
8719 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8720 |  |  |  | HR8719 (Lo-16bits)
8721 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8722 |  |  |  | HR8721 (Lo-16bits)
8723 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8724 |  |  |  | HR8723 (Lo-16bits)
8725 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8726 |  |  |  | HR8725 (Lo-16bits)
8727 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8728 |  |  |  | HR8727 (Lo-16bits)
8729 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8730 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8731 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8732 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8733 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8734 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8735 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8736 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8737 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8738 |  |  |  | HR8737 (Lo-16bits)
8739 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8740 |  |  |  | HR8739 (Lo-16bits)
8741 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8742 |  |  |  | HR8741 (Lo-16bits)
8743 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8744 |  |  |  | HR8743 (Lo-16bits)
8745 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8746 |  |  |  | HR8745 (Lo-16bits)
8747 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8748 |  |  |  | HR8747 (Lo-16bits)
8749 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8750 |  |  |  | HR8749 (Lo-16bits)
8751 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8752 |  |  |  | HR8751 (Lo-16bits)
8753 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8754 |  |  |  | HR8753 (Lo-16bits)
8755 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8756 |  |  |  | HR8755 (Lo-16bits)
8757 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8758 |  |  |  | HR8757 (Lo-16bits)
8759 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8760 |  |  |  | HR8759 (Lo-16bits)
8761 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8762 |  |  |  | HR8761 (Lo-16bits)
8763 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8764 |  |  |  | HR8763 (Lo-16bits)
8765 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8766 |  |  |  | HR8765 (Lo-16bits)
8767 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8768 |  |  |  | HR8767 (Lo-16bits)
8769 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8770 |  |  |  | HR8769 (Lo-16bits)
8771 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8772 |  |  |  | HR8771 (Lo-16bits)
8773 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8774 |  |  |  | HR8773 (Lo-16bits)
8775 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8776 |  |  |  | HR8775 (Lo-16bits)
8777 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8778 |  |  |  | HR8777 (Lo-16bits)
8779 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8780 |  |  |  | HR8779 (Lo-16bits)
8781 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8782 |  |  |  | HR8781 (Lo-16bits)
8783 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8784 |  |  |  | HR8783 (Lo-16bits)
8785 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8786 |  |  |  | HR8785 (Lo-16bits)
8787 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8788 |  |  |  | HR8787 (Lo-16bits)
8789 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8790 |  |  |  | HR8789 (Lo-16bits)
8791 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8792 |  |  |  | HR8791 (Lo-16bits)
8793 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8794 |  |  |  | HR8793 (Lo-16bits)
8795 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8796 |  |  |  | HR8795 (Lo-16bits)
8797 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8798 |  |  |  | HR8797 (Lo-16bits)
8799 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8800 |  |  |  | HR8799 (Lo-16bits)
8801 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8802 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8803 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8804 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8805 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8806 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8807 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8808 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8809 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8810 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8811 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8812 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8813 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8814 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8815 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8816 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8817 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8818 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8819 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8820 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8821 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8822 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8823 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8824 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8825 | PGS1:PS1 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8826 | PGS1:PS2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8827 | PGS1:PS3 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8828 | PGS1:PS4 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8829 | PGS1:PS5 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8830 | PGS1:PS6 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8831 | PGS1:PS7 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8832 | PGS1:PS8 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8833 | PGS1:PS9 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8834 | PGS1:PS10 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8835 | FRQC1:f> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8836 | FRQC1:f>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8837 | FRQC1:f>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8838 | FRQC1:f>>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8839 | FRQC1:f< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8840 | FRQC1:f<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8841 | FRQC1:f<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8842 | FRQC1:f<<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8843 | FRQV1:f</> [81O/81U] mode | R(W) | 1 | 0=Disabled;1=Activated
8844 | FRQV1:f> Enable | R(W) | 1 | 0=No;1=Yes
8845 | FRQV1:f> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8846 | FRQV1:f>> Enable | R(W) | 1 | 0=No;1=Yes
8847 | FRQV1:f>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8848 | FRQV1:f>>> Enable | R(W) | 1 | 0=No;1=Yes
8849 | FRQV1:f>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8850 | FRQV1:f>>>> Enable | R(W) | 1 | 0=No;1=Yes
8851 | FRQV1:f>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8852 | FRQV1:f< Enable | R(W) | 1 | 0=No;1=Yes
8853 | FRQV1:f< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8854 | FRQV1:f<< Enable | R(W) | 1 | 0=No;1=Yes
8855 | FRQV1:f<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8856 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8857 | FRQV1:f<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8858 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8859 | FRQV1:f<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8860 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8861 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8862 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8863 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8864 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8865 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8866 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8867 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8868 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8869 |  |  |  | HR8868 (Lo-16bits)
8870 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8871 |  |  |  | HR8870 (Lo-16bits)
8872 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8873 |  |  |  | HR8872 (Lo-16bits)
8874 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8875 |  |  |  | HR8874 (Lo-16bits)
8876 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8877 |  |  |  | HR8876 (Lo-16bits)
8878 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8879 |  |  |  | HR8878 (Lo-16bits)
8880 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8881 |  |  |  | HR8880 (Lo-16bits)
8882 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8883 |  |  |  | HR8882 (Lo-16bits)
8884 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8885 |  |  |  | HR8884 (Lo-16bits)
8886 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8887 |  |  |  | HR8886 (Lo-16bits)
8888 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8889 |  |  |  | HR8888 (Lo-16bits)
8890 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8891 |  |  |  | HR8890 (Lo-16bits)
8892 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8893 |  |  |  | HR8892 (Lo-16bits)
8894 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8895 |  |  |  | HR8894 (Lo-16bits)
8896 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8897 |  |  |  | HR8896 (Lo-16bits)
8898 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8899 |  |  |  | HR8898 (Lo-16bits)
8900 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8901 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8902 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8903 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8904 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8905 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8906 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8907 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8908 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8909 |  |  |  | HR8908 (Lo-16bits)
8910 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8911 |  |  |  | HR8910 (Lo-16bits)
8912 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8913 |  |  |  | HR8912 (Lo-16bits)
8914 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8915 |  |  |  | HR8914 (Lo-16bits)
8916 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8917 |  |  |  | HR8916 (Lo-16bits)
8918 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8919 |  |  |  | HR8918 (Lo-16bits)
8920 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8921 |  |  |  | HR8920 (Lo-16bits)
8922 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8923 |  |  |  | HR8922 (Lo-16bits)
8924 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8925 |  |  |  | HR8924 (Lo-16bits)
8926 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8927 |  |  |  | HR8926 (Lo-16bits)
8928 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8929 |  |  |  | HR8928 (Lo-16bits)
8930 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8931 |  |  |  | HR8930 (Lo-16bits)
8932 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8933 |  |  |  | HR8932 (Lo-16bits)
8934 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8935 |  |  |  | HR8934 (Lo-16bits)
8936 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8937 |  |  |  | HR8936 (Lo-16bits)
8938 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8939 |  |  |  | HR8938 (Lo-16bits)
8940 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8941 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8942 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8943 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8944 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8945 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8946 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8947 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8948 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8949 |  |  |  | HR8948 (Lo-16bits)
8950 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8951 |  |  |  | HR8950 (Lo-16bits)
8952 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8953 |  |  |  | HR8952 (Lo-16bits)
8954 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8955 |  |  |  | HR8954 (Lo-16bits)
8956 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8957 |  |  |  | HR8956 (Lo-16bits)
8958 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8959 |  |  |  | HR8958 (Lo-16bits)
8960 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8961 |  |  |  | HR8960 (Lo-16bits)
8962 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8963 |  |  |  | HR8962 (Lo-16bits)
8964 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8965 |  |  |  | HR8964 (Lo-16bits)
8966 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8967 |  |  |  | HR8966 (Lo-16bits)
8968 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8969 |  |  |  | HR8968 (Lo-16bits)
8970 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8971 |  |  |  | HR8970 (Lo-16bits)
8972 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8973 |  |  |  | HR8972 (Lo-16bits)
8974 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8975 |  |  |  | HR8974 (Lo-16bits)
8976 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8977 |  |  |  | HR8976 (Lo-16bits)
8978 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8979 |  |  |  | HR8978 (Lo-16bits)
8980 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8981 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8982 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8983 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8984 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8985 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8986 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8987 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8988 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8989 |  |  |  | HR8988 (Lo-16bits)
8990 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8991 |  |  |  | HR8990 (Lo-16bits)
8992 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8993 |  |  |  | HR8992 (Lo-16bits)
8994 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8995 |  |  |  | HR8994 (Lo-16bits)
8996 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8997 |  |  |  | HR8996 (Lo-16bits)
8998 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8999 |  |  |  | HR8998 (Lo-16bits)
9000 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9001 |  |  |  | HR9000 (Lo-16bits)
9002 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9003 |  |  |  | HR9002 (Lo-16bits)
9004 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9005 |  |  |  | HR9004 (Lo-16bits)
9006 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9007 |  |  |  | HR9006 (Lo-16bits)
9008 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9009 |  |  |  | HR9008 (Lo-16bits)
9010 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9011 |  |  |  | HR9010 (Lo-16bits)
9012 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9013 |  |  |  | HR9012 (Lo-16bits)
9014 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9015 |  |  |  | HR9014 (Lo-16bits)
9016 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9017 |  |  |  | HR9016 (Lo-16bits)
9018 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9019 |  |  |  | HR9018 (Lo-16bits)
9020 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9021 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9022 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9023 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9024 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9025 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9026 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9027 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9028 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9029 |  |  |  | HR9028 (Lo-16bits)
9030 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9031 |  |  |  | HR9030 (Lo-16bits)
9032 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9033 |  |  |  | HR9032 (Lo-16bits)
9034 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9035 |  |  |  | HR9034 (Lo-16bits)
9036 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9037 |  |  |  | HR9036 (Lo-16bits)
9038 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9039 |  |  |  | HR9038 (Lo-16bits)
9040 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9041 |  |  |  | HR9040 (Lo-16bits)
9042 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9043 |  |  |  | HR9042 (Lo-16bits)
9044 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9045 |  |  |  | HR9044 (Lo-16bits)
9046 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9047 |  |  |  | HR9046 (Lo-16bits)
9048 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9049 |  |  |  | HR9048 (Lo-16bits)
9050 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9051 |  |  |  | HR9050 (Lo-16bits)
9052 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9053 |  |  |  | HR9052 (Lo-16bits)
9054 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9055 |  |  |  | HR9054 (Lo-16bits)
9056 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9057 |  |  |  | HR9056 (Lo-16bits)
9058 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9059 |  |  |  | HR9058 (Lo-16bits)
9060 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9061 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9062 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9063 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9064 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9065 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9066 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9067 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9068 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9069 |  |  |  | HR9068 (Lo-16bits)
9070 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9071 |  |  |  | HR9070 (Lo-16bits)
9072 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9073 |  |  |  | HR9072 (Lo-16bits)
9074 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9075 |  |  |  | HR9074 (Lo-16bits)
9076 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9077 |  |  |  | HR9076 (Lo-16bits)
9078 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9079 |  |  |  | HR9078 (Lo-16bits)
9080 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9081 |  |  |  | HR9080 (Lo-16bits)
9082 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9083 |  |  |  | HR9082 (Lo-16bits)
9084 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9085 |  |  |  | HR9084 (Lo-16bits)
9086 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9087 |  |  |  | HR9086 (Lo-16bits)
9088 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9089 |  |  |  | HR9088 (Lo-16bits)
9090 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9091 |  |  |  | HR9090 (Lo-16bits)
9092 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9093 |  |  |  | HR9092 (Lo-16bits)
9094 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9095 |  |  |  | HR9094 (Lo-16bits)
9096 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9097 |  |  |  | HR9096 (Lo-16bits)
9098 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9099 |  |  |  | HR9098 (Lo-16bits)
9100 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9101 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9102 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9103 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9104 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9105 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9106 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9107 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9108 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9109 |  |  |  | HR9108 (Lo-16bits)
9110 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9111 |  |  |  | HR9110 (Lo-16bits)
9112 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9113 |  |  |  | HR9112 (Lo-16bits)
9114 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9115 |  |  |  | HR9114 (Lo-16bits)
9116 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9117 |  |  |  | HR9116 (Lo-16bits)
9118 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9119 |  |  |  | HR9118 (Lo-16bits)
9120 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9121 |  |  |  | HR9120 (Lo-16bits)
9122 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9123 |  |  |  | HR9122 (Lo-16bits)
9124 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9125 |  |  |  | HR9124 (Lo-16bits)
9126 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9127 |  |  |  | HR9126 (Lo-16bits)
9128 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9129 |  |  |  | HR9128 (Lo-16bits)
9130 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9131 |  |  |  | HR9130 (Lo-16bits)
9132 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9133 |  |  |  | HR9132 (Lo-16bits)
9134 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9135 |  |  |  | HR9134 (Lo-16bits)
9136 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9137 |  |  |  | HR9136 (Lo-16bits)
9138 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9139 |  |  |  | HR9138 (Lo-16bits)
9140 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9141 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9142 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9143 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9144 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9145 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9146 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9147 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9148 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9149 |  |  |  | HR9148 (Lo-16bits)
9150 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9151 |  |  |  | HR9150 (Lo-16bits)
9152 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9153 |  |  |  | HR9152 (Lo-16bits)
9154 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9155 |  |  |  | HR9154 (Lo-16bits)
9156 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9157 |  |  |  | HR9156 (Lo-16bits)
9158 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9159 |  |  |  | HR9158 (Lo-16bits)
9160 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9161 |  |  |  | HR9160 (Lo-16bits)
9162 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9163 |  |  |  | HR9162 (Lo-16bits)
9164 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9165 |  |  |  | HR9164 (Lo-16bits)
9166 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9167 |  |  |  | HR9166 (Lo-16bits)
9168 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9169 |  |  |  | HR9168 (Lo-16bits)
9170 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9171 |  |  |  | HR9170 (Lo-16bits)
9172 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9173 |  |  |  | HR9172 (Lo-16bits)
9174 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9175 |  |  |  | HR9174 (Lo-16bits)
9176 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9177 |  |  |  | HR9176 (Lo-16bits)
9178 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9179 |  |  |  | HR9178 (Lo-16bits)
9180 | DFT1:df/dt >/< (1) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9181 | DFT1:df/dt >/< (2) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9182 | DFT1:df/dt >/< (3) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9183 | DFT1:df/dt >/< (4) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9184 | DFT1:df/dt >/< (5) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9185 | DFT1:df/dt >/< (6) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9186 | DFT1:df/dt >/< (7) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9187 | DFT1:df/dt >/< (8) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9188 | RHC1:Counter is now | R | 1 | 0=Idle;1=Counting
9189 | RHC1:Running hours | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9190 |  |  |  | HR9189 (Lo-16bits)
9191 | RHC1:Start count | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9192 |  |  |  | HR9191 (Lo-16bits)
9193 | GST1:Generator is now | R | 1 | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
9194 | PWR1:PQS>/< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9195 | PWR2:PQS>>/<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9196 | PWR3:PQS>>>/<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9197 | PWR4:PQS>>>>/<<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9198 | OPW1:P> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9199 | UPW1:P< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9200 | RPW1:Prev> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9201 | SEF1:U03rd< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9202 | SEF1:U03rd< Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
9203 | UEX1:Q< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9204 | UIM1:Z< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9205 | UIM2:Z<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9206 | VOC1:Iv> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9207 | VOC1:Voltage measurement | R | 1 | 0=Invalid U1 not avail.;1=Ok
9208 | VHZ1:V/Hz(1) > condition | R | 1 | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
9209 | VHZ1:V/Hz(2) > condition | R | 1 | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
9210 | UPF1:PF< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
9211 | RTDIN:S1 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9212 |  |  |  | HR9211 (Lo-16bits)
9213 | RTDIN:S1 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9214 |  |  |  | HR9213 (Lo-16bits)
9215 | RTDIN:S1 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9216 | RTDIN:S1 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9217 |  |  |  | HR9216 (Lo-16bits)
9218 | RTDIN:S2 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9219 |  |  |  | HR9218 (Lo-16bits)
9220 | RTDIN:S2 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9221 |  |  |  | HR9220 (Lo-16bits)
9222 | RTDIN:S2 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9223 | RTDIN:S2 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9224 |  |  |  | HR9223 (Lo-16bits)
9225 | RTDIN:S3 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9226 |  |  |  | HR9225 (Lo-16bits)
9227 | RTDIN:S3 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9228 |  |  |  | HR9227 (Lo-16bits)
9229 | RTDIN:S3 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9230 | RTDIN:S3 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9231 |  |  |  | HR9230 (Lo-16bits)
9232 | RTDIN:S4 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9233 |  |  |  | HR9232 (Lo-16bits)
9234 | RTDIN:S4 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9235 |  |  |  | HR9234 (Lo-16bits)
9236 | RTDIN:S4 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9237 | RTDIN:S4 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9238 |  |  |  | HR9237 (Lo-16bits)
9239 | RTDIN:S5 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9240 |  |  |  | HR9239 (Lo-16bits)
9241 | RTDIN:S5 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9242 |  |  |  | HR9241 (Lo-16bits)
9243 | RTDIN:S5 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9244 | RTDIN:S5 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9245 |  |  |  | HR9244 (Lo-16bits)
9246 | RTDIN:S6 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9247 |  |  |  | HR9246 (Lo-16bits)
9248 | RTDIN:S6 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9249 |  |  |  | HR9248 (Lo-16bits)
9250 | RTDIN:S6 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9251 | RTDIN:S6 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9252 |  |  |  | HR9251 (Lo-16bits)
9253 | RTDIN:S7 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9254 |  |  |  | HR9253 (Lo-16bits)
9255 | RTDIN:S7 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9256 |  |  |  | HR9255 (Lo-16bits)
9257 | RTDIN:S7 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9258 |  |  |  | HR9257 (Lo-16bits)
9259 | RTDIN:S7 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9260 | RTDIN:S7 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9261 |  |  |  | HR9260 (Lo-16bits)
9262 | RTDIN:S8 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9263 |  |  |  | HR9262 (Lo-16bits)
9264 | RTDIN:S8 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9265 |  |  |  | HR9264 (Lo-16bits)
9266 | RTDIN:S8 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9267 |  |  |  | HR9266 (Lo-16bits)
9268 | RTDIN:S8 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9269 | RTDIN:S8 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9270 |  |  |  | HR9269 (Lo-16bits)
9271 | RTDIN:S9 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9272 |  |  |  | HR9271 (Lo-16bits)
9273 | RTDIN:S9 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9274 |  |  |  | HR9273 (Lo-16bits)
9275 | RTDIN:S9 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9276 | RTDIN:S9 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9277 |  |  |  | HR9276 (Lo-16bits)
9278 | RTDIN:S10 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9279 |  |  |  | HR9278 (Lo-16bits)
9280 | RTDIN:S10 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9281 |  |  |  | HR9280 (Lo-16bits)
9282 | RTDIN:S10 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9283 | RTDIN:S10 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9284 |  |  |  | HR9283 (Lo-16bits)
9285 | RTDIN:S11 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9286 |  |  |  | HR9285 (Lo-16bits)
9287 | RTDIN:S11 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9288 |  |  |  | HR9287 (Lo-16bits)
9289 | RTDIN:S11 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9290 | RTDIN:S11 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9291 |  |  |  | HR9290 (Lo-16bits)
9292 | RTDIN:S12 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9293 |  |  |  | HR9292 (Lo-16bits)
9294 | RTDIN:S12 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9295 |  |  |  | HR9294 (Lo-16bits)
9296 | RTDIN:S12 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9297 | RTDIN:S12 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9298 |  |  |  | HR9297 (Lo-16bits)
9299 | RTDIN:S13 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9300 |  |  |  | HR9299 (Lo-16bits)
9301 | RTDIN:S13 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9302 |  |  |  | HR9301 (Lo-16bits)
9303 | RTDIN:S13 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9304 | RTDIN:S13 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9305 |  |  |  | HR9304 (Lo-16bits)
9306 | RTDIN:S14 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9307 |  |  |  | HR9306 (Lo-16bits)
9308 | RTDIN:S14 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9309 |  |  |  | HR9308 (Lo-16bits)
9310 | RTDIN:S14 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9311 | RTDIN:S14 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9312 |  |  |  | HR9311 (Lo-16bits)
9313 | RTDIN:S15 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9314 |  |  |  | HR9313 (Lo-16bits)
9315 | RTDIN:S15 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9316 |  |  |  | HR9315 (Lo-16bits)
9317 | RTDIN:S15 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9318 |  |  |  | HR9317 (Lo-16bits)
9319 | RTDIN:S15 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9320 | RTDIN:S15 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9321 |  |  |  | HR9320 (Lo-16bits)
9322 | RTDIN:S16 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9323 |  |  |  | HR9322 (Lo-16bits)
9324 | RTDIN:S16 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9325 |  |  |  | HR9324 (Lo-16bits)
9326 | RTDIN:S16 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9327 |  |  |  | HR9326 (Lo-16bits)
9328 | RTDIN:S16 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9329 | RTDIN:S16 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9330 |  |  |  | HR9329 (Lo-16bits)
9331 | RTD1:S1 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9332 |  |  |  | HR9331 (Lo-16bits)
9333 | RTD1:S2 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9334 |  |  |  | HR9333 (Lo-16bits)
9335 | RTD1:S3 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9336 |  |  |  | HR9335 (Lo-16bits)
9337 | RTD1:S4 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9338 |  |  |  | HR9337 (Lo-16bits)
9339 | RTD1:S5 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9340 |  |  |  | HR9339 (Lo-16bits)
9341 | RTD1:S6 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9342 |  |  |  | HR9341 (Lo-16bits)
9343 | RTD1:S7 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9344 |  |  |  | HR9343 (Lo-16bits)
9345 | RTD1:S8 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9346 |  |  |  | HR9345 (Lo-16bits)
9347 | RTD1:S9 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9348 |  |  |  | HR9347 (Lo-16bits)
9349 | RTD1:S10 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9350 |  |  |  | HR9349 (Lo-16bits)
9351 | RTD1:S11 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9352 |  |  |  | HR9351 (Lo-16bits)
9353 | RTD1:S12 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9354 |  |  |  | HR9353 (Lo-16bits)
9355 | RTD1:S13 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9356 |  |  |  | HR9355 (Lo-16bits)
9357 | RTD1:S14 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9358 |  |  |  | HR9357 (Lo-16bits)
9359 | RTD1:S15 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9360 |  |  |  | HR9359 (Lo-16bits)
9361 | RTD1:S16 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9362 |  |  |  | HR9361 (Lo-16bits)
9363 | RTD1:S1 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9364 |  |  |  | HR9363 (Lo-16bits)
9365 | RTD1:S1 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9366 |  |  |  | HR9365 (Lo-16bits)
9367 | RTD1:S1 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9368 |  |  |  | HR9367 (Lo-16bits)
9369 | RTD1:S2 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9370 |  |  |  | HR9369 (Lo-16bits)
9371 | RTD1:S2 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9372 |  |  |  | HR9371 (Lo-16bits)
9373 | RTD1:S2 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9374 |  |  |  | HR9373 (Lo-16bits)
9375 | RTD1:S3 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9376 |  |  |  | HR9375 (Lo-16bits)
9377 | RTD1:S3 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9378 |  |  |  | HR9377 (Lo-16bits)
9379 | RTD1:S3 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9380 |  |  |  | HR9379 (Lo-16bits)
9381 | RTD1:S4 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9382 |  |  |  | HR9381 (Lo-16bits)
9383 | RTD1:S4 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9384 |  |  |  | HR9383 (Lo-16bits)
9385 | RTD1:S4 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9386 |  |  |  | HR9385 (Lo-16bits)
9387 | RTD1:S5 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9388 |  |  |  | HR9387 (Lo-16bits)
9389 | RTD1:S5 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9390 |  |  |  | HR9389 (Lo-16bits)
9391 | RTD1:S5 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9392 |  |  |  | HR9391 (Lo-16bits)
9393 | RTD1:S6 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9394 |  |  |  | HR9393 (Lo-16bits)
9395 | RTD1:S6 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9396 |  |  |  | HR9395 (Lo-16bits)
9397 | RTD1:S6 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9398 |  |  |  | HR9397 (Lo-16bits)
9399 | RTD1:S7 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9400 |  |  |  | HR9399 (Lo-16bits)
9401 | RTD1:S7 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9402 |  |  |  | HR9401 (Lo-16bits)
9403 | RTD1:S7 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9404 |  |  |  | HR9403 (Lo-16bits)
9405 | RTD1:S8 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9406 |  |  |  | HR9405 (Lo-16bits)
9407 | RTD1:S8 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9408 |  |  |  | HR9407 (Lo-16bits)
9409 | RTD1:S8 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9410 |  |  |  | HR9409 (Lo-16bits)
9411 | RTD1:S9 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9412 |  |  |  | HR9411 (Lo-16bits)
9413 | RTD1:S9 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9414 |  |  |  | HR9413 (Lo-16bits)
9415 | RTD1:S9 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9416 |  |  |  | HR9415 (Lo-16bits)
9417 | RTD1:S10 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9418 |  |  |  | HR9417 (Lo-16bits)
9419 | RTD1:S10 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9420 |  |  |  | HR9419 (Lo-16bits)
9421 | RTD1:S10 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9422 |  |  |  | HR9421 (Lo-16bits)
9423 | RTD1:S11 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9424 |  |  |  | HR9423 (Lo-16bits)
9425 | RTD1:S11 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9426 |  |  |  | HR9425 (Lo-16bits)
9427 | RTD1:S11 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9428 |  |  |  | HR9427 (Lo-16bits)
9429 | RTD1:S12 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9430 |  |  |  | HR9429 (Lo-16bits)
9431 | RTD1:S12 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9432 |  |  |  | HR9431 (Lo-16bits)
9433 | RTD1:S12 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9434 |  |  |  | HR9433 (Lo-16bits)
9435 | RTD1:S13 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9436 |  |  |  | HR9435 (Lo-16bits)
9437 | RTD1:S13 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9438 |  |  |  | HR9437 (Lo-16bits)
9439 | RTD1:S13 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9440 |  |  |  | HR9439 (Lo-16bits)
9441 | RTD1:S14 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9442 |  |  |  | HR9441 (Lo-16bits)
9443 | RTD1:S14 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9444 |  |  |  | HR9443 (Lo-16bits)
9445 | RTD1:S14 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9446 |  |  |  | HR9445 (Lo-16bits)
9447 | RTD1:S15 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9448 |  |  |  | HR9447 (Lo-16bits)
9449 | RTD1:S15 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9450 |  |  |  | HR9449 (Lo-16bits)
9451 | RTD1:S15 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9452 |  |  |  | HR9451 (Lo-16bits)
9453 | RTD1:S16 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9454 |  |  |  | HR9453 (Lo-16bits)
9455 | RTD1:S16 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9456 |  |  |  | HR9455 (Lo-16bits)
9457 | RTD1:S16 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9458 |  |  |  | HR9457 (Lo-16bits)
9459 | ARC1:I/I0 Arc> condition | R | 1 | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
9460 | ARC1:I/I0 Arc> S1 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9461 |  |  |  | HR9460 (Lo-16bits)
9462 | ARC1:I/I0 Arc> S2 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9463 |  |  |  | HR9462 (Lo-16bits)
9464 | ARC1:I/I0 Arc> S3 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9465 |  |  |  | HR9464 (Lo-16bits)
9466 | ARC1:I/I0 Arc> S4 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9467 |  |  |  | HR9466 (Lo-16bits)
9468 | ARC1:I/I0 Arc> IO unit fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9469 |  |  |  | HR9468 (Lo-16bits)
9470 | CTS1:CTS1 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9471 | CTS2:CTS2 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9472 | VTS1:VTS condition | R | 1 | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
9473 | VTS1:Bus voltages | R | 1 | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
9474 | FLX1:Fault locator condition | R | 1 | 0=Idle;1=Triggered;2=Calc ready
9475 | THD1:THD condition | R | 1 | 0=Normal;1=Start;2=Alarm;3=Blocked
9476 | CBW1:CBW condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On
9477 | NJK1:U0> RECL condition | R | 1 | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
9478 | SOF1:SOTF condition | R | 1 | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
9479 | PCS1:PCS1 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9480 |  |  |  | HR9479 (Lo-16bits)
9481 | PCS2:PCS2 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9482 |  |  |  | HR9481 (Lo-16bits)
9483 | PCS3:PCS3 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9484 |  |  |  | HR9483 (Lo-16bits)
9485 | PCS4:PCS4 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9486 |  |  |  | HR9485 (Lo-16bits)
9487 | PCS5:PCS5 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9488 |  |  |  | HR9487 (Lo-16bits)
9489 | SYN1:SYN1 Condition | R | 2 | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok (Hi-16bits)
9490 |  |  |  | HR9489 (Lo-16bits)
9491 | SYN1:SYN2 Condition | R | 2 | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok (Hi-16bits)
9492 |  |  |  | HR9491 (Lo-16bits)
9493 | SYN1:SYN3 Condition | R | 2 | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok (Hi-16bits)
9494 |  |  |  | HR9493 (Lo-16bits)
9495 | SYN1:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9496 |  |  |  | HR9495 (Lo-16bits)
9497 | SYN1:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9498 |  |  |  | HR9497 (Lo-16bits)
9499 | SYN1:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9500 |  |  |  | HR9499 (Lo-16bits)
9501 | SYN1:SYN2 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9502 |  |  |  | HR9501 (Lo-16bits)
9503 | SYN1:SYN2 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9504 |  |  |  | HR9503 (Lo-16bits)
9505 | SYN1:SYN2 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9506 |  |  |  | HR9505 (Lo-16bits)
9507 | SYN1:SYN3 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9508 |  |  |  | HR9507 (Lo-16bits)
9509 | SYN1:SYN3 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9510 |  |  |  | HR9509 (Lo-16bits)
9511 | SYN1:SYN3 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9512 |  |  |  | HR9511 (Lo-16bits)
9513 | VJP1:<DELTA><alpha> > condition | R | 1 | 0=Normal;1=Blocked;2=Trip;3=Alarm
9514 | VJP1:Voltage meas selected | R | 1 | 0=Selection Ok;1=Selection not available
9515 | OBJ1:Object1 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9516 | OBJ2:Object2 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9517 | OBJ3:Object3 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9518 | OBJ4:Object4 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9519 | OBJ5:Object5 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9520 | OBJ6:Object6 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9521 | OBJ7:Object7 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9522 | OBJ8:Object8 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9523 | OBJ9:Object9 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9524 | OBJ10:Object10 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9525 | CIN1:Ind.1 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9526 | CIN2:Ind.2 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9527 | CIN3:Ind.3 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9528 | CIN4:Ind.4 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9529 | CIN5:Ind.5 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9530 | AR1:Auto-recloser [79] Mode | RW | 1 | 0=Disabled;1=Activated
9531 | AR1:AR Status | R | 2 | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear (Hi-16bits)
9532 |  |  |  | HR9531 (Lo-16bits)
9533 | AR1:Timer active | R | 1 | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
9534 | VRG1:Vreg settings condition | R | 2 | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok (Hi-16bits)
9535 |  |  |  | HR9534 (Lo-16bits)
9536 | VRG1:Vreg condition | R | 2 | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on (Hi-16bits)
9537 |  |  |  | HR9536 (Lo-16bits)
9538 | VRG1:Vreg timer active | R | 1 | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
9539 | VRG1:Voltage now | R | 2 | FLOAT [0...140] (Hi-16bits)
9540 |  |  |  | HR9539 (Lo-16bits)
9541 | VRG1:Voltage difference to set target | R | 2 | FLOAT [-140...140] (Hi-16bits)
9542 |  |  |  | HR9541 (Lo-16bits)
9543 | VRG1:Voltage meas condition | R | 1 | 0=Not configured;1=System U12;2=System U23;3=System U31;4=VT4 meas U12;5=VT4 meas U23;6=VT4 meas U31;7=VT4 conf not ok
9544 | VRG1:Tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
9545 |  |  |  | HR9544 (Lo-16bits)
9546 | VRG1:Absolute tap location | R | 2 | FLOAT [0...50] (Hi-16bits)
9547 |  |  |  | HR9546 (Lo-16bits)
9548 | VRG1:Control mode | R | 1 | 0=Auto;1=Manual (loc&rem)
9549 | VRG1:Remote tap control input | RW | 1 | 0=Stop;1=Lower;2=Higher
9550 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9551 |  |  |  | HR9550 (Lo-16bits)
9552 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9553 |  |  |  | HR9552 (Lo-16bits)
9554 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9555 |  |  |  | HR9554 (Lo-16bits)
9556 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9557 |  |  |  | HR9556 (Lo-16bits)
9558 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9559 |  |  |  | HR9558 (Lo-16bits)
9560 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9561 |  |  |  | HR9560 (Lo-16bits)
9562 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9563 |  |  |  | HR9562 (Lo-16bits)
9564 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9565 |  |  |  | HR9564 (Lo-16bits)
9566 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9567 |  |  |  | HR9566 (Lo-16bits)
9568 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9569 |  |  |  | HR9568 (Lo-16bits)
9570 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9571 |  |  |  | HR9570 (Lo-16bits)
9572 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9573 |  |  |  | HR9572 (Lo-16bits)
9574 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9575 |  |  |  | HR9574 (Lo-16bits)
9576 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9577 |  |  |  | HR9576 (Lo-16bits)
9578 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9579 |  |  |  | HR9578 (Lo-16bits)
9580 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9581 |  |  |  | HR9580 (Lo-16bits)
9582 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9583 |  |  |  | HR9582 (Lo-16bits)
9584 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9585 |  |  |  | HR9584 (Lo-16bits)
9586 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9587 |  |  |  | HR9586 (Lo-16bits)
9588 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9589 |  |  |  | HR9588 (Lo-16bits)
9590 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9591 |  |  |  | HR9590 (Lo-16bits)
9592 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9593 |  |  |  | HR9592 (Lo-16bits)
9594 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9595 |  |  |  | HR9594 (Lo-16bits)
9596 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9597 |  |  |  | HR9596 (Lo-16bits)
9598 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9599 |  |  |  | HR9598 (Lo-16bits)
9600 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9601 |  |  |  | HR9600 (Lo-16bits)
9602 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9603 |  |  |  | HR9602 (Lo-16bits)
9604 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9605 |  |  |  | HR9604 (Lo-16bits)
9606 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9607 |  |  |  | HR9606 (Lo-16bits)
9608 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9609 |  |  |  | HR9608 (Lo-16bits)
9610 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9611 |  |  |  | HR9610 (Lo-16bits)
9612 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9613 |  |  |  | HR9612 (Lo-16bits)
9614 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9615 |  |  |  | HR9614 (Lo-16bits)
9616 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9617 |  |  |  | HR9616 (Lo-16bits)
9618 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9619 |  |  |  | HR9618 (Lo-16bits)
9620 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9621 |  |  |  | HR9620 (Lo-16bits)
9622 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9623 |  |  |  | HR9622 (Lo-16bits)
9624 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9625 |  |  |  | HR9624 (Lo-16bits)
9626 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9627 |  |  |  | HR9626 (Lo-16bits)
9628 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9629 |  |  |  | HR9628 (Lo-16bits)
9630 | EMON1:I> (50) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9631 | EMON1:I0> (50N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9632 | EMON1:Idir> (67) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9633 | EMON1:I0dir> (67N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9634 | EMON1:I0Int> (67NT) Monitor condition | R | 1 | 0=Normal;1=FLT FW;2=FLT REV
9635 | EMON1:U< (27) Monitor condition | R | 1 | 0=Normal;1=Undervoltage;2=No voltage
9636 | EMON1:U0> (59N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9637 | EMON1:FL (21FL) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9638 | ALARM:Alarms 1-32 | R | 2 | 0b=A1;1b=A2;2b=A3;3b=A4;4b=A5;5b=A6;6b=A7;7b=A8;8b=A9;9b=A10;10b=A11;11b=A12;12b=A13;13b=A14;14b=A15;15b=A16;16b=A17;17b=A18;18b=A19;19b=A20;20b=A21;21b=A22;22b=A23;23b=A24;24b=A25;25b=A26;26b=A27;27b=A28;28b=A29;29b=A30;30b=A31;31b=A32 (Hi-16bits)
9639 |  |  |  | HR9638 (Lo-16bits)
9640 | ALARM:Alarms 33-64 | R | 2 | 0b=A33;1b=A34;2b=A35;3b=A36;4b=A37;5b=A38;6b=A39;7b=A40;8b=A41;9b=A42;10b=A43;11b=A44;12b=A45;13b=A46;14b=A47;15b=A48;16b=A49;17b=A50;18b=A51;19b=A52;20b=A53;21b=A54;22b=A55;23b=A56;24b=A57;25b=A58;26b=A59;27b=A60;28b=A61;29b=A62;30b=A63;31b=A64 (Hi-16bits)
9641 |  |  |  | HR9640 (Lo-16bits)
9642 | GSYN:Synchronizer mode | RW | 1 | 0=Disabled;1=Activated
9643 | GSYN:Synchronizing by | RW | 1 | 0=Autosynchronizer;1=Manual commands
9644 | GSYN:Manual switching mode | RW | 1 | 0=Assisted synchroswitch;1=I know what I am doing
9645 | GSYN:Magnitude side A | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9646 |  |  |  | HR9645 (Lo-16bits)
9647 | GSYN:Magnitude side B | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9648 |  |  |  | HR9647 (Lo-16bits)
9649 | GSYN:Frequency side A | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9650 |  |  |  | HR9649 (Lo-16bits)
9651 | GSYN:Frequency side B | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9652 |  |  |  | HR9651 (Lo-16bits)
9653 | GSYN:Magnitude difference | R | 2 | FLOAT [-200...200] (Hi-16bits)
9654 |  |  |  | HR9653 (Lo-16bits)
9655 | GSYN:Frequency difference | R | 2 | FLOAT [-100...100] (Hi-16bits)
9656 |  |  |  | HR9655 (Lo-16bits)
9657 | GSYN:Angle difference | R | 2 | FLOAT [-360...360] (Hi-16bits)
9658 |  |  |  | HR9657 (Lo-16bits)
9659 | GSYN:Magnitude difference on closing BRK | R | 2 | FLOAT [-200...200] (Hi-16bits)
9660 |  |  |  | HR9659 (Lo-16bits)
9661 | GSYN:Frequency difference on closing BRK | R | 2 | FLOAT [-100...100] (Hi-16bits)
9662 |  |  |  | HR9661 (Lo-16bits)
9663 | GSYN:Angle difference on closing BRK | R | 2 | FLOAT [-360...360] (Hi-16bits)
9664 |  |  |  | HR9663 (Lo-16bits)
9665 | GSYN:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9666 |  |  |  | HR9665 (Lo-16bits)
9667 | GSYN:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9668 |  |  |  | HR9667 (Lo-16bits)
9669 | GSYN:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9670 |  |  |  | HR9669 (Lo-16bits)
9671 | GSYN:Synchronizing time left | R | 2 | FLOAT [0...1800] (Hi-16bits)
9672 |  |  |  | HR9671 (Lo-16bits)
9673 | GSYN:Magnitude difference fine tune | RW | 2 | FLOAT [-200...200] (Hi-16bits)
9674 |  |  |  | HR9673 (Lo-16bits)
9675 | GSYN:Frequency difference fine tune | RW | 2 | FLOAT [-100...100] (Hi-16bits)
9676 |  |  |  | HR9675 (Lo-16bits)
9677 | GSYN:Angle difference fine tune | RW | 2 | FLOAT [-360...360] (Hi-16bits)
9678 |  |  |  | HR9677 (Lo-16bits)
9679 | GSYN:Start Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9680 |  |  |  | HR9679 (Lo-16bits)
9681 | GSYN:Stop Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9682 |  |  |  | HR9681 (Lo-16bits)
9683 | GSYN:Block and Interrupt Synchronizing | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9684 |  |  |  | HR9683 (Lo-16bits)
9685 | GSYN:Breaker Closed | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9686 |  |  |  | HR9685 (Lo-16bits)
9687 | GSYN:Manual increase voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9688 |  |  |  | HR9687 (Lo-16bits)
9689 | GSYN:Manual decrease voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9690 |  |  |  | HR9689 (Lo-16bits)
9691 | GSYN:Manual increase frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9692 |  |  |  | HR9691 (Lo-16bits)
9693 | GSYN:Manual decrease frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9694 |  |  |  | HR9693 (Lo-16bits)
9695 | GSYN:Manual Close Breaker | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9696 |  |  |  | HR9695 (Lo-16bits)
9697 | GSYN:GSYN Voltage Mag.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9698 |  |  |  | HR9697 (Lo-16bits)
9699 | GSYN:GSYN Voltage Freq.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9700 |  |  |  | HR9699 (Lo-16bits)
9701 | GSYN:GSYN Voltage Ang.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9702 |  |  |  | HR9701 (Lo-16bits)
9703 | GSYN:GSYN Blocked | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9704 |  |  |  | HR9703 (Lo-16bits)
9705 | GSYN:GSYN Running | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9706 |  |  |  | HR9705 (Lo-16bits)
9707 | GSYN:GSYN Increase Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9708 |  |  |  | HR9707 (Lo-16bits)
9709 | GSYN:GSYN Decrease Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9710 |  |  |  | HR9709 (Lo-16bits)
9711 | GSYN:GSYN Increase Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9712 |  |  |  | HR9711 (Lo-16bits)
9713 | GSYN:GSYN Decrease Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9714 |  |  |  | HR9713 (Lo-16bits)
9715 | GSYN:GSYN Breaker Close Pulse | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9716 |  |  |  | HR9715 (Lo-16bits)
9717 | GSYN:GSYN Long Sync Time | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9718 |  |  |  | HR9717 (Lo-16bits)
9719 | GSYN:GSYN Nets Standstill | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9720 |  |  |  | HR9719 (Lo-16bits)
9721 | GSYN:GSYN Nets Departing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9722 |  |  |  | HR9721 (Lo-16bits)
9723 | GSYN:GSYN Nets Enclosing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9724 |  |  |  | HR9723 (Lo-16bits)
9725 | VREC:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9726 | VREC:Scale current values to primary | RW | 1 | 0=No;1=Yes
9727 | VREC:Record fault types (Overcurrrent & Voltage Over/Under) faults | RW | 1 | 0=No;1=Yes
9728 | VREC:Trigger register to memory | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9729 |  |  |  | HR9728 (Lo-16bits)
9730 | VREC:VREC Magnitude 1 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9731 |  |  |  | HR9730 (Lo-16bits)
9732 | VREC:VREC Magnitude 2 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9733 |  |  |  | HR9732 (Lo-16bits)
9734 | VREC:VREC Magnitude 3 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9735 |  |  |  | HR9734 (Lo-16bits)
9736 | VREC:VREC Magnitude 4 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9737 |  |  |  | HR9736 (Lo-16bits)
9738 | VREC:VREC Magnitude 5 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9739 |  |  |  | HR9738 (Lo-16bits)
9740 | VREC:VREC Magnitude 6 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9741 |  |  |  | HR9740 (Lo-16bits)
9742 | VREC:VREC Magnitude 7 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9743 |  |  |  | HR9742 (Lo-16bits)
9744 | VREC:VREC Magnitude 8 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9745 |  |  |  | HR9744 (Lo-16bits)
9746 | RTB:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9747 | RTB:Scale current values to primary | RW | 1 | 0=No;1=Yes
9748 | RTB:RTS to bus Magnitude 1 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9749 |  |  |  | HR9748 (Lo-16bits)
9750 | RTB:RTS to bus Magnitude 2 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9751 |  |  |  | HR9750 (Lo-16bits)
9752 | RTB:RTS to bus Magnitude 3 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9753 |  |  |  | HR9752 (Lo-16bits)
9754 | RTB:RTS to bus Magnitude 4 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9755 |  |  |  | HR9754 (Lo-16bits)
9756 | RTB:RTS to bus Magnitude 5 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9757 |  |  |  | HR9756 (Lo-16bits)
9758 | RTB:RTS to bus Magnitude 6 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9759 |  |  |  | HR9758 (Lo-16bits)
9760 | RTB:RTS to bus Magnitude 7 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9761 |  |  |  | HR9760 (Lo-16bits)
9762 | RTB:RTS to bus Magnitude 8 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9763 |  |  |  | HR9762 (Lo-16bits)
9764 | RTB:RTS to bus Magnitude 9 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9765 |  |  |  | HR9764 (Lo-16bits)
9766 | RTB:RTS to bus Magnitude 10 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9767 |  |  |  | HR9766 (Lo-16bits)
9768 | AOUT:mA In Channel 1 | R | 2 | FLOAT [0...24] (Hi-16bits)
9769 |  |  |  | HR9768 (Lo-16bits)
9770 | AOUT:mA In Channel 2 | R | 2 | FLOAT [0...24] (Hi-16bits)
9771 |  |  |  | HR9770 (Lo-16bits)
9772 | AOUT:mA Out Channel 1 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9773 |  |  |  | HR9772 (Lo-16bits)
9774 | AOUT:mA Out Channel 1 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9775 |  |  |  | HR9774 (Lo-16bits)
9776 | AOUT:mA Out Channel 2 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9777 |  |  |  | HR9776 (Lo-16bits)
9778 | AOUT:mA Out Channel 2 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9779 |  |  |  | HR9778 (Lo-16bits)
9780 | AOUT:mA Out Channel 3 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9781 |  |  |  | HR9780 (Lo-16bits)
9782 | AOUT:mA Out Channel 3 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9783 |  |  |  | HR9782 (Lo-16bits)
9784 | AOUT:mA Out Channel 4 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9785 |  |  |  | HR9784 (Lo-16bits)
9786 | AOUT:mA Out Channel 4 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9787 |  |  |  | HR9786 (Lo-16bits)
9788 | AOUT:mA Out Channel 5 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9789 |  |  |  | HR9788 (Lo-16bits)
9790 | AOUT:mA Out Channel 5 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9791 |  |  |  | HR9790 (Lo-16bits)
9792 | AOUT:mA Out Channel 6 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9793 |  |  |  | HR9792 (Lo-16bits)
9794 | AOUT:mA Out Channel 6 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9795 |  |  |  | HR9794 (Lo-16bits)
9796 | AOUT:mA Out Channel 7 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9797 |  |  |  | HR9796 (Lo-16bits)
9798 | AOUT:mA Out Channel 7 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9799 |  |  |  | HR9798 (Lo-16bits)
9800 | AOUT:mA Out Channel 8 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9801 |  |  |  | HR9800 (Lo-16bits)
9802 | AOUT:mA Out Channel 8 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9803 |  |  |  | HR9802 (Lo-16bits)
9906 | Object6 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9907 | Object7 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9908 | Object8 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9909 | Object9 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9910 | Object10 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020

## AQ-R215, v2.1.1.3-247
HR | Parameter | Access | Length | Info
1 | Modbus requests | R/W=0 | 1 | Diagnostic request counter
2 | Modbus quality | R | 1 | Diagnostic quality
3 | Modbus errors | R/W=0 | 1 | Diagnostic error counter
4 | Modbus Ctrl OK | R/W=0 | 1 | Diagnostic Control OK counter
5 | Modbus Ctrl Errors | R/W=0 | 1 | Diagnostic Control Error counter
6 | Object1 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
7 | Object2 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
8 | Object3 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9 | Object4 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
10 | Object5 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
11 | Previous Event register | R | 6 | Event code
12 | Previous Event register | R | 6 | Event timestamp (ms)
13 | Previous Event register | R | 6 | Event timestamp (sec Hi-16bits)
14 | Previous Event register | R | 6 | Event timestamp (sec Lo-16bits)
15 | Previous Event register | R | 6 | Event sequential index
16 | Previous Event register | R | 6 | RESERVED
17 | Event register | R | 6 | Event code
18 | Event register | R | 6 | Event timestamp (ms)
19 | Event register | R | 6 | Event timestamp (sec Hi-16bits)
20 | Event register | R | 6 | Event timestamp (sec Lo-16bits)
21 | Event register | R | 6 | Event sequential index
22 | Event register | R | 6 | RESERVED
23 | System time | RW | 3 | System time (ms)
24 | System time | RW | 3 | System time (sec Hi-16bits)
25 | System time | RW | 3 | System time (sec Lo-16bits)
26 | MEAS1:Pri.Pha.curr.IL1 ff. | R | 2 | FLOAT [0...100000] (Hi-16bits)
27 |  |  |  | HR26 (Lo-16bits)
28 | MEAS1:Pri.Pha.curr.IL2 ff. | R | 2 | FLOAT [0...100000] (Hi-16bits)
29 |  |  |  | HR28 (Lo-16bits)
30 | MEAS1:Pri.Pha.curr.IL3 ff. | R | 2 | FLOAT [0...100000] (Hi-16bits)
31 |  |  |  | HR30 (Lo-16bits)
32 | MEAS1:Pri.Pha.curr.IL1 3h. | R | 2 | FLOAT [0...100000] (Hi-16bits)
33 |  |  |  | HR32 (Lo-16bits)
34 | MEAS1:Pri.Pha.curr.IL2 3h. | R | 2 | FLOAT [0...100000] (Hi-16bits)
35 |  |  |  | HR34 (Lo-16bits)
36 | MEAS1:Pri.Pha.curr.IL3 3h. | R | 2 | FLOAT [0...100000] (Hi-16bits)
37 |  |  |  | HR36 (Lo-16bits)
38 | MEAS1:Pha.angle IL1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
39 |  |  |  | HR38 (Lo-16bits)
40 | MEAS1:Pha.angle IL2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
41 |  |  |  | HR40 (Lo-16bits)
42 | MEAS1:Pha.angle IL3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
43 |  |  |  | HR42 (Lo-16bits)
44 | MEAS1:Pri.Res.curr.I01 ff. | R | 2 | FLOAT [0...100000] (Hi-16bits)
45 |  |  |  | HR44 (Lo-16bits)
46 | MEAS1:Pri.Res.curr.I01 3h. | R | 2 | FLOAT [0...100000] (Hi-16bits)
47 |  |  |  | HR46 (Lo-16bits)
48 | MEAS1:Res.curr.angle I01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
49 |  |  |  | HR48 (Lo-16bits)
50 | MEAS1:Pri.Res.curr.I02 ff. | R | 2 | FLOAT [0...100000] (Hi-16bits)
51 |  |  |  | HR50 (Lo-16bits)
52 | MEAS1:Pri.Res.curr.I02 3h. | R | 2 | FLOAT [0...100000] (Hi-16bits)
53 |  |  |  | HR52 (Lo-16bits)
54 | MEAS1:Res.curr.angle I02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
55 |  |  |  | HR54 (Lo-16bits)
56 | MEAS1:Pri.calc.I0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
57 |  |  |  | HR56 (Lo-16bits)
58 | MEAS1:calc.I0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
59 |  |  |  | HR58 (Lo-16bits)
60 | MEAS1:Pha.curr.IL1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
61 |  |  |  | HR60 (Lo-16bits)
62 | MEAS1:Pha.curr.IL2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
63 |  |  |  | HR62 (Lo-16bits)
64 | MEAS1:Pha.curr.IL3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
65 |  |  |  | HR64 (Lo-16bits)
66 | MEAS1:Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
67 |  |  |  | HR66 (Lo-16bits)
68 | MEAS1:Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
69 |  |  |  | HR68 (Lo-16bits)
70 | MEAS1:Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
71 |  |  |  | HR70 (Lo-16bits)
72 | MEAS1:Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
73 |  |  |  | HR72 (Lo-16bits)
74 | MEAS1:Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
75 |  |  |  | HR74 (Lo-16bits)
76 | MEAS1:Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
77 |  |  |  | HR76 (Lo-16bits)
78 | MEAS1:Res.curr.I01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
79 |  |  |  | HR78 (Lo-16bits)
80 | MEAS1:Res.curr.I02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
81 |  |  |  | HR80 (Lo-16bits)
82 | MEAS1:Pha.L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
83 |  |  |  | HR82 (Lo-16bits)
84 | MEAS1:Pha.L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
85 |  |  |  | HR84 (Lo-16bits)
86 | MEAS1:Pha.L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
87 |  |  |  | HR86 (Lo-16bits)
88 | MEAS1:Pha.L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
89 |  |  |  | HR88 (Lo-16bits)
90 | MEAS1:Pha.L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
91 |  |  |  | HR90 (Lo-16bits)
92 | MEAS1:Pha.L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
93 |  |  |  | HR92 (Lo-16bits)
94 | MEAS1:Res.I01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
95 |  |  |  | HR94 (Lo-16bits)
96 | MEAS1:Res.I01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
97 |  |  |  | HR96 (Lo-16bits)
98 | MEAS1:Res.I02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
99 |  |  |  | HR98 (Lo-16bits)
100 | MEAS1:Res.I02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
101 |  |  |  | HR100 (Lo-16bits)
102 | MEAS1:P-P curr.IL1 | R | 2 | FLOAT [0...500] (Hi-16bits)
103 |  |  |  | HR102 (Lo-16bits)
104 | MEAS1:P-P curr.IL2 | R | 2 | FLOAT [0...500] (Hi-16bits)
105 |  |  |  | HR104 (Lo-16bits)
106 | MEAS1:P-P curr.IL3 | R | 2 | FLOAT [0...500] (Hi-16bits)
107 |  |  |  | HR106 (Lo-16bits)
108 | MEAS1:P-P curr.I01 | R | 2 | FLOAT [0...500] (Hi-16bits)
109 |  |  |  | HR108 (Lo-16bits)
110 | MEAS1:P-P curr.I02 | R | 2 | FLOAT [0...500] (Hi-16bits)
111 |  |  |  | HR110 (Lo-16bits)
112 | MEAS1:IL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
113 |  |  |  | HR112 (Lo-16bits)
114 | MEAS1:IL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
115 |  |  |  | HR114 (Lo-16bits)
116 | MEAS1:IL1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
117 |  |  |  | HR116 (Lo-16bits)
118 | MEAS1:IL1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
119 |  |  |  | HR118 (Lo-16bits)
120 | MEAS1:IL1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
121 |  |  |  | HR120 (Lo-16bits)
122 | MEAS1:IL1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
123 |  |  |  | HR122 (Lo-16bits)
124 | MEAS1:IL1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
125 |  |  |  | HR124 (Lo-16bits)
126 | MEAS1:IL1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
127 |  |  |  | HR126 (Lo-16bits)
128 | MEAS1:IL1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
129 |  |  |  | HR128 (Lo-16bits)
130 | MEAS1:IL1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
131 |  |  |  | HR130 (Lo-16bits)
132 | MEAS1:IL1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
133 |  |  |  | HR132 (Lo-16bits)
134 | MEAS1:IL1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
135 |  |  |  | HR134 (Lo-16bits)
136 | MEAS1:IL1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
137 |  |  |  | HR136 (Lo-16bits)
138 | MEAS1:IL1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
139 |  |  |  | HR138 (Lo-16bits)
140 | MEAS1:IL1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
141 |  |  |  | HR140 (Lo-16bits)
142 | MEAS1:IL1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
143 |  |  |  | HR142 (Lo-16bits)
144 | MEAS1:IL1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
145 |  |  |  | HR144 (Lo-16bits)
146 | MEAS1:IL1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
147 |  |  |  | HR146 (Lo-16bits)
148 | MEAS1:IL1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
149 |  |  |  | HR148 (Lo-16bits)
150 | MEAS1:IL1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
151 |  |  |  | HR150 (Lo-16bits)
152 | MEAS1:IL1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
153 |  |  |  | HR152 (Lo-16bits)
154 | MEAS1:IL1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
155 |  |  |  | HR154 (Lo-16bits)
156 | MEAS1:IL1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
157 |  |  |  | HR156 (Lo-16bits)
158 | MEAS1:IL1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
159 |  |  |  | HR158 (Lo-16bits)
160 | MEAS1:IL1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
161 |  |  |  | HR160 (Lo-16bits)
162 | MEAS1:IL1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
163 |  |  |  | HR162 (Lo-16bits)
164 | MEAS1:IL1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
165 |  |  |  | HR164 (Lo-16bits)
166 | MEAS1:IL1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
167 |  |  |  | HR166 (Lo-16bits)
168 | MEAS1:IL1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
169 |  |  |  | HR168 (Lo-16bits)
170 | MEAS1:IL1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
171 |  |  |  | HR170 (Lo-16bits)
172 | MEAS1:IL1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
173 |  |  |  | HR172 (Lo-16bits)
174 | MEAS1:IL1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
175 |  |  |  | HR174 (Lo-16bits)
176 | MEAS1:IL1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
177 |  |  |  | HR176 (Lo-16bits)
178 | MEAS1:IL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
179 |  |  |  | HR178 (Lo-16bits)
180 | MEAS1:IL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
181 |  |  |  | HR180 (Lo-16bits)
182 | MEAS1:IL2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
183 |  |  |  | HR182 (Lo-16bits)
184 | MEAS1:IL2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
185 |  |  |  | HR184 (Lo-16bits)
186 | MEAS1:IL2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
187 |  |  |  | HR186 (Lo-16bits)
188 | MEAS1:IL2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
189 |  |  |  | HR188 (Lo-16bits)
190 | MEAS1:IL2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
191 |  |  |  | HR190 (Lo-16bits)
192 | MEAS1:IL2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
193 |  |  |  | HR192 (Lo-16bits)
194 | MEAS1:IL2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
195 |  |  |  | HR194 (Lo-16bits)
196 | MEAS1:IL2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
197 |  |  |  | HR196 (Lo-16bits)
198 | MEAS1:IL2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
199 |  |  |  | HR198 (Lo-16bits)
200 | MEAS1:IL2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
201 |  |  |  | HR200 (Lo-16bits)
202 | MEAS1:IL2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
203 |  |  |  | HR202 (Lo-16bits)
204 | MEAS1:IL2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
205 |  |  |  | HR204 (Lo-16bits)
206 | MEAS1:IL2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
207 |  |  |  | HR206 (Lo-16bits)
208 | MEAS1:IL2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
209 |  |  |  | HR208 (Lo-16bits)
210 | MEAS1:IL2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
211 |  |  |  | HR210 (Lo-16bits)
212 | MEAS1:IL2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
213 |  |  |  | HR212 (Lo-16bits)
214 | MEAS1:IL2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
215 |  |  |  | HR214 (Lo-16bits)
216 | MEAS1:IL2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
217 |  |  |  | HR216 (Lo-16bits)
218 | MEAS1:IL2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
219 |  |  |  | HR218 (Lo-16bits)
220 | MEAS1:IL2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
221 |  |  |  | HR220 (Lo-16bits)
222 | MEAS1:IL2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
223 |  |  |  | HR222 (Lo-16bits)
224 | MEAS1:IL2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
225 |  |  |  | HR224 (Lo-16bits)
226 | MEAS1:IL2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
227 |  |  |  | HR226 (Lo-16bits)
228 | MEAS1:IL2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
229 |  |  |  | HR228 (Lo-16bits)
230 | MEAS1:IL2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
231 |  |  |  | HR230 (Lo-16bits)
232 | MEAS1:IL2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
233 |  |  |  | HR232 (Lo-16bits)
234 | MEAS1:IL2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
235 |  |  |  | HR234 (Lo-16bits)
236 | MEAS1:IL2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
237 |  |  |  | HR236 (Lo-16bits)
238 | MEAS1:IL2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
239 |  |  |  | HR238 (Lo-16bits)
240 | MEAS1:IL2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
241 |  |  |  | HR240 (Lo-16bits)
242 | MEAS1:IL2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
243 |  |  |  | HR242 (Lo-16bits)
244 | MEAS1:IL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
245 |  |  |  | HR244 (Lo-16bits)
246 | MEAS1:IL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
247 |  |  |  | HR246 (Lo-16bits)
248 | MEAS1:IL3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
249 |  |  |  | HR248 (Lo-16bits)
250 | MEAS1:IL3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
251 |  |  |  | HR250 (Lo-16bits)
252 | MEAS1:IL3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
253 |  |  |  | HR252 (Lo-16bits)
254 | MEAS1:IL3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
255 |  |  |  | HR254 (Lo-16bits)
256 | MEAS1:IL3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
257 |  |  |  | HR256 (Lo-16bits)
258 | MEAS1:IL3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
259 |  |  |  | HR258 (Lo-16bits)
260 | MEAS1:IL3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
261 |  |  |  | HR260 (Lo-16bits)
262 | MEAS1:IL3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
263 |  |  |  | HR262 (Lo-16bits)
264 | MEAS1:IL3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
265 |  |  |  | HR264 (Lo-16bits)
266 | MEAS1:IL3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
267 |  |  |  | HR266 (Lo-16bits)
268 | MEAS1:IL3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
269 |  |  |  | HR268 (Lo-16bits)
270 | MEAS1:IL3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
271 |  |  |  | HR270 (Lo-16bits)
272 | MEAS1:IL3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
273 |  |  |  | HR272 (Lo-16bits)
274 | MEAS1:IL3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
275 |  |  |  | HR274 (Lo-16bits)
276 | MEAS1:IL3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
277 |  |  |  | HR276 (Lo-16bits)
278 | MEAS1:IL3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
279 |  |  |  | HR278 (Lo-16bits)
280 | MEAS1:IL3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
281 |  |  |  | HR280 (Lo-16bits)
282 | MEAS1:IL3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
283 |  |  |  | HR282 (Lo-16bits)
284 | MEAS1:IL3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
285 |  |  |  | HR284 (Lo-16bits)
286 | MEAS1:IL3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
287 |  |  |  | HR286 (Lo-16bits)
288 | MEAS1:IL3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
289 |  |  |  | HR288 (Lo-16bits)
290 | MEAS1:IL3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
291 |  |  |  | HR290 (Lo-16bits)
292 | MEAS1:IL3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
293 |  |  |  | HR292 (Lo-16bits)
294 | MEAS1:IL3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
295 |  |  |  | HR294 (Lo-16bits)
296 | MEAS1:IL3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
297 |  |  |  | HR296 (Lo-16bits)
298 | MEAS1:IL3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
299 |  |  |  | HR298 (Lo-16bits)
300 | MEAS1:IL3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
301 |  |  |  | HR300 (Lo-16bits)
302 | MEAS1:IL3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
303 |  |  |  | HR302 (Lo-16bits)
304 | MEAS1:IL3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
305 |  |  |  | HR304 (Lo-16bits)
306 | MEAS1:IL3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
307 |  |  |  | HR306 (Lo-16bits)
308 | MEAS1:IL3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
309 |  |  |  | HR308 (Lo-16bits)
310 | MEAS1:I01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
311 |  |  |  | HR310 (Lo-16bits)
312 | MEAS1:I01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
313 |  |  |  | HR312 (Lo-16bits)
314 | MEAS1:I01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
315 |  |  |  | HR314 (Lo-16bits)
316 | MEAS1:I01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
317 |  |  |  | HR316 (Lo-16bits)
318 | MEAS1:I01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
319 |  |  |  | HR318 (Lo-16bits)
320 | MEAS1:I01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
321 |  |  |  | HR320 (Lo-16bits)
322 | MEAS1:I01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
323 |  |  |  | HR322 (Lo-16bits)
324 | MEAS1:I01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
325 |  |  |  | HR324 (Lo-16bits)
326 | MEAS1:I01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
327 |  |  |  | HR326 (Lo-16bits)
328 | MEAS1:I01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
329 |  |  |  | HR328 (Lo-16bits)
330 | MEAS1:I01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
331 |  |  |  | HR330 (Lo-16bits)
332 | MEAS1:I01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
333 |  |  |  | HR332 (Lo-16bits)
334 | MEAS1:I01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
335 |  |  |  | HR334 (Lo-16bits)
336 | MEAS1:I01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
337 |  |  |  | HR336 (Lo-16bits)
338 | MEAS1:I01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
339 |  |  |  | HR338 (Lo-16bits)
340 | MEAS1:I01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
341 |  |  |  | HR340 (Lo-16bits)
342 | MEAS1:I01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
343 |  |  |  | HR342 (Lo-16bits)
344 | MEAS1:I01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
345 |  |  |  | HR344 (Lo-16bits)
346 | MEAS1:I01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
347 |  |  |  | HR346 (Lo-16bits)
348 | MEAS1:I01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
349 |  |  |  | HR348 (Lo-16bits)
350 | MEAS1:I01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
351 |  |  |  | HR350 (Lo-16bits)
352 | MEAS1:I01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
353 |  |  |  | HR352 (Lo-16bits)
354 | MEAS1:I01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
355 |  |  |  | HR354 (Lo-16bits)
356 | MEAS1:I01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
357 |  |  |  | HR356 (Lo-16bits)
358 | MEAS1:I01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
359 |  |  |  | HR358 (Lo-16bits)
360 | MEAS1:I01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
361 |  |  |  | HR360 (Lo-16bits)
362 | MEAS1:I01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
363 |  |  |  | HR362 (Lo-16bits)
364 | MEAS1:I01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
365 |  |  |  | HR364 (Lo-16bits)
366 | MEAS1:I01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
367 |  |  |  | HR366 (Lo-16bits)
368 | MEAS1:I01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
369 |  |  |  | HR368 (Lo-16bits)
370 | MEAS1:I01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
371 |  |  |  | HR370 (Lo-16bits)
372 | MEAS1:I01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
373 |  |  |  | HR372 (Lo-16bits)
374 | MEAS1:I01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
375 |  |  |  | HR374 (Lo-16bits)
376 | MEAS1:I02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
377 |  |  |  | HR376 (Lo-16bits)
378 | MEAS1:I02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
379 |  |  |  | HR378 (Lo-16bits)
380 | MEAS1:I02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
381 |  |  |  | HR380 (Lo-16bits)
382 | MEAS1:I02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
383 |  |  |  | HR382 (Lo-16bits)
384 | MEAS1:I02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
385 |  |  |  | HR384 (Lo-16bits)
386 | MEAS1:I02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
387 |  |  |  | HR386 (Lo-16bits)
388 | MEAS1:I02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
389 |  |  |  | HR388 (Lo-16bits)
390 | MEAS1:I02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
391 |  |  |  | HR390 (Lo-16bits)
392 | MEAS1:I02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
393 |  |  |  | HR392 (Lo-16bits)
394 | MEAS1:I02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
395 |  |  |  | HR394 (Lo-16bits)
396 | MEAS1:I02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
397 |  |  |  | HR396 (Lo-16bits)
398 | MEAS1:I02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
399 |  |  |  | HR398 (Lo-16bits)
400 | MEAS1:I02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
401 |  |  |  | HR400 (Lo-16bits)
402 | MEAS1:I02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
403 |  |  |  | HR402 (Lo-16bits)
404 | MEAS1:I02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
405 |  |  |  | HR404 (Lo-16bits)
406 | MEAS1:I02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
407 |  |  |  | HR406 (Lo-16bits)
408 | MEAS1:I02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
409 |  |  |  | HR408 (Lo-16bits)
410 | MEAS1:I02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
411 |  |  |  | HR410 (Lo-16bits)
412 | MEAS1:I02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
413 |  |  |  | HR412 (Lo-16bits)
414 | MEAS1:I02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
415 |  |  |  | HR414 (Lo-16bits)
416 | MEAS1:I02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
417 |  |  |  | HR416 (Lo-16bits)
418 | MEAS1:I02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
419 |  |  |  | HR418 (Lo-16bits)
420 | MEAS1:I02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
421 |  |  |  | HR420 (Lo-16bits)
422 | MEAS1:I02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
423 |  |  |  | HR422 (Lo-16bits)
424 | MEAS1:I02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
425 |  |  |  | HR424 (Lo-16bits)
426 | MEAS1:I02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
427 |  |  |  | HR426 (Lo-16bits)
428 | MEAS1:I02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
429 |  |  |  | HR428 (Lo-16bits)
430 | MEAS1:I02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
431 |  |  |  | HR430 (Lo-16bits)
432 | MEAS1:I02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
433 |  |  |  | HR432 (Lo-16bits)
434 | MEAS1:I02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
435 |  |  |  | HR434 (Lo-16bits)
436 | MEAS1:I02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
437 |  |  |  | HR436 (Lo-16bits)
438 | MEAS1:I02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
439 |  |  |  | HR438 (Lo-16bits)
440 | MEAS1:I02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
441 |  |  |  | HR440 (Lo-16bits)
442 | MEAS1:Meas1 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
443 |  |  |  | HR442 (Lo-16bits)
444 | MEAS2:Pri.Pha.curr.I''L1 | R | 2 | FLOAT [0...100000] (Hi-16bits)
445 |  |  |  | HR444 (Lo-16bits)
446 | MEAS2:Pri.Pha.curr.I''L2 | R | 2 | FLOAT [0...100000] (Hi-16bits)
447 |  |  |  | HR446 (Lo-16bits)
448 | MEAS2:Pri.Pha.curr.I''L3 | R | 2 | FLOAT [0...100000] (Hi-16bits)
449 |  |  |  | HR448 (Lo-16bits)
450 | MEAS2:Pha.angle I''L1 | R | 2 | FLOAT [-360...360] (Hi-16bits)
451 |  |  |  | HR450 (Lo-16bits)
452 | MEAS2:Pha.angle I''L2 | R | 2 | FLOAT [-360...360] (Hi-16bits)
453 |  |  |  | HR452 (Lo-16bits)
454 | MEAS2:Pha.angle I''L3 | R | 2 | FLOAT [-360...360] (Hi-16bits)
455 |  |  |  | HR454 (Lo-16bits)
456 | MEAS2:Pri.Res.curr.I''01 | R | 2 | FLOAT [0...100000] (Hi-16bits)
457 |  |  |  | HR456 (Lo-16bits)
458 | MEAS2:Res.curr.angle I''01 | R | 2 | FLOAT [-360...360] (Hi-16bits)
459 |  |  |  | HR458 (Lo-16bits)
460 | MEAS2:Pri.Res.curr.I''02 | R | 2 | FLOAT [0...100000] (Hi-16bits)
461 |  |  |  | HR460 (Lo-16bits)
462 | MEAS2:Res.curr.angle I''02 | R | 2 | FLOAT [-360...360] (Hi-16bits)
463 |  |  |  | HR462 (Lo-16bits)
464 | MEAS2:Pri.calc.I''0 | R | 2 | FLOAT [0...100000] (Hi-16bits)
465 |  |  |  | HR464 (Lo-16bits)
466 | MEAS2:calc.I''0 Pha.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
467 |  |  |  | HR466 (Lo-16bits)
468 | MEAS2:Pha.curr.I''L1 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
469 |  |  |  | HR468 (Lo-16bits)
470 | MEAS2:Pha.curr.I''L2 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
471 |  |  |  | HR470 (Lo-16bits)
472 | MEAS2:Pha.curr.I''L3 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
473 |  |  |  | HR472 (Lo-16bits)
474 | MEAS2:I'' Pri.Pos.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
475 |  |  |  | HR474 (Lo-16bits)
476 | MEAS2:I'' Pri.Neg.seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
477 |  |  |  | HR476 (Lo-16bits)
478 | MEAS2:I'' Pri.Zero seq.curr. | R | 2 | FLOAT [0...100000] (Hi-16bits)
479 |  |  |  | HR478 (Lo-16bits)
480 | MEAS2:I'' Pos.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
481 |  |  |  | HR480 (Lo-16bits)
482 | MEAS2:I'' Neg.seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
483 |  |  |  | HR482 (Lo-16bits)
484 | MEAS2:I'' Zero seq.curr.angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
485 |  |  |  | HR484 (Lo-16bits)
486 | MEAS2:Res.curr.I''01 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
487 |  |  |  | HR486 (Lo-16bits)
488 | MEAS2:Res.curr.I''02 TRMS Pri | R | 2 | FLOAT [0...100000] (Hi-16bits)
489 |  |  |  | HR488 (Lo-16bits)
490 | MEAS2:Pha.I''L1 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
491 |  |  |  | HR490 (Lo-16bits)
492 | MEAS2:Pha.I''L1 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
493 |  |  |  | HR492 (Lo-16bits)
494 | MEAS2:Pha.I''L2 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
495 |  |  |  | HR494 (Lo-16bits)
496 | MEAS2:Pha.I''L2 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
497 |  |  |  | HR496 (Lo-16bits)
498 | MEAS2:Pha.I''L3 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
499 |  |  |  | HR498 (Lo-16bits)
500 | MEAS2:Pha.I''L3 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
501 |  |  |  | HR500 (Lo-16bits)
502 | MEAS2:Res.I''01 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
503 |  |  |  | HR502 (Lo-16bits)
504 | MEAS2:Res.I''01 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
505 |  |  |  | HR504 (Lo-16bits)
506 | MEAS2:Res.I''02 ampl. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
507 |  |  |  | HR506 (Lo-16bits)
508 | MEAS2:Res.I''02 pow. THD | R | 2 | FLOAT [0...100] (Hi-16bits)
509 |  |  |  | HR508 (Lo-16bits)
510 | MEAS2:P-P curr.I''L1 | R | 2 | FLOAT [0...500] (Hi-16bits)
511 |  |  |  | HR510 (Lo-16bits)
512 | MEAS2:P-P curr.I''L2 | R | 2 | FLOAT [0...500] (Hi-16bits)
513 |  |  |  | HR512 (Lo-16bits)
514 | MEAS2:P-P curr.I''L3 | R | 2 | FLOAT [0...500] (Hi-16bits)
515 |  |  |  | HR514 (Lo-16bits)
516 | MEAS2:P-P curr.I''01 | R | 2 | FLOAT [0...500] (Hi-16bits)
517 |  |  |  | HR516 (Lo-16bits)
518 | MEAS2:P-P curr.I''02 | R | 2 | FLOAT [0...500] (Hi-16bits)
519 |  |  |  | HR518 (Lo-16bits)
520 | MEAS2:I''L1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
521 |  |  |  | HR520 (Lo-16bits)
522 | MEAS2:I''L1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
523 |  |  |  | HR522 (Lo-16bits)
524 | MEAS2:I''L1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
525 |  |  |  | HR524 (Lo-16bits)
526 | MEAS2:I''L1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
527 |  |  |  | HR526 (Lo-16bits)
528 | MEAS2:I''L1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
529 |  |  |  | HR528 (Lo-16bits)
530 | MEAS2:I''L1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
531 |  |  |  | HR530 (Lo-16bits)
532 | MEAS2:I''L1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
533 |  |  |  | HR532 (Lo-16bits)
534 | MEAS2:I''L1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
535 |  |  |  | HR534 (Lo-16bits)
536 | MEAS2:I''L1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
537 |  |  |  | HR536 (Lo-16bits)
538 | MEAS2:I''L1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
539 |  |  |  | HR538 (Lo-16bits)
540 | MEAS2:I''L1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
541 |  |  |  | HR540 (Lo-16bits)
542 | MEAS2:I''L1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
543 |  |  |  | HR542 (Lo-16bits)
544 | MEAS2:I''L1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
545 |  |  |  | HR544 (Lo-16bits)
546 | MEAS2:I''L1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
547 |  |  |  | HR546 (Lo-16bits)
548 | MEAS2:I''L1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
549 |  |  |  | HR548 (Lo-16bits)
550 | MEAS2:I''L1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
551 |  |  |  | HR550 (Lo-16bits)
552 | MEAS2:I''L1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
553 |  |  |  | HR552 (Lo-16bits)
554 | MEAS2:I''L1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
555 |  |  |  | HR554 (Lo-16bits)
556 | MEAS2:I''L1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
557 |  |  |  | HR556 (Lo-16bits)
558 | MEAS2:I''L1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
559 |  |  |  | HR558 (Lo-16bits)
560 | MEAS2:I''L1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
561 |  |  |  | HR560 (Lo-16bits)
562 | MEAS2:I''L1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
563 |  |  |  | HR562 (Lo-16bits)
564 | MEAS2:I''L1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
565 |  |  |  | HR564 (Lo-16bits)
566 | MEAS2:I''L1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
567 |  |  |  | HR566 (Lo-16bits)
568 | MEAS2:I''L1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
569 |  |  |  | HR568 (Lo-16bits)
570 | MEAS2:I''L1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
571 |  |  |  | HR570 (Lo-16bits)
572 | MEAS2:I''L1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
573 |  |  |  | HR572 (Lo-16bits)
574 | MEAS2:I''L1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
575 |  |  |  | HR574 (Lo-16bits)
576 | MEAS2:I''L1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
577 |  |  |  | HR576 (Lo-16bits)
578 | MEAS2:I''L1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
579 |  |  |  | HR578 (Lo-16bits)
580 | MEAS2:I''L1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
581 |  |  |  | HR580 (Lo-16bits)
582 | MEAS2:I''L1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
583 |  |  |  | HR582 (Lo-16bits)
584 | MEAS2:I''L1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
585 |  |  |  | HR584 (Lo-16bits)
586 | MEAS2:I''L2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
587 |  |  |  | HR586 (Lo-16bits)
588 | MEAS2:I''L2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
589 |  |  |  | HR588 (Lo-16bits)
590 | MEAS2:I''L2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
591 |  |  |  | HR590 (Lo-16bits)
592 | MEAS2:I''L2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
593 |  |  |  | HR592 (Lo-16bits)
594 | MEAS2:I''L2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
595 |  |  |  | HR594 (Lo-16bits)
596 | MEAS2:I''L2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
597 |  |  |  | HR596 (Lo-16bits)
598 | MEAS2:I''L2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
599 |  |  |  | HR598 (Lo-16bits)
600 | MEAS2:I''L2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
601 |  |  |  | HR600 (Lo-16bits)
602 | MEAS2:I''L2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
603 |  |  |  | HR602 (Lo-16bits)
604 | MEAS2:I''L2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
605 |  |  |  | HR604 (Lo-16bits)
606 | MEAS2:I''L2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
607 |  |  |  | HR606 (Lo-16bits)
608 | MEAS2:I''L2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
609 |  |  |  | HR608 (Lo-16bits)
610 | MEAS2:I''L2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
611 |  |  |  | HR610 (Lo-16bits)
612 | MEAS2:I''L2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
613 |  |  |  | HR612 (Lo-16bits)
614 | MEAS2:I''L2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
615 |  |  |  | HR614 (Lo-16bits)
616 | MEAS2:I''L2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
617 |  |  |  | HR616 (Lo-16bits)
618 | MEAS2:I''L2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
619 |  |  |  | HR618 (Lo-16bits)
620 | MEAS2:I''L2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
621 |  |  |  | HR620 (Lo-16bits)
622 | MEAS2:I''L2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
623 |  |  |  | HR622 (Lo-16bits)
624 | MEAS2:I''L2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
625 |  |  |  | HR624 (Lo-16bits)
626 | MEAS2:I''L2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
627 |  |  |  | HR626 (Lo-16bits)
628 | MEAS2:I''L2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
629 |  |  |  | HR628 (Lo-16bits)
630 | MEAS2:I''L2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
631 |  |  |  | HR630 (Lo-16bits)
632 | MEAS2:I''L2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
633 |  |  |  | HR632 (Lo-16bits)
634 | MEAS2:I''L2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
635 |  |  |  | HR634 (Lo-16bits)
636 | MEAS2:I''L2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
637 |  |  |  | HR636 (Lo-16bits)
638 | MEAS2:I''L2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
639 |  |  |  | HR638 (Lo-16bits)
640 | MEAS2:I''L2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
641 |  |  |  | HR640 (Lo-16bits)
642 | MEAS2:I''L2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
643 |  |  |  | HR642 (Lo-16bits)
644 | MEAS2:I''L2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
645 |  |  |  | HR644 (Lo-16bits)
646 | MEAS2:I''L2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
647 |  |  |  | HR646 (Lo-16bits)
648 | MEAS2:I''L2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
649 |  |  |  | HR648 (Lo-16bits)
650 | MEAS2:I''L2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
651 |  |  |  | HR650 (Lo-16bits)
652 | MEAS2:I''L3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
653 |  |  |  | HR652 (Lo-16bits)
654 | MEAS2:I''L3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
655 |  |  |  | HR654 (Lo-16bits)
656 | MEAS2:I''L3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
657 |  |  |  | HR656 (Lo-16bits)
658 | MEAS2:I''L3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
659 |  |  |  | HR658 (Lo-16bits)
660 | MEAS2:I''L3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
661 |  |  |  | HR660 (Lo-16bits)
662 | MEAS2:I''L3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
663 |  |  |  | HR662 (Lo-16bits)
664 | MEAS2:I''L3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
665 |  |  |  | HR664 (Lo-16bits)
666 | MEAS2:I''L3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
667 |  |  |  | HR666 (Lo-16bits)
668 | MEAS2:I''L3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
669 |  |  |  | HR668 (Lo-16bits)
670 | MEAS2:I''L3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
671 |  |  |  | HR670 (Lo-16bits)
672 | MEAS2:I''L3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
673 |  |  |  | HR672 (Lo-16bits)
674 | MEAS2:I''L3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
675 |  |  |  | HR674 (Lo-16bits)
676 | MEAS2:I''L3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
677 |  |  |  | HR676 (Lo-16bits)
678 | MEAS2:I''L3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
679 |  |  |  | HR678 (Lo-16bits)
680 | MEAS2:I''L3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
681 |  |  |  | HR680 (Lo-16bits)
682 | MEAS2:I''L3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
683 |  |  |  | HR682 (Lo-16bits)
684 | MEAS2:I''L3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
685 |  |  |  | HR684 (Lo-16bits)
686 | MEAS2:I''L3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
687 |  |  |  | HR686 (Lo-16bits)
688 | MEAS2:I''L3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
689 |  |  |  | HR688 (Lo-16bits)
690 | MEAS2:I''L3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
691 |  |  |  | HR690 (Lo-16bits)
692 | MEAS2:I''L3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
693 |  |  |  | HR692 (Lo-16bits)
694 | MEAS2:I''L3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
695 |  |  |  | HR694 (Lo-16bits)
696 | MEAS2:I''L3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
697 |  |  |  | HR696 (Lo-16bits)
698 | MEAS2:I''L3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
699 |  |  |  | HR698 (Lo-16bits)
700 | MEAS2:I''L3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
701 |  |  |  | HR700 (Lo-16bits)
702 | MEAS2:I''L3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
703 |  |  |  | HR702 (Lo-16bits)
704 | MEAS2:I''L3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
705 |  |  |  | HR704 (Lo-16bits)
706 | MEAS2:I''L3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
707 |  |  |  | HR706 (Lo-16bits)
708 | MEAS2:I''L3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
709 |  |  |  | HR708 (Lo-16bits)
710 | MEAS2:I''L3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
711 |  |  |  | HR710 (Lo-16bits)
712 | MEAS2:I''L3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
713 |  |  |  | HR712 (Lo-16bits)
714 | MEAS2:I''L3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
715 |  |  |  | HR714 (Lo-16bits)
716 | MEAS2:I''L3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
717 |  |  |  | HR716 (Lo-16bits)
718 | MEAS2:I''01 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
719 |  |  |  | HR718 (Lo-16bits)
720 | MEAS2:I''01 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
721 |  |  |  | HR720 (Lo-16bits)
722 | MEAS2:I''01 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
723 |  |  |  | HR722 (Lo-16bits)
724 | MEAS2:I''01 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
725 |  |  |  | HR724 (Lo-16bits)
726 | MEAS2:I''01 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
727 |  |  |  | HR726 (Lo-16bits)
728 | MEAS2:I''01 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
729 |  |  |  | HR728 (Lo-16bits)
730 | MEAS2:I''01 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
731 |  |  |  | HR730 (Lo-16bits)
732 | MEAS2:I''01 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
733 |  |  |  | HR732 (Lo-16bits)
734 | MEAS2:I''01 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
735 |  |  |  | HR734 (Lo-16bits)
736 | MEAS2:I''01 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
737 |  |  |  | HR736 (Lo-16bits)
738 | MEAS2:I''01 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
739 |  |  |  | HR738 (Lo-16bits)
740 | MEAS2:I''01 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
741 |  |  |  | HR740 (Lo-16bits)
742 | MEAS2:I''01 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
743 |  |  |  | HR742 (Lo-16bits)
744 | MEAS2:I''01 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
745 |  |  |  | HR744 (Lo-16bits)
746 | MEAS2:I''01 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
747 |  |  |  | HR746 (Lo-16bits)
748 | MEAS2:I''01 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
749 |  |  |  | HR748 (Lo-16bits)
750 | MEAS2:I''01 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
751 |  |  |  | HR750 (Lo-16bits)
752 | MEAS2:I''01 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
753 |  |  |  | HR752 (Lo-16bits)
754 | MEAS2:I''01 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
755 |  |  |  | HR754 (Lo-16bits)
756 | MEAS2:I''01 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
757 |  |  |  | HR756 (Lo-16bits)
758 | MEAS2:I''01 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
759 |  |  |  | HR758 (Lo-16bits)
760 | MEAS2:I''01 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
761 |  |  |  | HR760 (Lo-16bits)
762 | MEAS2:I''01 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
763 |  |  |  | HR762 (Lo-16bits)
764 | MEAS2:I''01 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
765 |  |  |  | HR764 (Lo-16bits)
766 | MEAS2:I''01 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
767 |  |  |  | HR766 (Lo-16bits)
768 | MEAS2:I''01 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
769 |  |  |  | HR768 (Lo-16bits)
770 | MEAS2:I''01 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
771 |  |  |  | HR770 (Lo-16bits)
772 | MEAS2:I''01 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
773 |  |  |  | HR772 (Lo-16bits)
774 | MEAS2:I''01 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
775 |  |  |  | HR774 (Lo-16bits)
776 | MEAS2:I''01 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
777 |  |  |  | HR776 (Lo-16bits)
778 | MEAS2:I''01 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
779 |  |  |  | HR778 (Lo-16bits)
780 | MEAS2:I''01 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
781 |  |  |  | HR780 (Lo-16bits)
782 | MEAS2:I''01 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
783 |  |  |  | HR782 (Lo-16bits)
784 | MEAS2:I''02 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
785 |  |  |  | HR784 (Lo-16bits)
786 | MEAS2:I''02 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
787 |  |  |  | HR786 (Lo-16bits)
788 | MEAS2:I''02 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
789 |  |  |  | HR788 (Lo-16bits)
790 | MEAS2:I''02 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
791 |  |  |  | HR790 (Lo-16bits)
792 | MEAS2:I''02 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
793 |  |  |  | HR792 (Lo-16bits)
794 | MEAS2:I''02 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
795 |  |  |  | HR794 (Lo-16bits)
796 | MEAS2:I''02 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
797 |  |  |  | HR796 (Lo-16bits)
798 | MEAS2:I''02 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
799 |  |  |  | HR798 (Lo-16bits)
800 | MEAS2:I''02 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
801 |  |  |  | HR800 (Lo-16bits)
802 | MEAS2:I''02 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
803 |  |  |  | HR802 (Lo-16bits)
804 | MEAS2:I''02 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
805 |  |  |  | HR804 (Lo-16bits)
806 | MEAS2:I''02 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
807 |  |  |  | HR806 (Lo-16bits)
808 | MEAS2:I''02 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
809 |  |  |  | HR808 (Lo-16bits)
810 | MEAS2:I''02 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
811 |  |  |  | HR810 (Lo-16bits)
812 | MEAS2:I''02 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
813 |  |  |  | HR812 (Lo-16bits)
814 | MEAS2:I''02 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
815 |  |  |  | HR814 (Lo-16bits)
816 | MEAS2:I''02 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
817 |  |  |  | HR816 (Lo-16bits)
818 | MEAS2:I''02 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
819 |  |  |  | HR818 (Lo-16bits)
820 | MEAS2:I''02 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
821 |  |  |  | HR820 (Lo-16bits)
822 | MEAS2:I''02 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
823 |  |  |  | HR822 (Lo-16bits)
824 | MEAS2:I''02 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
825 |  |  |  | HR824 (Lo-16bits)
826 | MEAS2:I''02 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
827 |  |  |  | HR826 (Lo-16bits)
828 | MEAS2:I''02 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
829 |  |  |  | HR828 (Lo-16bits)
830 | MEAS2:I''02 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
831 |  |  |  | HR830 (Lo-16bits)
832 | MEAS2:I''02 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
833 |  |  |  | HR832 (Lo-16bits)
834 | MEAS2:I''02 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
835 |  |  |  | HR834 (Lo-16bits)
836 | MEAS2:I''02 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
837 |  |  |  | HR836 (Lo-16bits)
838 | MEAS2:I''02 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
839 |  |  |  | HR838 (Lo-16bits)
840 | MEAS2:I''02 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
841 |  |  |  | HR840 (Lo-16bits)
842 | MEAS2:I''02 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
843 |  |  |  | HR842 (Lo-16bits)
844 | MEAS2:I''02 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
845 |  |  |  | HR844 (Lo-16bits)
846 | MEAS2:I''02 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
847 |  |  |  | HR846 (Lo-16bits)
848 | MEAS2:I''02 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
849 |  |  |  | HR848 (Lo-16bits)
850 | MEAS2:MEAS2 IL ang. Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
851 |  |  |  | HR850 (Lo-16bits)
852 | MEAS3:U1Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
853 |  |  |  | HR852 (Lo-16bits)
854 | MEAS3:U1Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
855 |  |  |  | HR854 (Lo-16bits)
856 | MEAS3:U2Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
857 |  |  |  | HR856 (Lo-16bits)
858 | MEAS3:U2Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
859 |  |  |  | HR858 (Lo-16bits)
860 | MEAS3:U3Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
861 |  |  |  | HR860 (Lo-16bits)
862 | MEAS3:U3Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
863 |  |  |  | HR862 (Lo-16bits)
864 | MEAS3:U4Volt pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
865 |  |  |  | HR864 (Lo-16bits)
866 | MEAS3:U4Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
867 |  |  |  | HR866 (Lo-16bits)
868 | MEAS3:U1 Volt pri ff | R | 2 | FLOAT [0...1000000] (Hi-16bits)
869 |  |  |  | HR868 (Lo-16bits)
870 | MEAS3:U1 Volt sec ff | R | 2 | FLOAT [0...500] (Hi-16bits)
871 |  |  |  | HR870 (Lo-16bits)
872 | MEAS3:U1 Angle ff | R | 2 | FLOAT [-360...360] (Hi-16bits)
873 |  |  |  | HR872 (Lo-16bits)
874 | MEAS3:U2 Volt pri ff | R | 2 | FLOAT [0...1000000] (Hi-16bits)
875 |  |  |  | HR874 (Lo-16bits)
876 | MEAS3:U2 Volt sec ff | R | 2 | FLOAT [0...500] (Hi-16bits)
877 |  |  |  | HR876 (Lo-16bits)
878 | MEAS3:U2 Angle ff | R | 2 | FLOAT [-360...360] (Hi-16bits)
879 |  |  |  | HR878 (Lo-16bits)
880 | MEAS3:U3 Volt pri ff | R | 2 | FLOAT [0...1000000] (Hi-16bits)
881 |  |  |  | HR880 (Lo-16bits)
882 | MEAS3:U3 Volt sec ff | R | 2 | FLOAT [0...500] (Hi-16bits)
883 |  |  |  | HR882 (Lo-16bits)
884 | MEAS3:U3 Angle ff | R | 2 | FLOAT [-360...360] (Hi-16bits)
885 |  |  |  | HR884 (Lo-16bits)
886 | MEAS3:U4 Volt pri ff | R | 2 | FLOAT [0...1000000] (Hi-16bits)
887 |  |  |  | HR886 (Lo-16bits)
888 | MEAS3:U4 Volt sec ff | R | 2 | FLOAT [0...500] (Hi-16bits)
889 |  |  |  | HR888 (Lo-16bits)
890 | MEAS3:U4 Angle ff | R | 2 | FLOAT [-360...360] (Hi-16bits)
891 |  |  |  | HR890 (Lo-16bits)
892 | MEAS3:U1 Volt pri 3h | R | 2 | FLOAT [0...1000000] (Hi-16bits)
893 |  |  |  | HR892 (Lo-16bits)
894 | MEAS3:U1 Volt sec 3h | R | 2 | FLOAT [0...500] (Hi-16bits)
895 |  |  |  | HR894 (Lo-16bits)
896 | MEAS3:U1 Angle 3h | R | 2 | FLOAT [-360...360] (Hi-16bits)
897 |  |  |  | HR896 (Lo-16bits)
898 | MEAS3:U2 Volt pri 3h | R | 2 | FLOAT [0...1000000] (Hi-16bits)
899 |  |  |  | HR898 (Lo-16bits)
900 | MEAS3:U2 Volt sec 3h | R | 2 | FLOAT [0...500] (Hi-16bits)
901 |  |  |  | HR900 (Lo-16bits)
902 | MEAS3:U2 Angle 3h | R | 2 | FLOAT [-360...360] (Hi-16bits)
903 |  |  |  | HR902 (Lo-16bits)
904 | MEAS3:U3 Volt pri 3h | R | 2 | FLOAT [0...1000000] (Hi-16bits)
905 |  |  |  | HR904 (Lo-16bits)
906 | MEAS3:U3 Volt sec 3h | R | 2 | FLOAT [0...500] (Hi-16bits)
907 |  |  |  | HR906 (Lo-16bits)
908 | MEAS3:U3 Angle 3h | R | 2 | FLOAT [-360...360] (Hi-16bits)
909 |  |  |  | HR908 (Lo-16bits)
910 | MEAS3:U4 Volt pri 3h | R | 2 | FLOAT [0...1000000] (Hi-16bits)
911 |  |  |  | HR910 (Lo-16bits)
912 | MEAS3:U4 Volt sec 3h | R | 2 | FLOAT [0...500] (Hi-16bits)
913 |  |  |  | HR912 (Lo-16bits)
914 | MEAS3:U4 Angle 3h | R | 2 | FLOAT [-360...360] (Hi-16bits)
915 |  |  |  | HR914 (Lo-16bits)
916 | MEAS3:U1Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
917 |  |  |  | HR916 (Lo-16bits)
918 | MEAS3:U1Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
919 |  |  |  | HR918 (Lo-16bits)
920 | MEAS3:U2Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
921 |  |  |  | HR920 (Lo-16bits)
922 | MEAS3:U2Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
923 |  |  |  | HR922 (Lo-16bits)
924 | MEAS3:U3Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
925 |  |  |  | HR924 (Lo-16bits)
926 | MEAS3:U3Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
927 |  |  |  | HR926 (Lo-16bits)
928 | MEAS3:U4Volt TRMS pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
929 |  |  |  | HR928 (Lo-16bits)
930 | MEAS3:U4Volt TRMS sec | R | 2 | FLOAT [0...500] (Hi-16bits)
931 |  |  |  | HR930 (Lo-16bits)
932 | MEAS3:Pos.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
933 |  |  |  | HR932 (Lo-16bits)
934 | MEAS3:Pos.seq.Volt.sec | R | 2 | FLOAT [0...480] (Hi-16bits)
935 |  |  |  | HR934 (Lo-16bits)
936 | MEAS3:Neg.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
937 |  |  |  | HR936 (Lo-16bits)
938 | MEAS3:Neg.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
939 |  |  |  | HR938 (Lo-16bits)
940 | MEAS3:Zero.seq.Volt.pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
941 |  |  |  | HR940 (Lo-16bits)
942 | MEAS3:Zero.seq.Volt.sec | R | 2 | FLOAT [0...500] (Hi-16bits)
943 |  |  |  | HR942 (Lo-16bits)
944 | MEAS3:U0 Calc. pri | R | 2 | FLOAT [0...1000000] (Hi-16bits)
945 |  |  |  | HR944 (Lo-16bits)
946 | MEAS3:U0 Calc.Volt sec | R | 2 | FLOAT [0...500] (Hi-16bits)
947 |  |  |  | HR946 (Lo-16bits)
948 | MEAS3:U1 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
949 |  |  |  | HR948 (Lo-16bits)
950 | MEAS3:U2 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
951 |  |  |  | HR950 (Lo-16bits)
952 | MEAS3:U3 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
953 |  |  |  | HR952 (Lo-16bits)
954 | MEAS3:U4 Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
955 |  |  |  | HR954 (Lo-16bits)
956 | MEAS3:Pos.Seq volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
957 |  |  |  | HR956 (Lo-16bits)
958 | MEAS3:Neg.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
959 |  |  |  | HR958 (Lo-16bits)
960 | MEAS3:Zero.Seq.volt.Angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
961 |  |  |  | HR960 (Lo-16bits)
962 | MEAS3:System volt UL12 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
963 |  |  |  | HR962 (Lo-16bits)
964 | MEAS3:System volt UL12 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
965 |  |  |  | HR964 (Lo-16bits)
966 | MEAS3:System volt UL12 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
967 |  |  |  | HR966 (Lo-16bits)
968 | MEAS3:System volt UL23 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
969 |  |  |  | HR968 (Lo-16bits)
970 | MEAS3:System volt UL23 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
971 |  |  |  | HR970 (Lo-16bits)
972 | MEAS3:System volt UL23 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
973 |  |  |  | HR972 (Lo-16bits)
974 | MEAS3:System volt UL31 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
975 |  |  |  | HR974 (Lo-16bits)
976 | MEAS3:System volt UL31 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
977 |  |  |  | HR976 (Lo-16bits)
978 | MEAS3:System volt UL31 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
979 |  |  |  | HR978 (Lo-16bits)
980 | MEAS3:System volt UL1 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
981 |  |  |  | HR980 (Lo-16bits)
982 | MEAS3:System volt UL1 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
983 |  |  |  | HR982 (Lo-16bits)
984 | MEAS3:System volt UL1 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
985 |  |  |  | HR984 (Lo-16bits)
986 | MEAS3:System volt UL2 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
987 |  |  |  | HR986 (Lo-16bits)
988 | MEAS3:System volt UL2 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
989 |  |  |  | HR988 (Lo-16bits)
990 | MEAS3:System volt UL2 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
991 |  |  |  | HR990 (Lo-16bits)
992 | MEAS3:System volt UL3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
993 |  |  |  | HR992 (Lo-16bits)
994 | MEAS3:System volt UL3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
995 |  |  |  | HR994 (Lo-16bits)
996 | MEAS3:System volt UL3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
997 |  |  |  | HR996 (Lo-16bits)
998 | MEAS3:System volt U0 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
999 |  |  |  | HR998 (Lo-16bits)
1000 | MEAS3:System volt U0 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
1001 |  |  |  | HR1000 (Lo-16bits)
1002 | MEAS3:System volt U0 mag(%) | R | 2 | FLOAT [0...120] (Hi-16bits)
1003 |  |  |  | HR1002 (Lo-16bits)
1004 | MEAS3:System volt U0 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
1005 |  |  |  | HR1004 (Lo-16bits)
1006 | MEAS3:System volt U3 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1007 |  |  |  | HR1006 (Lo-16bits)
1008 | MEAS3:System volt U3 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
1009 |  |  |  | HR1008 (Lo-16bits)
1010 | MEAS3:System volt U3 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
1011 |  |  |  | HR1010 (Lo-16bits)
1012 | MEAS3:System volt U4 mag | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1013 |  |  |  | HR1012 (Lo-16bits)
1014 | MEAS3:System volt U4 mag(kV) | R | 2 | FLOAT [0...1000] (Hi-16bits)
1015 |  |  |  | HR1014 (Lo-16bits)
1016 | MEAS3:System volt U4 ang | R | 2 | FLOAT [-360...360] (Hi-16bits)
1017 |  |  |  | HR1016 (Lo-16bits)
1018 | MEAS3:System volt UL1 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
1019 |  |  |  | HR1018 (Lo-16bits)
1020 | MEAS3:System volt UL2 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
1021 |  |  |  | HR1020 (Lo-16bits)
1022 | MEAS3:System volt UL3 ang Ref | R | 2 | FLOAT [-360...360] (Hi-16bits)
1023 |  |  |  | HR1022 (Lo-16bits)
1024 | MEAS3:UL1 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
1025 |  |  |  | HR1024 (Lo-16bits)
1026 | MEAS3:UL1 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
1027 |  |  |  | HR1026 (Lo-16bits)
1028 | MEAS3:UL2 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
1029 |  |  |  | HR1028 (Lo-16bits)
1030 | MEAS3:UL2 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
1031 |  |  |  | HR1030 (Lo-16bits)
1032 | MEAS3:UL3 Amplitude THD | R | 2 | FLOAT [0...100] (Hi-16bits)
1033 |  |  |  | HR1032 (Lo-16bits)
1034 | MEAS3:UL3 Power THD | R | 2 | FLOAT [0...100] (Hi-16bits)
1035 |  |  |  | HR1034 (Lo-16bits)
1036 | MEAS3:U1 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1037 |  |  |  | HR1036 (Lo-16bits)
1038 | MEAS3:U1 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1039 |  |  |  | HR1038 (Lo-16bits)
1040 | MEAS3:U1 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1041 |  |  |  | HR1040 (Lo-16bits)
1042 | MEAS3:U1 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1043 |  |  |  | HR1042 (Lo-16bits)
1044 | MEAS3:U1 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1045 |  |  |  | HR1044 (Lo-16bits)
1046 | MEAS3:U1 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1047 |  |  |  | HR1046 (Lo-16bits)
1048 | MEAS3:U1 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1049 |  |  |  | HR1048 (Lo-16bits)
1050 | MEAS3:U1 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1051 |  |  |  | HR1050 (Lo-16bits)
1052 | MEAS3:U1 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1053 |  |  |  | HR1052 (Lo-16bits)
1054 | MEAS3:U1 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1055 |  |  |  | HR1054 (Lo-16bits)
1056 | MEAS3:U1 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1057 |  |  |  | HR1056 (Lo-16bits)
1058 | MEAS3:U1 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1059 |  |  |  | HR1058 (Lo-16bits)
1060 | MEAS3:U1 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1061 |  |  |  | HR1060 (Lo-16bits)
1062 | MEAS3:U1 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1063 |  |  |  | HR1062 (Lo-16bits)
1064 | MEAS3:U1 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1065 |  |  |  | HR1064 (Lo-16bits)
1066 | MEAS3:U1 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1067 |  |  |  | HR1066 (Lo-16bits)
1068 | MEAS3:U1 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1069 |  |  |  | HR1068 (Lo-16bits)
1070 | MEAS3:U1 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1071 |  |  |  | HR1070 (Lo-16bits)
1072 | MEAS3:U1 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1073 |  |  |  | HR1072 (Lo-16bits)
1074 | MEAS3:U1 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1075 |  |  |  | HR1074 (Lo-16bits)
1076 | MEAS3:U1 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1077 |  |  |  | HR1076 (Lo-16bits)
1078 | MEAS3:U1 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1079 |  |  |  | HR1078 (Lo-16bits)
1080 | MEAS3:U1 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1081 |  |  |  | HR1080 (Lo-16bits)
1082 | MEAS3:U1 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1083 |  |  |  | HR1082 (Lo-16bits)
1084 | MEAS3:U1 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1085 |  |  |  | HR1084 (Lo-16bits)
1086 | MEAS3:U1 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1087 |  |  |  | HR1086 (Lo-16bits)
1088 | MEAS3:U1 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1089 |  |  |  | HR1088 (Lo-16bits)
1090 | MEAS3:U1 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1091 |  |  |  | HR1090 (Lo-16bits)
1092 | MEAS3:U1 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1093 |  |  |  | HR1092 (Lo-16bits)
1094 | MEAS3:U1 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1095 |  |  |  | HR1094 (Lo-16bits)
1096 | MEAS3:U1 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1097 |  |  |  | HR1096 (Lo-16bits)
1098 | MEAS3:U2 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1099 |  |  |  | HR1098 (Lo-16bits)
1100 | MEAS3:U2 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1101 |  |  |  | HR1100 (Lo-16bits)
1102 | MEAS3:U2 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1103 |  |  |  | HR1102 (Lo-16bits)
1104 | MEAS3:U2 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1105 |  |  |  | HR1104 (Lo-16bits)
1106 | MEAS3:U2 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1107 |  |  |  | HR1106 (Lo-16bits)
1108 | MEAS3:U2 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1109 |  |  |  | HR1108 (Lo-16bits)
1110 | MEAS3:U2 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1111 |  |  |  | HR1110 (Lo-16bits)
1112 | MEAS3:U2 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1113 |  |  |  | HR1112 (Lo-16bits)
1114 | MEAS3:U2 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1115 |  |  |  | HR1114 (Lo-16bits)
1116 | MEAS3:U2 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1117 |  |  |  | HR1116 (Lo-16bits)
1118 | MEAS3:U2 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1119 |  |  |  | HR1118 (Lo-16bits)
1120 | MEAS3:U2 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1121 |  |  |  | HR1120 (Lo-16bits)
1122 | MEAS3:U2 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1123 |  |  |  | HR1122 (Lo-16bits)
1124 | MEAS3:U2 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1125 |  |  |  | HR1124 (Lo-16bits)
1126 | MEAS3:U2 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1127 |  |  |  | HR1126 (Lo-16bits)
1128 | MEAS3:U2 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1129 |  |  |  | HR1128 (Lo-16bits)
1130 | MEAS3:U2 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1131 |  |  |  | HR1130 (Lo-16bits)
1132 | MEAS3:U2 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1133 |  |  |  | HR1132 (Lo-16bits)
1134 | MEAS3:U2 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1135 |  |  |  | HR1134 (Lo-16bits)
1136 | MEAS3:U2 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1137 |  |  |  | HR1136 (Lo-16bits)
1138 | MEAS3:U2 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1139 |  |  |  | HR1138 (Lo-16bits)
1140 | MEAS3:U2 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1141 |  |  |  | HR1140 (Lo-16bits)
1142 | MEAS3:U2 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1143 |  |  |  | HR1142 (Lo-16bits)
1144 | MEAS3:U2 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1145 |  |  |  | HR1144 (Lo-16bits)
1146 | MEAS3:U2 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1147 |  |  |  | HR1146 (Lo-16bits)
1148 | MEAS3:U2 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1149 |  |  |  | HR1148 (Lo-16bits)
1150 | MEAS3:U2 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1151 |  |  |  | HR1150 (Lo-16bits)
1152 | MEAS3:U2 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1153 |  |  |  | HR1152 (Lo-16bits)
1154 | MEAS3:U2 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1155 |  |  |  | HR1154 (Lo-16bits)
1156 | MEAS3:U2 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1157 |  |  |  | HR1156 (Lo-16bits)
1158 | MEAS3:U2 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1159 |  |  |  | HR1158 (Lo-16bits)
1160 | MEAS3:U3 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1161 |  |  |  | HR1160 (Lo-16bits)
1162 | MEAS3:U3 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1163 |  |  |  | HR1162 (Lo-16bits)
1164 | MEAS3:U3 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1165 |  |  |  | HR1164 (Lo-16bits)
1166 | MEAS3:U3 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1167 |  |  |  | HR1166 (Lo-16bits)
1168 | MEAS3:U3 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1169 |  |  |  | HR1168 (Lo-16bits)
1170 | MEAS3:U3 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1171 |  |  |  | HR1170 (Lo-16bits)
1172 | MEAS3:U3 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1173 |  |  |  | HR1172 (Lo-16bits)
1174 | MEAS3:U3 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1175 |  |  |  | HR1174 (Lo-16bits)
1176 | MEAS3:U3 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1177 |  |  |  | HR1176 (Lo-16bits)
1178 | MEAS3:U3 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1179 |  |  |  | HR1178 (Lo-16bits)
1180 | MEAS3:U3 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1181 |  |  |  | HR1180 (Lo-16bits)
1182 | MEAS3:U3 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1183 |  |  |  | HR1182 (Lo-16bits)
1184 | MEAS3:U3 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1185 |  |  |  | HR1184 (Lo-16bits)
1186 | MEAS3:U3 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1187 |  |  |  | HR1186 (Lo-16bits)
1188 | MEAS3:U3 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1189 |  |  |  | HR1188 (Lo-16bits)
1190 | MEAS3:U3 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1191 |  |  |  | HR1190 (Lo-16bits)
1192 | MEAS3:U3 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1193 |  |  |  | HR1192 (Lo-16bits)
1194 | MEAS3:U3 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1195 |  |  |  | HR1194 (Lo-16bits)
1196 | MEAS3:U3 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1197 |  |  |  | HR1196 (Lo-16bits)
1198 | MEAS3:U3 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1199 |  |  |  | HR1198 (Lo-16bits)
1200 | MEAS3:U3 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1201 |  |  |  | HR1200 (Lo-16bits)
1202 | MEAS3:U3 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1203 |  |  |  | HR1202 (Lo-16bits)
1204 | MEAS3:U3 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1205 |  |  |  | HR1204 (Lo-16bits)
1206 | MEAS3:U3 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1207 |  |  |  | HR1206 (Lo-16bits)
1208 | MEAS3:U3 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1209 |  |  |  | HR1208 (Lo-16bits)
1210 | MEAS3:U3 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1211 |  |  |  | HR1210 (Lo-16bits)
1212 | MEAS3:U3 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1213 |  |  |  | HR1212 (Lo-16bits)
1214 | MEAS3:U3 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1215 |  |  |  | HR1214 (Lo-16bits)
1216 | MEAS3:U3 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1217 |  |  |  | HR1216 (Lo-16bits)
1218 | MEAS3:U3 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1219 |  |  |  | HR1218 (Lo-16bits)
1220 | MEAS3:U3 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1221 |  |  |  | HR1220 (Lo-16bits)
1222 | MEAS3:U4 Fund | R | 2 | FLOAT [0...100000] (Hi-16bits)
1223 |  |  |  | HR1222 (Lo-16bits)
1224 | MEAS3:U4 2.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1225 |  |  |  | HR1224 (Lo-16bits)
1226 | MEAS3:U4 3.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1227 |  |  |  | HR1226 (Lo-16bits)
1228 | MEAS3:U4 4.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1229 |  |  |  | HR1228 (Lo-16bits)
1230 | MEAS3:U4 5.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1231 |  |  |  | HR1230 (Lo-16bits)
1232 | MEAS3:U4 6.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1233 |  |  |  | HR1232 (Lo-16bits)
1234 | MEAS3:U4 7.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1235 |  |  |  | HR1234 (Lo-16bits)
1236 | MEAS3:U4 8.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1237 |  |  |  | HR1236 (Lo-16bits)
1238 | MEAS3:U4 9.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1239 |  |  |  | HR1238 (Lo-16bits)
1240 | MEAS3:U4 10.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1241 |  |  |  | HR1240 (Lo-16bits)
1242 | MEAS3:U4 11.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1243 |  |  |  | HR1242 (Lo-16bits)
1244 | MEAS3:U4 12.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1245 |  |  |  | HR1244 (Lo-16bits)
1246 | MEAS3:U4 13.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1247 |  |  |  | HR1246 (Lo-16bits)
1248 | MEAS3:U4 14.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1249 |  |  |  | HR1248 (Lo-16bits)
1250 | MEAS3:U4 15.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1251 |  |  |  | HR1250 (Lo-16bits)
1252 | MEAS3:U4 16.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1253 |  |  |  | HR1252 (Lo-16bits)
1254 | MEAS3:U4 17.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1255 |  |  |  | HR1254 (Lo-16bits)
1256 | MEAS3:U4 18.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1257 |  |  |  | HR1256 (Lo-16bits)
1258 | MEAS3:U4 19.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1259 |  |  |  | HR1258 (Lo-16bits)
1260 | MEAS3:U4 20.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1261 |  |  |  | HR1260 (Lo-16bits)
1262 | MEAS3:U4 21.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1263 |  |  |  | HR1262 (Lo-16bits)
1264 | MEAS3:U4 22.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1265 |  |  |  | HR1264 (Lo-16bits)
1266 | MEAS3:U4 23.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1267 |  |  |  | HR1266 (Lo-16bits)
1268 | MEAS3:U4 24.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1269 |  |  |  | HR1268 (Lo-16bits)
1270 | MEAS3:U4 25.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1271 |  |  |  | HR1270 (Lo-16bits)
1272 | MEAS3:U4 26.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1273 |  |  |  | HR1272 (Lo-16bits)
1274 | MEAS3:U4 27.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1275 |  |  |  | HR1274 (Lo-16bits)
1276 | MEAS3:U4 28.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1277 |  |  |  | HR1276 (Lo-16bits)
1278 | MEAS3:U4 29.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1279 |  |  |  | HR1278 (Lo-16bits)
1280 | MEAS3:U4 30.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1281 |  |  |  | HR1280 (Lo-16bits)
1282 | MEAS3:U4 31.harm | R | 2 | FLOAT [0...100000] (Hi-16bits)
1283 |  |  |  | HR1282 (Lo-16bits)
1284 | IMERX:IL1 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1285 |  |  |  | HR1284 (Lo-16bits)
1286 | IMERX:IL1 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1287 |  |  |  | HR1286 (Lo-16bits)
1288 | IMERX:IL2 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1289 |  |  |  | HR1288 (Lo-16bits)
1290 | IMERX:IL2 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1291 |  |  |  | HR1290 (Lo-16bits)
1292 | IMERX:IL3 Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1293 |  |  |  | HR1292 (Lo-16bits)
1294 | IMERX:IL3 Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1295 |  |  |  | HR1294 (Lo-16bits)
1296 | IMERX:Pos.seq. Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1297 |  |  |  | HR1296 (Lo-16bits)
1298 | IMERX:Pos.Seq. Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1299 |  |  |  | HR1298 (Lo-16bits)
1300 | IMERX:I01 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1301 |  |  |  | HR1300 (Lo-16bits)
1302 | IMERX:I01 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1303 |  |  |  | HR1302 (Lo-16bits)
1304 | IMERX:I02 Residual Resistive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1305 |  |  |  | HR1304 (Lo-16bits)
1306 | IMERX:I02 Residual Reactive Current Pri. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1307 |  |  |  | HR1306 (Lo-16bits)
1308 | IMERX:I01 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1309 |  |  |  | HR1308 (Lo-16bits)
1310 | IMERX:I01 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1311 |  |  |  | HR1310 (Lo-16bits)
1312 | IMERX:I02 Residual Resistive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1313 |  |  |  | HR1312 (Lo-16bits)
1314 | IMERX:I02 Residual Reactive Current Sec. | R | 2 | FLOAT [-100000...100000] (Hi-16bits)
1315 |  |  |  | HR1314 (Lo-16bits)
1316 | POW1:Export Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1317 |  |  |  | HR1316 (Lo-16bits)
1318 | POW1:Export Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1319 |  |  |  | HR1318 (Lo-16bits)
1320 | POW1:Import Active Energy (P) MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1321 |  |  |  | HR1320 (Lo-16bits)
1322 | POW1:Import Active Energy (P) kWh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1323 |  |  |  | HR1322 (Lo-16bits)
1324 | POW1:Active Energy (P) Export/Import balance MWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1325 |  |  |  | HR1324 (Lo-16bits)
1326 | POW1:Active Energy (P) Export/Import balance kWh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1327 |  |  |  | HR1326 (Lo-16bits)
1328 | POW1:Exported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1329 |  |  |  | HR1328 (Lo-16bits)
1330 | POW1:Exported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1331 |  |  |  | HR1330 (Lo-16bits)
1332 | POW1:Imported (Q) while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1333 |  |  |  | HR1332 (Lo-16bits)
1334 | POW1:Imported (Q) while Export (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1335 |  |  |  | HR1334 (Lo-16bits)
1336 | POW1:Reactive Energy (Q) balance while Export (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1337 |  |  |  | HR1336 (Lo-16bits)
1338 | POW1:Reactive Energy (Q) balance while Export (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1339 |  |  |  | HR1338 (Lo-16bits)
1340 | POW1:Exported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1341 |  |  |  | HR1340 (Lo-16bits)
1342 | POW1:Exported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1343 |  |  |  | HR1342 (Lo-16bits)
1344 | POW1:Imported (Q) while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1345 |  |  |  | HR1344 (Lo-16bits)
1346 | POW1:Imported (Q) while Import (P) kVarh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1347 |  |  |  | HR1346 (Lo-16bits)
1348 | POW1:Reactive Energy (Q) balance while Import (P) MVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1349 |  |  |  | HR1348 (Lo-16bits)
1350 | POW1:Reactive Energy (Q) balance while Import (P) kVarh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1351 |  |  |  | HR1350 (Lo-16bits)
1352 | POW1:Apparent Energy (S) while Export (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1353 |  |  |  | HR1352 (Lo-16bits)
1354 | POW1:Apparent Energy (S) while Export (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1355 |  |  |  | HR1354 (Lo-16bits)
1356 | POW1:Apparent Energy (S) while Import (P) MVAh | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1357 |  |  |  | HR1356 (Lo-16bits)
1358 | POW1:Apparent Energy (S) while Import (P) kVAh | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1359 |  |  |  | HR1358 (Lo-16bits)
1360 | POW1:Apparent Energy (S) Net | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1361 |  |  |  | HR1360 (Lo-16bits)
1362 | POW1:Real Energy (P) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1363 |  |  |  | HR1362 (Lo-16bits)
1364 | POW1:Reactive Energy (Q) Net | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1365 |  |  |  | HR1364 (Lo-16bits)
1366 | POW1:Real Energy (P) Supply (Default supply direction towards busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1367 |  |  |  | HR1366 (Lo-16bits)
1368 | POW1:Reactive Energy (Q) Supply (Default supply direction towards busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1369 |  |  |  | HR1368 (Lo-16bits)
1370 | POW1:Real Energy (P) Demand (Default demand direction from busbar) | RW | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1371 |  |  |  | HR1370 (Lo-16bits)
1372 | POW1:Reactive Energy (Q) Demand (Default demand direction from busbar) | R | 2 | INT32 [-2147483647...2147483647] (Hi-16bits)
1373 |  |  |  | HR1372 (Lo-16bits)
1374 | POW1:Reset 3ph Energies | RW | 1 | 0=-;1=Reset
1375 | POW1:POW1 3PH Apparent power (S) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1376 |  |  |  | HR1375 (Lo-16bits)
1377 | POW1:POW1 3PH Apparent power (S MVA) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1378 |  |  |  | HR1377 (Lo-16bits)
1379 | POW1:POW1 3PH Active power (P) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1380 |  |  |  | HR1379 (Lo-16bits)
1381 | POW1:POW1 3PH Active power (P MW) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1382 |  |  |  | HR1381 (Lo-16bits)
1383 | POW1:POW1 3PH Reactive power (Q) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1384 |  |  |  | HR1383 (Lo-16bits)
1385 | POW1:POW1 3PH Reactive power (QMVar) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1386 |  |  |  | HR1385 (Lo-16bits)
1387 | POW1:POW1 3PH Tan(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1388 |  |  |  | HR1387 (Lo-16bits)
1389 | POW1:POW1 3PH Cos(phi) | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1390 |  |  |  | HR1389 (Lo-16bits)
1391 | POW1:3PH PF | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1392 |  |  |  | HR1391 (Lo-16bits)
1393 | ASC1:Curve1 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1394 |  |  |  | HR1393 (Lo-16bits)
1395 | ASC1:Curve1 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1396 |  |  |  | HR1395 (Lo-16bits)
1397 | ASC1:Curve2 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1398 |  |  |  | HR1397 (Lo-16bits)
1399 | ASC1:Curve2 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1400 |  |  |  | HR1399 (Lo-16bits)
1401 | ASC1:Curve3 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1402 |  |  |  | HR1401 (Lo-16bits)
1403 | ASC1:Curve3 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1404 |  |  |  | HR1403 (Lo-16bits)
1405 | ASC1:Curve4 Input | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1406 |  |  |  | HR1405 (Lo-16bits)
1407 | ASC1:Curve4 Output | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1408 |  |  |  | HR1407 (Lo-16bits)
1409 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1410 |  |  |  | HR1409 (Lo-16bits)
1411 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1412 |  |  |  | HR1411 (Lo-16bits)
1413 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1414 |  |  |  | HR1413 (Lo-16bits)
1415 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1416 |  |  |  | HR1415 (Lo-16bits)
1417 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1418 |  |  |  | HR1417 (Lo-16bits)
1419 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1420 |  |  |  | HR1419 (Lo-16bits)
1421 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1422 |  |  |  | HR1421 (Lo-16bits)
1423 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1424 |  |  |  | HR1423 (Lo-16bits)
1425 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1426 |  |  |  | HR1425 (Lo-16bits)
1427 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1428 |  |  |  | HR1427 (Lo-16bits)
1429 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1430 |  |  |  | HR1429 (Lo-16bits)
1431 | FLTREG:Recorded fault value | R | 2 | FLOAT [-1000000...1000000] (Hi-16bits)
1432 |  |  |  | HR1431 (Lo-16bits)
1433 | M1CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1434 |  |  |  | HR1433 (Lo-16bits)
1435 | M1CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1436 |  |  |  | HR1435 (Lo-16bits)
1437 | M1CT2:I01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1438 |  |  |  | HR1437 (Lo-16bits)
1439 | M1CT2:I01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1440 |  |  |  | HR1439 (Lo-16bits)
1441 | M1CT3:I02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1442 |  |  |  | HR1441 (Lo-16bits)
1443 | M1CT3:I02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1444 |  |  |  | HR1443 (Lo-16bits)
1445 | M2CT1:Phase CT primary | R(W) | 2 | FLOAT [1...25000] (Hi-16bits)
1446 |  |  |  | HR1445 (Lo-16bits)
1447 | M2CT1:Phase CT secondary | R(W) | 2 | FLOAT [0.2...20] (Hi-16bits)
1448 |  |  |  | HR1447 (Lo-16bits)
1449 | M2CT2:I''01 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1450 |  |  |  | HR1449 (Lo-16bits)
1451 | M2CT2:I''01 CT secondary | R(W) | 2 | FLOAT [0.1...10] (Hi-16bits)
1452 |  |  |  | HR1451 (Lo-16bits)
1453 | M2CT3:I''02 CT primary | R(W) | 2 | FLOAT [0.2...25000] (Hi-16bits)
1454 |  |  |  | HR1453 (Lo-16bits)
1455 | M2CT3:I''02 CT secondary | R(W) | 2 | FLOAT [0.001...10] (Hi-16bits)
1456 |  |  |  | HR1455 (Lo-16bits)
1457 | M1VT1:VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1458 |  |  |  | HR1457 (Lo-16bits)
1459 | M1VT1:VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1460 |  |  |  | HR1459 (Lo-16bits)
1461 | M1VT1:U3 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1462 |  |  |  | HR1461 (Lo-16bits)
1463 | M1VT1:U3 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1464 |  |  |  | HR1463 (Lo-16bits)
1465 | M1VT1:U4 Res/SS VT primary | R(W) | 2 | FLOAT [1...1000000] (Hi-16bits)
1466 |  |  |  | HR1465 (Lo-16bits)
1467 | M1VT1:U4 Res/SS VT secondary | R(W) | 2 | FLOAT [0.2...400] (Hi-16bits)
1468 |  |  |  | HR1467 (Lo-16bits)
1469 | FREQS:f atm. Protections (when not measurable returns to nominal) | R | 2 | FLOAT [0...75] (Hi-16bits)
1470 |  |  |  | HR1469 (Lo-16bits)
1471 | FREQS:f atm. Display (when not measurable is 0Hz) | R | 2 | FLOAT [0...75] (Hi-16bits)
1472 |  |  |  | HR1471 (Lo-16bits)
1473 | FREQS:SS1.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1474 |  |  |  | HR1473 (Lo-16bits)
1475 | FREQS:SS2.meas.frqs | R | 2 | FLOAT [0...75] (Hi-16bits)
1476 |  |  |  | HR1475 (Lo-16bits)
1477 | DIGI:DIs (cpu) | R | 2 | 0b=DI1;1b=DI2;2b=DI3; (Hi-16bits)
1478 |  |  |  | HR1477 (Lo-16bits)
1479 | DIGI:DIs (input option 1) | R | 2 | 0b=DI4;1b=DI5;2b=DI6;3b=DI7;4b=DI8;5b=DI9;6b=DI10;7b=DI11 (Hi-16bits)
1480 |  |  |  | HR1479 (Lo-16bits)
1481 | DIGI:DIs (input option 2) | R | 2 | 0b=DI12;1b=DI13;2b=DI14;3b=DI15;4b=DI16;5b=DI17;6b=DI18;7b=DI19 (Hi-16bits)
1482 |  |  |  | HR1481 (Lo-16bits)
1483 | DIGI:DIs (input option 3) | R | 2 | 0b=DI20;1b=DI21;2b=DI22;3b=DI23;4b=DI24;5b=DI25;6b=DI26;7b=DI27 (Hi-16bits)
1484 |  |  |  | HR1483 (Lo-16bits)
1485 | DIGI:DIs (input option 4) | R | 2 | 0b=D28;1b=DI29;2b=DI30;3b=DI31;4b=DI32;5b=DI33;6b=DI34;7b=DI35 (Hi-16bits)
1486 |  |  |  | HR1485 (Lo-16bits)
1487 | DIGI:DIs (input option 5) | R | 2 | 0b=DI36;1b=DI37;2b=DI38;3b=DI39;4b=DI40;5b=DI41;6b=DI42;7b=DI43 (Hi-16bits)
1488 |  |  |  | HR1487 (Lo-16bits)
1489 | DIGI:DIs (input option 6) | R | 2 | 0b=DI44;1b=DI45;2b=DI46;3b=DI47;4b=DI48;5b=DI49;6b=DI50;7b=DI51 (Hi-16bits)
1490 |  |  |  | HR1489 (Lo-16bits)
1491 | DIGI:Dis 1-32 | R | 2 | 0b=DI1;1b=DI2;2b=DI3;3b=DI4;4b=DI5;5b=DI6;6b=DI7;7b=DI8;8b=DI9;9b=DI10;10b=DI11;11b=DI12;12b=DI13;13b=DI14;14b=DI15;15b=DI16;16b=DI17;17b=DI18;18b=DI19;19b=DI20;20b=DI21;21b=DI22;22b=DI23;23b=DI24;24b=DI25;25b=DI26;26b=DI27;27b=D28;28b=DI29;29b=DI30;30b=DI31;31b=DI32 (Hi-16bits)
1492 |  |  |  | HR1491 (Lo-16bits)
1493 | DIGI:Dis 33-64 | R | 2 | 0b=DI33;1b=DI34;2b=DI35;3b=DI36;4b=DI37;5b=DI38;6b=DI39;7b=DI40;8b=DI41;9b=DI42;10b=DI43;11b=DI44;12b=DI45;13b=DI46;14b=DI47;15b=DI48;16b=DI49;17b=DI50;18b=DI51 (Hi-16bits)
1494 |  |  |  | HR1493 (Lo-16bits)
1495 | DIGI:DI1 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1496 |  |  |  | HR1495 (Lo-16bits)
1497 | DIGI:DI1 Counter Clear | RW | 1 | 0=-;1=Clear
1498 | DIGI:DI2 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1499 |  |  |  | HR1498 (Lo-16bits)
1500 | DIGI:DI2 Counter Clear | RW | 1 | 0=-;1=Clear
1501 | DIGI:DI3 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1502 |  |  |  | HR1501 (Lo-16bits)
1503 | DIGI:DI3 Counter Clear | RW | 1 | 0=-;1=Clear
1504 | DIGI:DI4 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1505 |  |  |  | HR1504 (Lo-16bits)
1506 | DIGI:DI4 Counter Clear | RW | 1 | 0=-;1=Clear
1507 | DIGI:DI5 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1508 |  |  |  | HR1507 (Lo-16bits)
1509 | DIGI:DI5 Counter Clear | RW | 1 | 0=-;1=Clear
1510 | DIGI:DI6 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1511 |  |  |  | HR1510 (Lo-16bits)
1512 | DIGI:DI6 Counter Clear | RW | 1 | 0=-;1=Clear
1513 | DIGI:DI7 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1514 |  |  |  | HR1513 (Lo-16bits)
1515 | DIGI:DI7 Counter Clear | RW | 1 | 0=-;1=Clear
1516 | DIGI:DI8 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1517 |  |  |  | HR1516 (Lo-16bits)
1518 | DIGI:DI8 Counter Clear | RW | 1 | 0=-;1=Clear
1519 | DIGI:DI9 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1520 |  |  |  | HR1519 (Lo-16bits)
1521 | DIGI:DI9 Counter Clear | RW | 1 | 0=-;1=Clear
1522 | DIGI:DI10 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1523 |  |  |  | HR1522 (Lo-16bits)
1524 | DIGI:DI10 Counter Clear | RW | 1 | 0=-;1=Clear
1525 | DIGI:DI11 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1526 |  |  |  | HR1525 (Lo-16bits)
1527 | DIGI:DI11 Counter Clear | RW | 1 | 0=-;1=Clear
1528 | DIGI:DI12 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1529 |  |  |  | HR1528 (Lo-16bits)
1530 | DIGI:DI12 Counter Clear | RW | 1 | 0=-;1=Clear
1531 | DIGI:DI13 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1532 |  |  |  | HR1531 (Lo-16bits)
1533 | DIGI:DI13 Counter Clear | RW | 1 | 0=-;1=Clear
1534 | DIGI:DI14 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1535 |  |  |  | HR1534 (Lo-16bits)
1536 | DIGI:DI14 Counter Clear | RW | 1 | 0=-;1=Clear
1537 | DIGI:DI15 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1538 |  |  |  | HR1537 (Lo-16bits)
1539 | DIGI:DI15 Counter Clear | RW | 1 | 0=-;1=Clear
1540 | DIGI:DI16 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1541 |  |  |  | HR1540 (Lo-16bits)
1542 | DIGI:DI16 Counter Clear | RW | 1 | 0=-;1=Clear
1543 | DIGI:DI17 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1544 |  |  |  | HR1543 (Lo-16bits)
1545 | DIGI:DI17 Counter Clear | RW | 1 | 0=-;1=Clear
1546 | DIGI:DI18 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1547 |  |  |  | HR1546 (Lo-16bits)
1548 | DIGI:DI18 Counter Clear | RW | 1 | 0=-;1=Clear
1549 | DIGI:DI19 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1550 |  |  |  | HR1549 (Lo-16bits)
1551 | DIGI:DI19 Counter Clear | RW | 1 | 0=-;1=Clear
1552 | DIGI:DI20 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1553 |  |  |  | HR1552 (Lo-16bits)
1554 | DIGI:DI20 Counter Clear | RW | 1 | 0=-;1=Clear
1555 | DIGI:DI21 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1556 |  |  |  | HR1555 (Lo-16bits)
1557 | DIGI:DI21 Counter Clear | RW | 1 | 0=-;1=Clear
1558 | DIGI:DI22 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1559 |  |  |  | HR1558 (Lo-16bits)
1560 | DIGI:DI22 Counter Clear | RW | 1 | 0=-;1=Clear
1561 | DIGI:DI23 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1562 |  |  |  | HR1561 (Lo-16bits)
1563 | DIGI:DI23 Counter Clear | RW | 1 | 0=-;1=Clear
1564 | DIGI:DI24 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1565 |  |  |  | HR1564 (Lo-16bits)
1566 | DIGI:DI24 Counter Clear | RW | 1 | 0=-;1=Clear
1567 | DIGI:DI25 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1568 |  |  |  | HR1567 (Lo-16bits)
1569 | DIGI:DI25 Counter Clear | RW | 1 | 0=-;1=Clear
1570 | DIGI:DI26 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1571 |  |  |  | HR1570 (Lo-16bits)
1572 | DIGI:DI26 Counter Clear | RW | 1 | 0=-;1=Clear
1573 | DIGI:DI27 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1574 |  |  |  | HR1573 (Lo-16bits)
1575 | DIGI:DI27 Counter Clear | RW | 1 | 0=-;1=Clear
1576 | DIGI:DI28 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1577 |  |  |  | HR1576 (Lo-16bits)
1578 | DIGI:DI28 Counter Clear | RW | 1 | 0=-;1=Clear
1579 | DIGI:DI29 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1580 |  |  |  | HR1579 (Lo-16bits)
1581 | DIGI:DI29 Counter Clear | RW | 1 | 0=-;1=Clear
1582 | DIGI:DI30 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1583 |  |  |  | HR1582 (Lo-16bits)
1584 | DIGI:DI30 Counter Clear | RW | 1 | 0=-;1=Clear
1585 | DIGI:DI31 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1586 |  |  |  | HR1585 (Lo-16bits)
1587 | DIGI:DI31 Counter Clear | RW | 1 | 0=-;1=Clear
1588 | DIGI:DI32 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1589 |  |  |  | HR1588 (Lo-16bits)
1590 | DIGI:DI32 Counter Clear | RW | 1 | 0=-;1=Clear
1591 | DIGI:DI33 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1592 |  |  |  | HR1591 (Lo-16bits)
1593 | DIGI:DI33 Counter Clear | RW | 1 | 0=-;1=Clear
1594 | DIGI:DI34 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1595 |  |  |  | HR1594 (Lo-16bits)
1596 | DIGI:DI34 Counter Clear | RW | 1 | 0=-;1=Clear
1597 | DIGI:DI35 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1598 |  |  |  | HR1597 (Lo-16bits)
1599 | DIGI:DI35 Counter Clear | RW | 1 | 0=-;1=Clear
1600 | DIGI:DI36 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1601 |  |  |  | HR1600 (Lo-16bits)
1602 | DIGI:DI36 Counter Clear | RW | 1 | 0=-;1=Clear
1603 | DIGI:DI37 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1604 |  |  |  | HR1603 (Lo-16bits)
1605 | DIGI:DI37 Counter Clear | RW | 1 | 0=-;1=Clear
1606 | DIGI:DI38 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1607 |  |  |  | HR1606 (Lo-16bits)
1608 | DIGI:DI38 Counter Clear | RW | 1 | 0=-;1=Clear
1609 | DIGI:DI39 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1610 |  |  |  | HR1609 (Lo-16bits)
1611 | DIGI:DI39 Counter Clear | RW | 1 | 0=-;1=Clear
1612 | DIGI:DI40 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1613 |  |  |  | HR1612 (Lo-16bits)
1614 | DIGI:DI40 Counter Clear | RW | 1 | 0=-;1=Clear
1615 | DIGI:DI41 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1616 |  |  |  | HR1615 (Lo-16bits)
1617 | DIGI:DI41 Counter Clear | RW | 1 | 0=-;1=Clear
1618 | DIGI:DI42 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1619 |  |  |  | HR1618 (Lo-16bits)
1620 | DIGI:DI42 Counter Clear | RW | 1 | 0=-;1=Clear
1621 | DIGI:DI43 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1622 |  |  |  | HR1621 (Lo-16bits)
1623 | DIGI:DI43 Counter Clear | RW | 1 | 0=-;1=Clear
1624 | DIGI:DI44 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1625 |  |  |  | HR1624 (Lo-16bits)
1626 | DIGI:DI44 Counter Clear | RW | 1 | 0=-;1=Clear
1627 | DIGI:DI45 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1628 |  |  |  | HR1627 (Lo-16bits)
1629 | DIGI:DI45 Counter Clear | RW | 1 | 0=-;1=Clear
1630 | DIGI:DI46 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1631 |  |  |  | HR1630 (Lo-16bits)
1632 | DIGI:DI46 Counter Clear | RW | 1 | 0=-;1=Clear
1633 | DIGI:DI47 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1634 |  |  |  | HR1633 (Lo-16bits)
1635 | DIGI:DI47 Counter Clear | RW | 1 | 0=-;1=Clear
1636 | DIGI:DI48 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1637 |  |  |  | HR1636 (Lo-16bits)
1638 | DIGI:DI48 Counter Clear | RW | 1 | 0=-;1=Clear
1639 | DIGI:DI49 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1640 |  |  |  | HR1639 (Lo-16bits)
1641 | DIGI:DI49 Counter Clear | RW | 1 | 0=-;1=Clear
1642 | DIGI:DI50 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1643 |  |  |  | HR1642 (Lo-16bits)
1644 | DIGI:DI50 Counter Clear | RW | 1 | 0=-;1=Clear
1645 | DIGI:DI51 Counter | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1646 |  |  |  | HR1645 (Lo-16bits)
1647 | DIGI:DI51 Counter Clear | RW | 1 | 0=-;1=Clear
1648 | RELE:Outputs status | R | 2 | 0b=O1;1b=O2;2b=O3;3b=O4;4b=O5;5b=O6;6b=O7;7b=O8;8b=O9;9b=O10;10b=O11;11b=O12;12b=O13;13b=O14;14b=O15 (Hi-16bits)
1649 |  |  |  | HR1648 (Lo-16bits)
1650 | SGS:Active setting group | R | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8
1651 | SGS:Force SG | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1652 | SGS:Force SG change | RW | 1 | 0=Disabled;1=Enabled
1653 | SGS:Used setting groups | RW | 1 | 0=SG1;1=SG1...2;2=SG1...3;3=SG1...4;4=SG1...5;5=SG1...6;6=SG1...7;7=SG1...8
1654 | SGS:Remote SG change | RW | 1 | 0=none;1=SG1;2=SG2;3=SG3;4=SG4;5=SG5;6=SG6;7=SG7;8=SG8
1655 | CTRL:Local/Remote status | R | 1 | 0=Remote;1=Local
1656 | DEV:Serial number | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1657 |  |  |  | HR1656 (Lo-16bits)
1658 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1659 |  |  |  | HR1658 (Lo-16bits)
1660 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1661 |  |  |  | HR1660 (Lo-16bits)
1662 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1663 |  |  |  | HR1662 (Lo-16bits)
1664 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1665 |  |  |  | HR1664 (Lo-16bits)
1666 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1667 |  |  |  | HR1666 (Lo-16bits)
1668 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1669 |  |  |  | HR1668 (Lo-16bits)
1670 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1671 |  |  |  | HR1670 (Lo-16bits)
1672 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1673 |  |  |  | HR1672 (Lo-16bits)
1674 | DEV:SW version | R | 2 | STRING [...32] (Hi-16bits)
1675 |  |  |  | HR1674 (Lo-16bits)
1676 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1677 |  |  |  | HR1676 (Lo-16bits)
1678 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1679 |  |  |  | HR1678 (Lo-16bits)
1680 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1681 |  |  |  | HR1680 (Lo-16bits)
1682 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1683 |  |  |  | HR1682 (Lo-16bits)
1684 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1685 |  |  |  | HR1684 (Lo-16bits)
1686 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1687 |  |  |  | HR1686 (Lo-16bits)
1688 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1689 |  |  |  | HR1688 (Lo-16bits)
1690 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1691 |  |  |  | HR1690 (Lo-16bits)
1692 | DEV:HW conf. | R | 2 | STRING [0...32] (Hi-16bits)
1693 |  |  |  | HR1692 (Lo-16bits)
1694 | DIAG:Configuration changed | R | 2 | UINT32 [0...4294967295] (Hi-16bits)
1695 |  |  |  | HR1694 (Lo-16bits)
1696 | MBTCP:Enable mapped setting value modification through Modbus | RW | 1 | 0=Disabled;1=Enabled
1697 | MBIO:MBIO ModA Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1698 |  |  |  | HR1697 (Lo-16bits)
1699 | MBIO:MBIO ModA Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1700 |  |  |  | HR1699 (Lo-16bits)
1701 | MBIO:MBIO ModA Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1702 |  |  |  | HR1701 (Lo-16bits)
1703 | MBIO:MBIO ModA Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1704 |  |  |  | HR1703 (Lo-16bits)
1705 | MBIO:MBIO ModA Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1706 |  |  |  | HR1705 (Lo-16bits)
1707 | MBIO:MBIO ModA Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1708 |  |  |  | HR1707 (Lo-16bits)
1709 | MBIO:MBIO ModA Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1710 |  |  |  | HR1709 (Lo-16bits)
1711 | MBIO:MBIO ModA Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1712 |  |  |  | HR1711 (Lo-16bits)
1713 | MBIO:MBIO ModB Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1714 |  |  |  | HR1713 (Lo-16bits)
1715 | MBIO:MBIO ModB Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1716 |  |  |  | HR1715 (Lo-16bits)
1717 | MBIO:MBIO ModB Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1718 |  |  |  | HR1717 (Lo-16bits)
1719 | MBIO:MBIO ModB Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1720 |  |  |  | HR1719 (Lo-16bits)
1721 | MBIO:MBIO ModB Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1722 |  |  |  | HR1721 (Lo-16bits)
1723 | MBIO:MBIO ModB Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1724 |  |  |  | HR1723 (Lo-16bits)
1725 | MBIO:MBIO ModB Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1726 |  |  |  | HR1725 (Lo-16bits)
1727 | MBIO:MBIO ModB Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1728 |  |  |  | HR1727 (Lo-16bits)
1729 | MBIO:MBIO ModC Ch1 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1730 |  |  |  | HR1729 (Lo-16bits)
1731 | MBIO:MBIO ModC Ch2 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1732 |  |  |  | HR1731 (Lo-16bits)
1733 | MBIO:MBIO ModC Ch3 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1734 |  |  |  | HR1733 (Lo-16bits)
1735 | MBIO:MBIO ModC Ch4 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1736 |  |  |  | HR1735 (Lo-16bits)
1737 | MBIO:MBIO ModC Ch5 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1738 |  |  |  | HR1737 (Lo-16bits)
1739 | MBIO:MBIO ModC Ch6 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1740 |  |  |  | HR1739 (Lo-16bits)
1741 | MBIO:MBIO ModC Ch7 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1742 |  |  |  | HR1741 (Lo-16bits)
1743 | MBIO:MBIO ModC Ch8 Invalid | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
1744 |  |  |  | HR1743 (Lo-16bits)
1745 | LOGIC:Reset Latches | RW | 1 | 0=-;1=Reset
1746 | LOGIC1:Logic out 1-32 | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
1747 |  |  |  | HR1746 (Lo-16bits)
1748 | NOC1:I> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1749 | NOC1:I> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1750 | NOC1:I> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1751 | NOC1:I> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1752 | NOC1:I> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1753 | NOC1:I> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1754 |  |  |  | HR1753 (Lo-16bits)
1755 | NOC1:I> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1756 |  |  |  | HR1755 (Lo-16bits)
1757 | NOC1:I> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1758 |  |  |  | HR1757 (Lo-16bits)
1759 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1760 |  |  |  | HR1759 (Lo-16bits)
1761 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1762 |  |  |  | HR1761 (Lo-16bits)
1763 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1764 |  |  |  | HR1763 (Lo-16bits)
1765 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1766 |  |  |  | HR1765 (Lo-16bits)
1767 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1768 |  |  |  | HR1767 (Lo-16bits)
1769 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1770 |  |  |  | HR1769 (Lo-16bits)
1771 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1772 |  |  |  | HR1771 (Lo-16bits)
1773 | NOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1774 |  |  |  | HR1773 (Lo-16bits)
1775 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1776 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1777 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1778 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1779 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1780 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1781 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1782 | NOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
1783 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1784 |  |  |  | HR1783 (Lo-16bits)
1785 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1786 |  |  |  | HR1785 (Lo-16bits)
1787 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1788 |  |  |  | HR1787 (Lo-16bits)
1789 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1790 |  |  |  | HR1789 (Lo-16bits)
1791 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1792 |  |  |  | HR1791 (Lo-16bits)
1793 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1794 |  |  |  | HR1793 (Lo-16bits)
1795 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1796 |  |  |  | HR1795 (Lo-16bits)
1797 | NOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
1798 |  |  |  | HR1797 (Lo-16bits)
1799 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1800 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1801 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1802 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1803 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1804 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1805 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1806 | NOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
1807 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1808 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1809 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1810 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1811 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1812 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1813 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1814 | NOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1815 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1816 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1817 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1818 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1819 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1820 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1821 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1822 | NOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1823 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1824 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1825 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1826 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1827 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1828 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1829 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1830 | NOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
1831 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1832 |  |  |  | HR1831 (Lo-16bits)
1833 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1834 |  |  |  | HR1833 (Lo-16bits)
1835 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1836 |  |  |  | HR1835 (Lo-16bits)
1837 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1838 |  |  |  | HR1837 (Lo-16bits)
1839 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1840 |  |  |  | HR1839 (Lo-16bits)
1841 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1842 |  |  |  | HR1841 (Lo-16bits)
1843 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1844 |  |  |  | HR1843 (Lo-16bits)
1845 | NOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
1846 |  |  |  | HR1845 (Lo-16bits)
1847 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1848 |  |  |  | HR1847 (Lo-16bits)
1849 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1850 |  |  |  | HR1849 (Lo-16bits)
1851 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1852 |  |  |  | HR1851 (Lo-16bits)
1853 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1854 |  |  |  | HR1853 (Lo-16bits)
1855 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1856 |  |  |  | HR1855 (Lo-16bits)
1857 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1858 |  |  |  | HR1857 (Lo-16bits)
1859 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1860 |  |  |  | HR1859 (Lo-16bits)
1861 | NOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1862 |  |  |  | HR1861 (Lo-16bits)
1863 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1864 |  |  |  | HR1863 (Lo-16bits)
1865 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1866 |  |  |  | HR1865 (Lo-16bits)
1867 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1868 |  |  |  | HR1867 (Lo-16bits)
1869 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1870 |  |  |  | HR1869 (Lo-16bits)
1871 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1872 |  |  |  | HR1871 (Lo-16bits)
1873 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1874 |  |  |  | HR1873 (Lo-16bits)
1875 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1876 |  |  |  | HR1875 (Lo-16bits)
1877 | NOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1878 |  |  |  | HR1877 (Lo-16bits)
1879 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1880 |  |  |  | HR1879 (Lo-16bits)
1881 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1882 |  |  |  | HR1881 (Lo-16bits)
1883 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1884 |  |  |  | HR1883 (Lo-16bits)
1885 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1886 |  |  |  | HR1885 (Lo-16bits)
1887 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1888 |  |  |  | HR1887 (Lo-16bits)
1889 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1890 |  |  |  | HR1889 (Lo-16bits)
1891 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1892 |  |  |  | HR1891 (Lo-16bits)
1893 | NOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
1894 |  |  |  | HR1893 (Lo-16bits)
1895 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1896 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1897 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1898 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1899 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1900 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1901 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1902 | NOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
1903 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1904 |  |  |  | HR1903 (Lo-16bits)
1905 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1906 |  |  |  | HR1905 (Lo-16bits)
1907 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1908 |  |  |  | HR1907 (Lo-16bits)
1909 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1910 |  |  |  | HR1909 (Lo-16bits)
1911 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1912 |  |  |  | HR1911 (Lo-16bits)
1913 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1914 |  |  |  | HR1913 (Lo-16bits)
1915 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1916 |  |  |  | HR1915 (Lo-16bits)
1917 | NOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1918 |  |  |  | HR1917 (Lo-16bits)
1919 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1920 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1921 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1922 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1923 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1924 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1925 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1926 | NOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
1927 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1928 |  |  |  | HR1927 (Lo-16bits)
1929 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1930 |  |  |  | HR1929 (Lo-16bits)
1931 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1932 |  |  |  | HR1931 (Lo-16bits)
1933 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1934 |  |  |  | HR1933 (Lo-16bits)
1935 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1936 |  |  |  | HR1935 (Lo-16bits)
1937 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1938 |  |  |  | HR1937 (Lo-16bits)
1939 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1940 |  |  |  | HR1939 (Lo-16bits)
1941 | NOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
1942 |  |  |  | HR1941 (Lo-16bits)
1943 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1944 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1945 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1946 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1947 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1948 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1949 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1950 | NOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
1951 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1952 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1953 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1954 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1955 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1956 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1957 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1958 | NOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
1959 | NOC1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
1960 |  |  |  | HR1959 (Lo-16bits)
1961 | NOC1:Delay type | RW | 1 | 0=DT;1=IDMT
1962 | NOC1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
1963 |  |  |  | HR1962 (Lo-16bits)
1964 | NOC1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
1965 | NOC1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
1966 | NOC1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
1967 | NOC1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
1968 | NOC1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
1969 |  |  |  | HR1968 (Lo-16bits)
1970 | NOC1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
1971 |  |  |  | HR1970 (Lo-16bits)
1972 | NOC1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
1973 |  |  |  | HR1972 (Lo-16bits)
1974 | NOC1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
1975 |  |  |  | HR1974 (Lo-16bits)
1976 | NOC1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
1977 | NOC1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
1978 | NOC2:I>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
1979 | NOC2:I>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
1980 | NOC2:I>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
1981 | NOC2:I>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
1982 | NOC2:I>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
1983 | NOC2:I>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1984 |  |  |  | HR1983 (Lo-16bits)
1985 | NOC2:I>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1986 |  |  |  | HR1985 (Lo-16bits)
1987 | NOC2:I>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
1988 |  |  |  | HR1987 (Lo-16bits)
1989 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1990 |  |  |  | HR1989 (Lo-16bits)
1991 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1992 |  |  |  | HR1991 (Lo-16bits)
1993 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1994 |  |  |  | HR1993 (Lo-16bits)
1995 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1996 |  |  |  | HR1995 (Lo-16bits)
1997 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
1998 |  |  |  | HR1997 (Lo-16bits)
1999 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2000 |  |  |  | HR1999 (Lo-16bits)
2001 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2002 |  |  |  | HR2001 (Lo-16bits)
2003 | NOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2004 |  |  |  | HR2003 (Lo-16bits)
2005 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2006 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2007 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2008 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2009 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2010 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2011 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2012 | NOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
2013 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2014 |  |  |  | HR2013 (Lo-16bits)
2015 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2016 |  |  |  | HR2015 (Lo-16bits)
2017 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2018 |  |  |  | HR2017 (Lo-16bits)
2019 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2020 |  |  |  | HR2019 (Lo-16bits)
2021 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2022 |  |  |  | HR2021 (Lo-16bits)
2023 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2024 |  |  |  | HR2023 (Lo-16bits)
2025 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2026 |  |  |  | HR2025 (Lo-16bits)
2027 | NOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2028 |  |  |  | HR2027 (Lo-16bits)
2029 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2030 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2031 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2032 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2033 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2034 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2035 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2036 | NOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2037 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2038 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2039 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2040 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2041 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2042 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2043 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2044 | NOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2045 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2046 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2047 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2048 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2049 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2050 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2051 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2052 | NOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2053 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2054 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2055 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2056 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2057 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2058 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2059 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2060 | NOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2061 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2062 |  |  |  | HR2061 (Lo-16bits)
2063 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2064 |  |  |  | HR2063 (Lo-16bits)
2065 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2066 |  |  |  | HR2065 (Lo-16bits)
2067 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2068 |  |  |  | HR2067 (Lo-16bits)
2069 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2070 |  |  |  | HR2069 (Lo-16bits)
2071 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2072 |  |  |  | HR2071 (Lo-16bits)
2073 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2074 |  |  |  | HR2073 (Lo-16bits)
2075 | NOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2076 |  |  |  | HR2075 (Lo-16bits)
2077 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2078 |  |  |  | HR2077 (Lo-16bits)
2079 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2080 |  |  |  | HR2079 (Lo-16bits)
2081 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2082 |  |  |  | HR2081 (Lo-16bits)
2083 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2084 |  |  |  | HR2083 (Lo-16bits)
2085 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2086 |  |  |  | HR2085 (Lo-16bits)
2087 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2088 |  |  |  | HR2087 (Lo-16bits)
2089 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2090 |  |  |  | HR2089 (Lo-16bits)
2091 | NOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2092 |  |  |  | HR2091 (Lo-16bits)
2093 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2094 |  |  |  | HR2093 (Lo-16bits)
2095 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2096 |  |  |  | HR2095 (Lo-16bits)
2097 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2098 |  |  |  | HR2097 (Lo-16bits)
2099 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2100 |  |  |  | HR2099 (Lo-16bits)
2101 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2102 |  |  |  | HR2101 (Lo-16bits)
2103 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2104 |  |  |  | HR2103 (Lo-16bits)
2105 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2106 |  |  |  | HR2105 (Lo-16bits)
2107 | NOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2108 |  |  |  | HR2107 (Lo-16bits)
2109 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2110 |  |  |  | HR2109 (Lo-16bits)
2111 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2112 |  |  |  | HR2111 (Lo-16bits)
2113 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2114 |  |  |  | HR2113 (Lo-16bits)
2115 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2116 |  |  |  | HR2115 (Lo-16bits)
2117 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2118 |  |  |  | HR2117 (Lo-16bits)
2119 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2120 |  |  |  | HR2119 (Lo-16bits)
2121 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2122 |  |  |  | HR2121 (Lo-16bits)
2123 | NOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2124 |  |  |  | HR2123 (Lo-16bits)
2125 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2126 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2127 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2128 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2129 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2130 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2131 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2132 | NOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2133 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2134 |  |  |  | HR2133 (Lo-16bits)
2135 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2136 |  |  |  | HR2135 (Lo-16bits)
2137 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2138 |  |  |  | HR2137 (Lo-16bits)
2139 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2140 |  |  |  | HR2139 (Lo-16bits)
2141 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2142 |  |  |  | HR2141 (Lo-16bits)
2143 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2144 |  |  |  | HR2143 (Lo-16bits)
2145 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2146 |  |  |  | HR2145 (Lo-16bits)
2147 | NOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2148 |  |  |  | HR2147 (Lo-16bits)
2149 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2150 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2151 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2152 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2153 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2154 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2155 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2156 | NOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2157 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2158 |  |  |  | HR2157 (Lo-16bits)
2159 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2160 |  |  |  | HR2159 (Lo-16bits)
2161 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2162 |  |  |  | HR2161 (Lo-16bits)
2163 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2164 |  |  |  | HR2163 (Lo-16bits)
2165 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2166 |  |  |  | HR2165 (Lo-16bits)
2167 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2168 |  |  |  | HR2167 (Lo-16bits)
2169 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2170 |  |  |  | HR2169 (Lo-16bits)
2171 | NOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2172 |  |  |  | HR2171 (Lo-16bits)
2173 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2174 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2175 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2176 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2177 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2178 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2179 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2180 | NOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2181 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2182 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2183 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2184 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2185 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2186 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2187 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2188 | NOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2189 | NOC2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2190 |  |  |  | HR2189 (Lo-16bits)
2191 | NOC2:Delay type | RW | 1 | 0=DT;1=IDMT
2192 | NOC2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2193 |  |  |  | HR2192 (Lo-16bits)
2194 | NOC2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2195 | NOC2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2196 | NOC2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2197 | NOC2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2198 | NOC2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2199 |  |  |  | HR2198 (Lo-16bits)
2200 | NOC2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2201 |  |  |  | HR2200 (Lo-16bits)
2202 | NOC2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2203 |  |  |  | HR2202 (Lo-16bits)
2204 | NOC2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2205 |  |  |  | HR2204 (Lo-16bits)
2206 | NOC2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2207 | NOC2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2208 | NOC3:I>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2209 | NOC3:I>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2210 | NOC3:I>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2211 | NOC3:I>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2212 | NOC3:I>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2213 | NOC3:I>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2214 |  |  |  | HR2213 (Lo-16bits)
2215 | NOC3:I>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2216 |  |  |  | HR2215 (Lo-16bits)
2217 | NOC3:I>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2218 |  |  |  | HR2217 (Lo-16bits)
2219 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2220 |  |  |  | HR2219 (Lo-16bits)
2221 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2222 |  |  |  | HR2221 (Lo-16bits)
2223 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2224 |  |  |  | HR2223 (Lo-16bits)
2225 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2226 |  |  |  | HR2225 (Lo-16bits)
2227 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2228 |  |  |  | HR2227 (Lo-16bits)
2229 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2230 |  |  |  | HR2229 (Lo-16bits)
2231 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2232 |  |  |  | HR2231 (Lo-16bits)
2233 | NOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2234 |  |  |  | HR2233 (Lo-16bits)
2235 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2236 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2237 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2238 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2239 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2240 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2241 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2242 | NOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
2243 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2244 |  |  |  | HR2243 (Lo-16bits)
2245 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2246 |  |  |  | HR2245 (Lo-16bits)
2247 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2248 |  |  |  | HR2247 (Lo-16bits)
2249 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2250 |  |  |  | HR2249 (Lo-16bits)
2251 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2252 |  |  |  | HR2251 (Lo-16bits)
2253 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2254 |  |  |  | HR2253 (Lo-16bits)
2255 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2256 |  |  |  | HR2255 (Lo-16bits)
2257 | NOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2258 |  |  |  | HR2257 (Lo-16bits)
2259 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2260 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2261 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2262 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2263 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2264 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2265 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2266 | NOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2267 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2268 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2269 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2270 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2271 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2272 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2273 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2274 | NOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2275 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2276 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2277 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2278 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2279 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2280 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2281 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2282 | NOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2283 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2284 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2285 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2286 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2287 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2288 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2289 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2290 | NOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2291 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2292 |  |  |  | HR2291 (Lo-16bits)
2293 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2294 |  |  |  | HR2293 (Lo-16bits)
2295 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2296 |  |  |  | HR2295 (Lo-16bits)
2297 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2298 |  |  |  | HR2297 (Lo-16bits)
2299 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2300 |  |  |  | HR2299 (Lo-16bits)
2301 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2302 |  |  |  | HR2301 (Lo-16bits)
2303 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2304 |  |  |  | HR2303 (Lo-16bits)
2305 | NOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2306 |  |  |  | HR2305 (Lo-16bits)
2307 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2308 |  |  |  | HR2307 (Lo-16bits)
2309 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2310 |  |  |  | HR2309 (Lo-16bits)
2311 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2312 |  |  |  | HR2311 (Lo-16bits)
2313 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2314 |  |  |  | HR2313 (Lo-16bits)
2315 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2316 |  |  |  | HR2315 (Lo-16bits)
2317 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2318 |  |  |  | HR2317 (Lo-16bits)
2319 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2320 |  |  |  | HR2319 (Lo-16bits)
2321 | NOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2322 |  |  |  | HR2321 (Lo-16bits)
2323 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2324 |  |  |  | HR2323 (Lo-16bits)
2325 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2326 |  |  |  | HR2325 (Lo-16bits)
2327 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2328 |  |  |  | HR2327 (Lo-16bits)
2329 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2330 |  |  |  | HR2329 (Lo-16bits)
2331 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2332 |  |  |  | HR2331 (Lo-16bits)
2333 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2334 |  |  |  | HR2333 (Lo-16bits)
2335 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2336 |  |  |  | HR2335 (Lo-16bits)
2337 | NOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2338 |  |  |  | HR2337 (Lo-16bits)
2339 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2340 |  |  |  | HR2339 (Lo-16bits)
2341 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2342 |  |  |  | HR2341 (Lo-16bits)
2343 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2344 |  |  |  | HR2343 (Lo-16bits)
2345 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2346 |  |  |  | HR2345 (Lo-16bits)
2347 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2348 |  |  |  | HR2347 (Lo-16bits)
2349 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2350 |  |  |  | HR2349 (Lo-16bits)
2351 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2352 |  |  |  | HR2351 (Lo-16bits)
2353 | NOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2354 |  |  |  | HR2353 (Lo-16bits)
2355 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2356 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2357 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2358 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2359 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2360 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2361 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2362 | NOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2363 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2364 |  |  |  | HR2363 (Lo-16bits)
2365 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2366 |  |  |  | HR2365 (Lo-16bits)
2367 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2368 |  |  |  | HR2367 (Lo-16bits)
2369 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2370 |  |  |  | HR2369 (Lo-16bits)
2371 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2372 |  |  |  | HR2371 (Lo-16bits)
2373 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2374 |  |  |  | HR2373 (Lo-16bits)
2375 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2376 |  |  |  | HR2375 (Lo-16bits)
2377 | NOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2378 |  |  |  | HR2377 (Lo-16bits)
2379 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2380 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2381 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2382 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2383 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2384 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2385 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2386 | NOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2387 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2388 |  |  |  | HR2387 (Lo-16bits)
2389 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2390 |  |  |  | HR2389 (Lo-16bits)
2391 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2392 |  |  |  | HR2391 (Lo-16bits)
2393 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2394 |  |  |  | HR2393 (Lo-16bits)
2395 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2396 |  |  |  | HR2395 (Lo-16bits)
2397 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2398 |  |  |  | HR2397 (Lo-16bits)
2399 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2400 |  |  |  | HR2399 (Lo-16bits)
2401 | NOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2402 |  |  |  | HR2401 (Lo-16bits)
2403 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2404 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2405 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2406 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2407 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2408 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2409 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2410 | NOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2411 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2412 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2413 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2414 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2415 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2416 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2417 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2418 | NOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2419 | NOC3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2420 |  |  |  | HR2419 (Lo-16bits)
2421 | NOC3:Delay type | RW | 1 | 0=DT;1=IDMT
2422 | NOC3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2423 |  |  |  | HR2422 (Lo-16bits)
2424 | NOC3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2425 | NOC3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2426 | NOC3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2427 | NOC3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2428 | NOC3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2429 |  |  |  | HR2428 (Lo-16bits)
2430 | NOC3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2431 |  |  |  | HR2430 (Lo-16bits)
2432 | NOC3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2433 |  |  |  | HR2432 (Lo-16bits)
2434 | NOC3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2435 |  |  |  | HR2434 (Lo-16bits)
2436 | NOC3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2437 | NOC3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2438 | NOC4:I>>>> [50/51] mode | R(W) | 1 | 0=Disabled;1=Activated
2439 | NOC4:I>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2440 | NOC4:I>>>> Phases condition | R | 1 | 0=Normal;1=Start A;2=Start B;3=Start C;4=Trip A;5=Trip B;6=Trip C;7=Start AB;8=Start BC;9=Start CA;10=Start ABC;11=Trip AB;12=Trip BC;13=Trip CA;14=Trip ABC
2441 | NOC4:I>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2442 | NOC4:I>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2443 | NOC4:I>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2444 |  |  |  | HR2443 (Lo-16bits)
2445 | NOC4:I>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2446 |  |  |  | HR2445 (Lo-16bits)
2447 | NOC4:I>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2448 |  |  |  | HR2447 (Lo-16bits)
2449 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2450 |  |  |  | HR2449 (Lo-16bits)
2451 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2452 |  |  |  | HR2451 (Lo-16bits)
2453 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2454 |  |  |  | HR2453 (Lo-16bits)
2455 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2456 |  |  |  | HR2455 (Lo-16bits)
2457 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2458 |  |  |  | HR2457 (Lo-16bits)
2459 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2460 |  |  |  | HR2459 (Lo-16bits)
2461 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2462 |  |  |  | HR2461 (Lo-16bits)
2463 | NOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2464 |  |  |  | HR2463 (Lo-16bits)
2465 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2466 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2467 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2468 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2469 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2470 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2471 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2472 | NOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
2473 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2474 |  |  |  | HR2473 (Lo-16bits)
2475 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2476 |  |  |  | HR2475 (Lo-16bits)
2477 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2478 |  |  |  | HR2477 (Lo-16bits)
2479 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2480 |  |  |  | HR2479 (Lo-16bits)
2481 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2482 |  |  |  | HR2481 (Lo-16bits)
2483 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2484 |  |  |  | HR2483 (Lo-16bits)
2485 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2486 |  |  |  | HR2485 (Lo-16bits)
2487 | NOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2488 |  |  |  | HR2487 (Lo-16bits)
2489 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2490 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2491 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2492 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2493 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2494 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2495 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2496 | NOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2497 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2498 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2499 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2500 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2501 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2502 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2503 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2504 | NOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2505 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2506 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2507 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2508 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2509 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2510 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2511 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2512 | NOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2513 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2514 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2515 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2516 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2517 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2518 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2519 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2520 | NOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2521 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2522 |  |  |  | HR2521 (Lo-16bits)
2523 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2524 |  |  |  | HR2523 (Lo-16bits)
2525 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2526 |  |  |  | HR2525 (Lo-16bits)
2527 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2528 |  |  |  | HR2527 (Lo-16bits)
2529 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2530 |  |  |  | HR2529 (Lo-16bits)
2531 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2532 |  |  |  | HR2531 (Lo-16bits)
2533 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2534 |  |  |  | HR2533 (Lo-16bits)
2535 | NOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2536 |  |  |  | HR2535 (Lo-16bits)
2537 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2538 |  |  |  | HR2537 (Lo-16bits)
2539 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2540 |  |  |  | HR2539 (Lo-16bits)
2541 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2542 |  |  |  | HR2541 (Lo-16bits)
2543 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2544 |  |  |  | HR2543 (Lo-16bits)
2545 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2546 |  |  |  | HR2545 (Lo-16bits)
2547 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2548 |  |  |  | HR2547 (Lo-16bits)
2549 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2550 |  |  |  | HR2549 (Lo-16bits)
2551 | NOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2552 |  |  |  | HR2551 (Lo-16bits)
2553 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2554 |  |  |  | HR2553 (Lo-16bits)
2555 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2556 |  |  |  | HR2555 (Lo-16bits)
2557 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2558 |  |  |  | HR2557 (Lo-16bits)
2559 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2560 |  |  |  | HR2559 (Lo-16bits)
2561 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2562 |  |  |  | HR2561 (Lo-16bits)
2563 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2564 |  |  |  | HR2563 (Lo-16bits)
2565 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2566 |  |  |  | HR2565 (Lo-16bits)
2567 | NOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2568 |  |  |  | HR2567 (Lo-16bits)
2569 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2570 |  |  |  | HR2569 (Lo-16bits)
2571 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2572 |  |  |  | HR2571 (Lo-16bits)
2573 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2574 |  |  |  | HR2573 (Lo-16bits)
2575 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2576 |  |  |  | HR2575 (Lo-16bits)
2577 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2578 |  |  |  | HR2577 (Lo-16bits)
2579 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2580 |  |  |  | HR2579 (Lo-16bits)
2581 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2582 |  |  |  | HR2581 (Lo-16bits)
2583 | NOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2584 |  |  |  | HR2583 (Lo-16bits)
2585 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2586 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2587 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2588 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2589 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2590 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2591 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2592 | NOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2593 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2594 |  |  |  | HR2593 (Lo-16bits)
2595 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2596 |  |  |  | HR2595 (Lo-16bits)
2597 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2598 |  |  |  | HR2597 (Lo-16bits)
2599 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2600 |  |  |  | HR2599 (Lo-16bits)
2601 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2602 |  |  |  | HR2601 (Lo-16bits)
2603 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2604 |  |  |  | HR2603 (Lo-16bits)
2605 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2606 |  |  |  | HR2605 (Lo-16bits)
2607 | NOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2608 |  |  |  | HR2607 (Lo-16bits)
2609 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2610 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2611 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2612 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2613 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2614 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2615 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2616 | NOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2617 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2618 |  |  |  | HR2617 (Lo-16bits)
2619 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2620 |  |  |  | HR2619 (Lo-16bits)
2621 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2622 |  |  |  | HR2621 (Lo-16bits)
2623 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2624 |  |  |  | HR2623 (Lo-16bits)
2625 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2626 |  |  |  | HR2625 (Lo-16bits)
2627 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2628 |  |  |  | HR2627 (Lo-16bits)
2629 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2630 |  |  |  | HR2629 (Lo-16bits)
2631 | NOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2632 |  |  |  | HR2631 (Lo-16bits)
2633 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2634 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2635 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2636 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2637 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2638 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2639 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2640 | NOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2641 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2642 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2643 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2644 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2645 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2646 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2647 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2648 | NOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2649 | NOC4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
2650 |  |  |  | HR2649 (Lo-16bits)
2651 | NOC4:Delay type | RW | 1 | 0=DT;1=IDMT
2652 | NOC4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
2653 |  |  |  | HR2652 (Lo-16bits)
2654 | NOC4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
2655 | NOC4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2656 | NOC4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2657 | NOC4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
2658 | NOC4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
2659 |  |  |  | HR2658 (Lo-16bits)
2660 | NOC4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
2661 |  |  |  | HR2660 (Lo-16bits)
2662 | NOC4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
2663 |  |  |  | HR2662 (Lo-16bits)
2664 | NOC4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
2665 |  |  |  | HR2664 (Lo-16bits)
2666 | NOC4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
2667 | NOC4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
2668 | ROC1:Idrw> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2669 | ROC1:Idrw> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2670 | ROC2:Idrw>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2671 | ROC2:Idrw>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2672 | ROC3:Idrw>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2673 | ROC3:Idrw>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2674 | ROC4:Idrw>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2675 | ROC4:Idrw>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2676 | ROC5:Idrw>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2677 | ROC5:Idrw>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2678 | ROC6:Idrw>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2679 | ROC6:Idrw>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2680 | ROC7:Idrw>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2681 | ROC7:Idrw>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2682 | ROC8:Idrw>>>>>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2683 | ROC8:Idrw>>>>>>>> Current direction | R | 1 | 0=Undefined;1=Forward;2=Reverse
2684 | ROV1:Urw>/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2685 | ROV2:Urw>>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2686 | ROV3:Urw>>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2687 | ROV4:Urw>>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2688 | COL1:ICOL> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2689 | COL2:ICOL>> (49OL) mode | R(W) | 1 | 0=Disabled;1=Activated
2690 | CNU1:CNU> (50UB) mode | R(W) | 1 | 0=Disabled;1=Activated
2691 | UCP1:IUC> condition | R | 1 | 0=Normal;1=Blocked;2=Start On (Alarm);3=Start On (Alarm & Trip);4=Start On (Trip);5=Alarm On;6=Start On;7=Start On,Alarm On;8=Trip On;9=Alarm On, Trip On;10=Multistatus On
2692 | DOC1:Idir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2693 | DOC1:Idir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2694 | DOC1:Idir> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2695 | DOC1:Idir> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2696 |  |  |  | HR2695 (Lo-16bits)
2697 | DOC1:Idir> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2698 |  |  |  | HR2697 (Lo-16bits)
2699 | DOC1:Idir> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2700 |  |  |  | HR2699 (Lo-16bits)
2701 | DOC1:Idir> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2702 |  |  |  | HR2701 (Lo-16bits)
2703 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2704 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2705 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2706 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2707 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2708 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2709 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2710 | DOC1:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2711 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2712 |  |  |  | HR2711 (Lo-16bits)
2713 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2714 |  |  |  | HR2713 (Lo-16bits)
2715 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2716 |  |  |  | HR2715 (Lo-16bits)
2717 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2718 |  |  |  | HR2717 (Lo-16bits)
2719 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2720 |  |  |  | HR2719 (Lo-16bits)
2721 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2722 |  |  |  | HR2721 (Lo-16bits)
2723 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2724 |  |  |  | HR2723 (Lo-16bits)
2725 | DOC1:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2726 |  |  |  | HR2725 (Lo-16bits)
2727 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2728 |  |  |  | HR2727 (Lo-16bits)
2729 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2730 |  |  |  | HR2729 (Lo-16bits)
2731 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2732 |  |  |  | HR2731 (Lo-16bits)
2733 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2734 |  |  |  | HR2733 (Lo-16bits)
2735 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2736 |  |  |  | HR2735 (Lo-16bits)
2737 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2738 |  |  |  | HR2737 (Lo-16bits)
2739 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2740 |  |  |  | HR2739 (Lo-16bits)
2741 | DOC1:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2742 |  |  |  | HR2741 (Lo-16bits)
2743 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2744 |  |  |  | HR2743 (Lo-16bits)
2745 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2746 |  |  |  | HR2745 (Lo-16bits)
2747 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2748 |  |  |  | HR2747 (Lo-16bits)
2749 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2750 |  |  |  | HR2749 (Lo-16bits)
2751 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2752 |  |  |  | HR2751 (Lo-16bits)
2753 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2754 |  |  |  | HR2753 (Lo-16bits)
2755 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2756 |  |  |  | HR2755 (Lo-16bits)
2757 | DOC1:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2758 |  |  |  | HR2757 (Lo-16bits)
2759 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2760 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2761 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2762 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2763 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2764 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2765 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2766 | DOC1:Delay type | R(W) | 1 | 0=DT;1=IDMT
2767 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2768 |  |  |  | HR2767 (Lo-16bits)
2769 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2770 |  |  |  | HR2769 (Lo-16bits)
2771 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2772 |  |  |  | HR2771 (Lo-16bits)
2773 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2774 |  |  |  | HR2773 (Lo-16bits)
2775 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2776 |  |  |  | HR2775 (Lo-16bits)
2777 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2778 |  |  |  | HR2777 (Lo-16bits)
2779 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2780 |  |  |  | HR2779 (Lo-16bits)
2781 | DOC1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
2782 |  |  |  | HR2781 (Lo-16bits)
2783 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2784 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2785 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2786 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2787 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2788 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2789 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2790 | DOC1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
2791 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2792 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2793 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2794 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2795 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2796 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2797 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2798 | DOC1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
2799 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2800 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2801 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2802 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2803 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2804 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2805 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2806 | DOC1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
2807 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2808 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2809 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2810 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2811 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2812 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2813 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2814 | DOC1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
2815 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2816 |  |  |  | HR2815 (Lo-16bits)
2817 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2818 |  |  |  | HR2817 (Lo-16bits)
2819 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2820 |  |  |  | HR2819 (Lo-16bits)
2821 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2822 |  |  |  | HR2821 (Lo-16bits)
2823 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2824 |  |  |  | HR2823 (Lo-16bits)
2825 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2826 |  |  |  | HR2825 (Lo-16bits)
2827 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2828 |  |  |  | HR2827 (Lo-16bits)
2829 | DOC1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
2830 |  |  |  | HR2829 (Lo-16bits)
2831 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2832 |  |  |  | HR2831 (Lo-16bits)
2833 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2834 |  |  |  | HR2833 (Lo-16bits)
2835 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2836 |  |  |  | HR2835 (Lo-16bits)
2837 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2838 |  |  |  | HR2837 (Lo-16bits)
2839 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2840 |  |  |  | HR2839 (Lo-16bits)
2841 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2842 |  |  |  | HR2841 (Lo-16bits)
2843 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2844 |  |  |  | HR2843 (Lo-16bits)
2845 | DOC1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2846 |  |  |  | HR2845 (Lo-16bits)
2847 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2848 |  |  |  | HR2847 (Lo-16bits)
2849 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2850 |  |  |  | HR2849 (Lo-16bits)
2851 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2852 |  |  |  | HR2851 (Lo-16bits)
2853 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2854 |  |  |  | HR2853 (Lo-16bits)
2855 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2856 |  |  |  | HR2855 (Lo-16bits)
2857 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2858 |  |  |  | HR2857 (Lo-16bits)
2859 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2860 |  |  |  | HR2859 (Lo-16bits)
2861 | DOC1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2862 |  |  |  | HR2861 (Lo-16bits)
2863 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2864 |  |  |  | HR2863 (Lo-16bits)
2865 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2866 |  |  |  | HR2865 (Lo-16bits)
2867 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2868 |  |  |  | HR2867 (Lo-16bits)
2869 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2870 |  |  |  | HR2869 (Lo-16bits)
2871 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2872 |  |  |  | HR2871 (Lo-16bits)
2873 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2874 |  |  |  | HR2873 (Lo-16bits)
2875 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2876 |  |  |  | HR2875 (Lo-16bits)
2877 | DOC1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
2878 |  |  |  | HR2877 (Lo-16bits)
2879 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2880 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2881 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2882 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2883 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2884 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2885 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2886 | DOC1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
2887 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2888 |  |  |  | HR2887 (Lo-16bits)
2889 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2890 |  |  |  | HR2889 (Lo-16bits)
2891 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2892 |  |  |  | HR2891 (Lo-16bits)
2893 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2894 |  |  |  | HR2893 (Lo-16bits)
2895 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2896 |  |  |  | HR2895 (Lo-16bits)
2897 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2898 |  |  |  | HR2897 (Lo-16bits)
2899 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2900 |  |  |  | HR2899 (Lo-16bits)
2901 | DOC1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
2902 |  |  |  | HR2901 (Lo-16bits)
2903 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2904 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2905 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2906 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2907 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2908 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2909 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2910 | DOC1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
2911 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2912 |  |  |  | HR2911 (Lo-16bits)
2913 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2914 |  |  |  | HR2913 (Lo-16bits)
2915 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2916 |  |  |  | HR2915 (Lo-16bits)
2917 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2918 |  |  |  | HR2917 (Lo-16bits)
2919 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2920 |  |  |  | HR2919 (Lo-16bits)
2921 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2922 |  |  |  | HR2921 (Lo-16bits)
2923 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2924 |  |  |  | HR2923 (Lo-16bits)
2925 | DOC1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
2926 |  |  |  | HR2925 (Lo-16bits)
2927 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2928 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2929 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2930 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2931 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2932 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2933 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2934 | DOC1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
2935 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2936 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2937 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2938 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2939 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2940 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2941 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2942 | DOC1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
2943 | DOC2:Idir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
2944 | DOC2:Idir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
2945 | DOC2:Idir>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
2946 | DOC2:Idir>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
2947 |  |  |  | HR2946 (Lo-16bits)
2948 | DOC2:Idir>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2949 |  |  |  | HR2948 (Lo-16bits)
2950 | DOC2:Idir>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2951 |  |  |  | HR2950 (Lo-16bits)
2952 | DOC2:Idir>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
2953 |  |  |  | HR2952 (Lo-16bits)
2954 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2955 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2956 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2957 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2958 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2959 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2960 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2961 | DOC2:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
2962 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2963 |  |  |  | HR2962 (Lo-16bits)
2964 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2965 |  |  |  | HR2964 (Lo-16bits)
2966 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2967 |  |  |  | HR2966 (Lo-16bits)
2968 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2969 |  |  |  | HR2968 (Lo-16bits)
2970 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2971 |  |  |  | HR2970 (Lo-16bits)
2972 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2973 |  |  |  | HR2972 (Lo-16bits)
2974 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2975 |  |  |  | HR2974 (Lo-16bits)
2976 | DOC2:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
2977 |  |  |  | HR2976 (Lo-16bits)
2978 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2979 |  |  |  | HR2978 (Lo-16bits)
2980 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2981 |  |  |  | HR2980 (Lo-16bits)
2982 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2983 |  |  |  | HR2982 (Lo-16bits)
2984 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2985 |  |  |  | HR2984 (Lo-16bits)
2986 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2987 |  |  |  | HR2986 (Lo-16bits)
2988 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2989 |  |  |  | HR2988 (Lo-16bits)
2990 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2991 |  |  |  | HR2990 (Lo-16bits)
2992 | DOC2:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
2993 |  |  |  | HR2992 (Lo-16bits)
2994 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2995 |  |  |  | HR2994 (Lo-16bits)
2996 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2997 |  |  |  | HR2996 (Lo-16bits)
2998 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
2999 |  |  |  | HR2998 (Lo-16bits)
3000 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3001 |  |  |  | HR3000 (Lo-16bits)
3002 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3003 |  |  |  | HR3002 (Lo-16bits)
3004 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3005 |  |  |  | HR3004 (Lo-16bits)
3006 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3007 |  |  |  | HR3006 (Lo-16bits)
3008 | DOC2:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3009 |  |  |  | HR3008 (Lo-16bits)
3010 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3011 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3012 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3013 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3014 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3015 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3016 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3017 | DOC2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3018 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3019 |  |  |  | HR3018 (Lo-16bits)
3020 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3021 |  |  |  | HR3020 (Lo-16bits)
3022 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3023 |  |  |  | HR3022 (Lo-16bits)
3024 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3025 |  |  |  | HR3024 (Lo-16bits)
3026 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3027 |  |  |  | HR3026 (Lo-16bits)
3028 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3029 |  |  |  | HR3028 (Lo-16bits)
3030 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3031 |  |  |  | HR3030 (Lo-16bits)
3032 | DOC2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3033 |  |  |  | HR3032 (Lo-16bits)
3034 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3035 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3036 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3037 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3038 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3039 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3040 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3041 | DOC2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3042 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3043 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3044 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3045 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3046 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3047 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3048 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3049 | DOC2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3050 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3051 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3052 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3053 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3054 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3055 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3056 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3057 | DOC2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3058 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3059 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3060 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3061 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3062 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3063 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3064 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3065 | DOC2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3066 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3067 |  |  |  | HR3066 (Lo-16bits)
3068 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3069 |  |  |  | HR3068 (Lo-16bits)
3070 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3071 |  |  |  | HR3070 (Lo-16bits)
3072 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3073 |  |  |  | HR3072 (Lo-16bits)
3074 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3075 |  |  |  | HR3074 (Lo-16bits)
3076 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3077 |  |  |  | HR3076 (Lo-16bits)
3078 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3079 |  |  |  | HR3078 (Lo-16bits)
3080 | DOC2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3081 |  |  |  | HR3080 (Lo-16bits)
3082 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3083 |  |  |  | HR3082 (Lo-16bits)
3084 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3085 |  |  |  | HR3084 (Lo-16bits)
3086 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3087 |  |  |  | HR3086 (Lo-16bits)
3088 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3089 |  |  |  | HR3088 (Lo-16bits)
3090 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3091 |  |  |  | HR3090 (Lo-16bits)
3092 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3093 |  |  |  | HR3092 (Lo-16bits)
3094 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3095 |  |  |  | HR3094 (Lo-16bits)
3096 | DOC2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3097 |  |  |  | HR3096 (Lo-16bits)
3098 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3099 |  |  |  | HR3098 (Lo-16bits)
3100 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3101 |  |  |  | HR3100 (Lo-16bits)
3102 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3103 |  |  |  | HR3102 (Lo-16bits)
3104 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3105 |  |  |  | HR3104 (Lo-16bits)
3106 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3107 |  |  |  | HR3106 (Lo-16bits)
3108 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3109 |  |  |  | HR3108 (Lo-16bits)
3110 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3111 |  |  |  | HR3110 (Lo-16bits)
3112 | DOC2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3113 |  |  |  | HR3112 (Lo-16bits)
3114 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3115 |  |  |  | HR3114 (Lo-16bits)
3116 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3117 |  |  |  | HR3116 (Lo-16bits)
3118 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3119 |  |  |  | HR3118 (Lo-16bits)
3120 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3121 |  |  |  | HR3120 (Lo-16bits)
3122 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3123 |  |  |  | HR3122 (Lo-16bits)
3124 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3125 |  |  |  | HR3124 (Lo-16bits)
3126 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3127 |  |  |  | HR3126 (Lo-16bits)
3128 | DOC2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3129 |  |  |  | HR3128 (Lo-16bits)
3130 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3131 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3132 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3133 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3134 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3135 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3136 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3137 | DOC2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3138 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3139 |  |  |  | HR3138 (Lo-16bits)
3140 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3141 |  |  |  | HR3140 (Lo-16bits)
3142 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3143 |  |  |  | HR3142 (Lo-16bits)
3144 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3145 |  |  |  | HR3144 (Lo-16bits)
3146 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3147 |  |  |  | HR3146 (Lo-16bits)
3148 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3149 |  |  |  | HR3148 (Lo-16bits)
3150 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3151 |  |  |  | HR3150 (Lo-16bits)
3152 | DOC2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3153 |  |  |  | HR3152 (Lo-16bits)
3154 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3155 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3156 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3157 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3158 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3159 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3160 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3161 | DOC2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3162 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3163 |  |  |  | HR3162 (Lo-16bits)
3164 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3165 |  |  |  | HR3164 (Lo-16bits)
3166 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3167 |  |  |  | HR3166 (Lo-16bits)
3168 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3169 |  |  |  | HR3168 (Lo-16bits)
3170 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3171 |  |  |  | HR3170 (Lo-16bits)
3172 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3173 |  |  |  | HR3172 (Lo-16bits)
3174 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3175 |  |  |  | HR3174 (Lo-16bits)
3176 | DOC2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3177 |  |  |  | HR3176 (Lo-16bits)
3178 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3179 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3180 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3181 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3182 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3183 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3184 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3185 | DOC2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3186 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3187 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3188 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3189 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3190 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3191 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3192 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3193 | DOC2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3194 | DOC3:Idir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3195 | DOC3:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3196 | DOC3:Idir>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3197 | DOC3:Idir>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3198 |  |  |  | HR3197 (Lo-16bits)
3199 | DOC3:Idir>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3200 |  |  |  | HR3199 (Lo-16bits)
3201 | DOC3:Idir>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3202 |  |  |  | HR3201 (Lo-16bits)
3203 | DOC3:Idir>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3204 |  |  |  | HR3203 (Lo-16bits)
3205 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3206 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3207 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3208 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3209 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3210 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3211 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3212 | DOC3:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3213 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3214 |  |  |  | HR3213 (Lo-16bits)
3215 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3216 |  |  |  | HR3215 (Lo-16bits)
3217 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3218 |  |  |  | HR3217 (Lo-16bits)
3219 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3220 |  |  |  | HR3219 (Lo-16bits)
3221 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3222 |  |  |  | HR3221 (Lo-16bits)
3223 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3224 |  |  |  | HR3223 (Lo-16bits)
3225 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3226 |  |  |  | HR3225 (Lo-16bits)
3227 | DOC3:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3228 |  |  |  | HR3227 (Lo-16bits)
3229 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3230 |  |  |  | HR3229 (Lo-16bits)
3231 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3232 |  |  |  | HR3231 (Lo-16bits)
3233 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3234 |  |  |  | HR3233 (Lo-16bits)
3235 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3236 |  |  |  | HR3235 (Lo-16bits)
3237 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3238 |  |  |  | HR3237 (Lo-16bits)
3239 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3240 |  |  |  | HR3239 (Lo-16bits)
3241 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3242 |  |  |  | HR3241 (Lo-16bits)
3243 | DOC3:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3244 |  |  |  | HR3243 (Lo-16bits)
3245 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3246 |  |  |  | HR3245 (Lo-16bits)
3247 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3248 |  |  |  | HR3247 (Lo-16bits)
3249 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3250 |  |  |  | HR3249 (Lo-16bits)
3251 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3252 |  |  |  | HR3251 (Lo-16bits)
3253 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3254 |  |  |  | HR3253 (Lo-16bits)
3255 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3256 |  |  |  | HR3255 (Lo-16bits)
3257 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3258 |  |  |  | HR3257 (Lo-16bits)
3259 | DOC3:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3260 |  |  |  | HR3259 (Lo-16bits)
3261 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3262 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3263 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3264 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3265 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3266 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3267 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3268 | DOC3:Delay type | R(W) | 1 | 0=DT;1=IDMT
3269 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3270 |  |  |  | HR3269 (Lo-16bits)
3271 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3272 |  |  |  | HR3271 (Lo-16bits)
3273 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3274 |  |  |  | HR3273 (Lo-16bits)
3275 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3276 |  |  |  | HR3275 (Lo-16bits)
3277 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3278 |  |  |  | HR3277 (Lo-16bits)
3279 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3280 |  |  |  | HR3279 (Lo-16bits)
3281 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3282 |  |  |  | HR3281 (Lo-16bits)
3283 | DOC3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3284 |  |  |  | HR3283 (Lo-16bits)
3285 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3286 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3287 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3288 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3289 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3290 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3291 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3292 | DOC3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3293 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3294 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3295 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3296 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3297 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3298 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3299 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3300 | DOC3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3301 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3302 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3303 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3304 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3305 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3306 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3307 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3308 | DOC3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3309 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3310 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3311 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3312 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3313 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3314 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3315 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3316 | DOC3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3317 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3318 |  |  |  | HR3317 (Lo-16bits)
3319 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3320 |  |  |  | HR3319 (Lo-16bits)
3321 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3322 |  |  |  | HR3321 (Lo-16bits)
3323 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3324 |  |  |  | HR3323 (Lo-16bits)
3325 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3326 |  |  |  | HR3325 (Lo-16bits)
3327 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3328 |  |  |  | HR3327 (Lo-16bits)
3329 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3330 |  |  |  | HR3329 (Lo-16bits)
3331 | DOC3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3332 |  |  |  | HR3331 (Lo-16bits)
3333 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3334 |  |  |  | HR3333 (Lo-16bits)
3335 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3336 |  |  |  | HR3335 (Lo-16bits)
3337 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3338 |  |  |  | HR3337 (Lo-16bits)
3339 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3340 |  |  |  | HR3339 (Lo-16bits)
3341 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3342 |  |  |  | HR3341 (Lo-16bits)
3343 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3344 |  |  |  | HR3343 (Lo-16bits)
3345 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3346 |  |  |  | HR3345 (Lo-16bits)
3347 | DOC3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3348 |  |  |  | HR3347 (Lo-16bits)
3349 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3350 |  |  |  | HR3349 (Lo-16bits)
3351 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3352 |  |  |  | HR3351 (Lo-16bits)
3353 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3354 |  |  |  | HR3353 (Lo-16bits)
3355 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3356 |  |  |  | HR3355 (Lo-16bits)
3357 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3358 |  |  |  | HR3357 (Lo-16bits)
3359 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3360 |  |  |  | HR3359 (Lo-16bits)
3361 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3362 |  |  |  | HR3361 (Lo-16bits)
3363 | DOC3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3364 |  |  |  | HR3363 (Lo-16bits)
3365 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3366 |  |  |  | HR3365 (Lo-16bits)
3367 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3368 |  |  |  | HR3367 (Lo-16bits)
3369 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3370 |  |  |  | HR3369 (Lo-16bits)
3371 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3372 |  |  |  | HR3371 (Lo-16bits)
3373 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3374 |  |  |  | HR3373 (Lo-16bits)
3375 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3376 |  |  |  | HR3375 (Lo-16bits)
3377 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3378 |  |  |  | HR3377 (Lo-16bits)
3379 | DOC3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3380 |  |  |  | HR3379 (Lo-16bits)
3381 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3382 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3383 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3384 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3385 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3386 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3387 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3388 | DOC3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3389 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3390 |  |  |  | HR3389 (Lo-16bits)
3391 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3392 |  |  |  | HR3391 (Lo-16bits)
3393 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3394 |  |  |  | HR3393 (Lo-16bits)
3395 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3396 |  |  |  | HR3395 (Lo-16bits)
3397 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3398 |  |  |  | HR3397 (Lo-16bits)
3399 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3400 |  |  |  | HR3399 (Lo-16bits)
3401 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3402 |  |  |  | HR3401 (Lo-16bits)
3403 | DOC3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3404 |  |  |  | HR3403 (Lo-16bits)
3405 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3406 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3407 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3408 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3409 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3410 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3411 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3412 | DOC3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3413 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3414 |  |  |  | HR3413 (Lo-16bits)
3415 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3416 |  |  |  | HR3415 (Lo-16bits)
3417 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3418 |  |  |  | HR3417 (Lo-16bits)
3419 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3420 |  |  |  | HR3419 (Lo-16bits)
3421 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3422 |  |  |  | HR3421 (Lo-16bits)
3423 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3424 |  |  |  | HR3423 (Lo-16bits)
3425 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3426 |  |  |  | HR3425 (Lo-16bits)
3427 | DOC3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3428 |  |  |  | HR3427 (Lo-16bits)
3429 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3430 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3431 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3432 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3433 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3434 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3435 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3436 | DOC3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3437 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3438 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3439 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3440 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3441 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3442 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3443 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3444 | DOC3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3445 | DOC4:Idir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3446 | DOC4:Idir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3447 | DOC4:Idir>>>> Last fault type | R | 1 | 0=-;1=A-G;2=B-G;3=A-B;4=C-G;5=A-C;6=B-C;7=A-B-C
3448 | DOC4:Idir>>>> Last fault angle | R | 2 | FLOAT [-360.00...360.00] (Hi-16bits)
3449 |  |  |  | HR3448 (Lo-16bits)
3450 | DOC4:Idir>>>> Last fault IA current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3451 |  |  |  | HR3450 (Lo-16bits)
3452 | DOC4:Idir>>>> Last fault IB current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3453 |  |  |  | HR3452 (Lo-16bits)
3454 | DOC4:Idir>>>> Last fault IC current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3455 |  |  |  | HR3454 (Lo-16bits)
3456 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3457 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3458 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3459 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3460 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3461 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3462 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3463 | DOC4:Characteristic direction | R(W) | 1 | 0=Directional;1=NonDir
3464 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3465 |  |  |  | HR3464 (Lo-16bits)
3466 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3467 |  |  |  | HR3466 (Lo-16bits)
3468 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3469 |  |  |  | HR3468 (Lo-16bits)
3470 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3471 |  |  |  | HR3470 (Lo-16bits)
3472 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3473 |  |  |  | HR3472 (Lo-16bits)
3474 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3475 |  |  |  | HR3474 (Lo-16bits)
3476 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3477 |  |  |  | HR3476 (Lo-16bits)
3478 | DOC4:Operating sector size (+/-) | R(W) | 2 | FLOAT [1...170] (Hi-16bits)
3479 |  |  |  | HR3478 (Lo-16bits)
3480 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3481 |  |  |  | HR3480 (Lo-16bits)
3482 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3483 |  |  |  | HR3482 (Lo-16bits)
3484 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3485 |  |  |  | HR3484 (Lo-16bits)
3486 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3487 |  |  |  | HR3486 (Lo-16bits)
3488 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3489 |  |  |  | HR3488 (Lo-16bits)
3490 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3491 |  |  |  | HR3490 (Lo-16bits)
3492 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3493 |  |  |  | HR3492 (Lo-16bits)
3494 | DOC4:Operating sector center | R(W) | 2 | FLOAT [-180...180] (Hi-16bits)
3495 |  |  |  | HR3494 (Lo-16bits)
3496 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3497 |  |  |  | HR3496 (Lo-16bits)
3498 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3499 |  |  |  | HR3498 (Lo-16bits)
3500 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3501 |  |  |  | HR3500 (Lo-16bits)
3502 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3503 |  |  |  | HR3502 (Lo-16bits)
3504 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3505 |  |  |  | HR3504 (Lo-16bits)
3506 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3507 |  |  |  | HR3506 (Lo-16bits)
3508 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3509 |  |  |  | HR3508 (Lo-16bits)
3510 | DOC4:Pick-up setting Iset | R(W) | 2 | FLOAT [0.1...40] (Hi-16bits)
3511 |  |  |  | HR3510 (Lo-16bits)
3512 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3513 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3514 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3515 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3516 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3517 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3518 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3519 | DOC4:Delay type | R(W) | 1 | 0=DT;1=IDMT
3520 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3521 |  |  |  | HR3520 (Lo-16bits)
3522 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3523 |  |  |  | HR3522 (Lo-16bits)
3524 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3525 |  |  |  | HR3524 (Lo-16bits)
3526 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3527 |  |  |  | HR3526 (Lo-16bits)
3528 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3529 |  |  |  | HR3528 (Lo-16bits)
3530 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3531 |  |  |  | HR3530 (Lo-16bits)
3532 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3533 |  |  |  | HR3532 (Lo-16bits)
3534 | DOC4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3535 |  |  |  | HR3534 (Lo-16bits)
3536 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3537 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3538 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3539 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3540 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3541 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3542 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3543 | DOC4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3544 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3545 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3546 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3547 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3548 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3549 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3550 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3551 | DOC4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3552 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3553 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3554 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3555 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3556 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3557 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3558 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3559 | DOC4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3560 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3561 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3562 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3563 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3564 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3565 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3566 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3567 | DOC4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3568 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3569 |  |  |  | HR3568 (Lo-16bits)
3570 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3571 |  |  |  | HR3570 (Lo-16bits)
3572 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3573 |  |  |  | HR3572 (Lo-16bits)
3574 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3575 |  |  |  | HR3574 (Lo-16bits)
3576 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3577 |  |  |  | HR3576 (Lo-16bits)
3578 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3579 |  |  |  | HR3578 (Lo-16bits)
3580 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3581 |  |  |  | HR3580 (Lo-16bits)
3582 | DOC4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3583 |  |  |  | HR3582 (Lo-16bits)
3584 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3585 |  |  |  | HR3584 (Lo-16bits)
3586 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3587 |  |  |  | HR3586 (Lo-16bits)
3588 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3589 |  |  |  | HR3588 (Lo-16bits)
3590 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3591 |  |  |  | HR3590 (Lo-16bits)
3592 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3593 |  |  |  | HR3592 (Lo-16bits)
3594 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3595 |  |  |  | HR3594 (Lo-16bits)
3596 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3597 |  |  |  | HR3596 (Lo-16bits)
3598 | DOC4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3599 |  |  |  | HR3598 (Lo-16bits)
3600 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3601 |  |  |  | HR3600 (Lo-16bits)
3602 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3603 |  |  |  | HR3602 (Lo-16bits)
3604 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3605 |  |  |  | HR3604 (Lo-16bits)
3606 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3607 |  |  |  | HR3606 (Lo-16bits)
3608 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3609 |  |  |  | HR3608 (Lo-16bits)
3610 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3611 |  |  |  | HR3610 (Lo-16bits)
3612 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3613 |  |  |  | HR3612 (Lo-16bits)
3614 | DOC4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3615 |  |  |  | HR3614 (Lo-16bits)
3616 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3617 |  |  |  | HR3616 (Lo-16bits)
3618 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3619 |  |  |  | HR3618 (Lo-16bits)
3620 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3621 |  |  |  | HR3620 (Lo-16bits)
3622 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3623 |  |  |  | HR3622 (Lo-16bits)
3624 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3625 |  |  |  | HR3624 (Lo-16bits)
3626 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3627 |  |  |  | HR3626 (Lo-16bits)
3628 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3629 |  |  |  | HR3628 (Lo-16bits)
3630 | DOC4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3631 |  |  |  | HR3630 (Lo-16bits)
3632 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3633 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3634 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3635 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3636 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3637 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3638 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3639 | DOC4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3640 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3641 |  |  |  | HR3640 (Lo-16bits)
3642 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3643 |  |  |  | HR3642 (Lo-16bits)
3644 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3645 |  |  |  | HR3644 (Lo-16bits)
3646 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3647 |  |  |  | HR3646 (Lo-16bits)
3648 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3649 |  |  |  | HR3648 (Lo-16bits)
3650 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3651 |  |  |  | HR3650 (Lo-16bits)
3652 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3653 |  |  |  | HR3652 (Lo-16bits)
3654 | DOC4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3655 |  |  |  | HR3654 (Lo-16bits)
3656 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3657 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3658 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3659 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3660 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3661 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3662 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3663 | DOC4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3664 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3665 |  |  |  | HR3664 (Lo-16bits)
3666 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3667 |  |  |  | HR3666 (Lo-16bits)
3668 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3669 |  |  |  | HR3668 (Lo-16bits)
3670 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3671 |  |  |  | HR3670 (Lo-16bits)
3672 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3673 |  |  |  | HR3672 (Lo-16bits)
3674 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3675 |  |  |  | HR3674 (Lo-16bits)
3676 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3677 |  |  |  | HR3676 (Lo-16bits)
3678 | DOC4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3679 |  |  |  | HR3678 (Lo-16bits)
3680 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3681 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3682 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3683 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3684 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3685 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3686 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3687 | DOC4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3688 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3689 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3690 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3691 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3692 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3693 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3694 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3695 | DOC4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3696 | NEF1:I0> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3697 | NEF1:I0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3698 | NEF1:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3699 | NEF1:I0> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3700 | NEF1:I0> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3701 |  |  |  | HR3700 (Lo-16bits)
3702 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3703 |  |  |  | HR3702 (Lo-16bits)
3704 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3705 |  |  |  | HR3704 (Lo-16bits)
3706 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3707 |  |  |  | HR3706 (Lo-16bits)
3708 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3709 |  |  |  | HR3708 (Lo-16bits)
3710 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3711 |  |  |  | HR3710 (Lo-16bits)
3712 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3713 |  |  |  | HR3712 (Lo-16bits)
3714 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3715 |  |  |  | HR3714 (Lo-16bits)
3716 | NEF1:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3717 |  |  |  | HR3716 (Lo-16bits)
3718 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3719 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3720 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3721 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3722 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3723 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3724 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3725 | NEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
3726 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3727 |  |  |  | HR3726 (Lo-16bits)
3728 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3729 |  |  |  | HR3728 (Lo-16bits)
3730 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3731 |  |  |  | HR3730 (Lo-16bits)
3732 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3733 |  |  |  | HR3732 (Lo-16bits)
3734 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3735 |  |  |  | HR3734 (Lo-16bits)
3736 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3737 |  |  |  | HR3736 (Lo-16bits)
3738 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3739 |  |  |  | HR3738 (Lo-16bits)
3740 | NEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3741 |  |  |  | HR3740 (Lo-16bits)
3742 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3743 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3744 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3745 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3746 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3747 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3748 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3749 | NEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3750 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3751 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3752 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3753 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3754 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3755 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3756 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3757 | NEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3758 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3759 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3760 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3761 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3762 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3763 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3764 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3765 | NEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3766 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3767 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3768 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3769 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3770 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3771 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3772 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3773 | NEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3774 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3775 |  |  |  | HR3774 (Lo-16bits)
3776 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3777 |  |  |  | HR3776 (Lo-16bits)
3778 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3779 |  |  |  | HR3778 (Lo-16bits)
3780 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3781 |  |  |  | HR3780 (Lo-16bits)
3782 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3783 |  |  |  | HR3782 (Lo-16bits)
3784 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3785 |  |  |  | HR3784 (Lo-16bits)
3786 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3787 |  |  |  | HR3786 (Lo-16bits)
3788 | NEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
3789 |  |  |  | HR3788 (Lo-16bits)
3790 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3791 |  |  |  | HR3790 (Lo-16bits)
3792 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3793 |  |  |  | HR3792 (Lo-16bits)
3794 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3795 |  |  |  | HR3794 (Lo-16bits)
3796 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3797 |  |  |  | HR3796 (Lo-16bits)
3798 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3799 |  |  |  | HR3798 (Lo-16bits)
3800 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3801 |  |  |  | HR3800 (Lo-16bits)
3802 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3803 |  |  |  | HR3802 (Lo-16bits)
3804 | NEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3805 |  |  |  | HR3804 (Lo-16bits)
3806 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3807 |  |  |  | HR3806 (Lo-16bits)
3808 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3809 |  |  |  | HR3808 (Lo-16bits)
3810 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3811 |  |  |  | HR3810 (Lo-16bits)
3812 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3813 |  |  |  | HR3812 (Lo-16bits)
3814 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3815 |  |  |  | HR3814 (Lo-16bits)
3816 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3817 |  |  |  | HR3816 (Lo-16bits)
3818 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3819 |  |  |  | HR3818 (Lo-16bits)
3820 | NEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3821 |  |  |  | HR3820 (Lo-16bits)
3822 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3823 |  |  |  | HR3822 (Lo-16bits)
3824 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3825 |  |  |  | HR3824 (Lo-16bits)
3826 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3827 |  |  |  | HR3826 (Lo-16bits)
3828 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3829 |  |  |  | HR3828 (Lo-16bits)
3830 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3831 |  |  |  | HR3830 (Lo-16bits)
3832 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3833 |  |  |  | HR3832 (Lo-16bits)
3834 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3835 |  |  |  | HR3834 (Lo-16bits)
3836 | NEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
3837 |  |  |  | HR3836 (Lo-16bits)
3838 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3839 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3840 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3841 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3842 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3843 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3844 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3845 | NEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
3846 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3847 |  |  |  | HR3846 (Lo-16bits)
3848 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3849 |  |  |  | HR3848 (Lo-16bits)
3850 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3851 |  |  |  | HR3850 (Lo-16bits)
3852 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3853 |  |  |  | HR3852 (Lo-16bits)
3854 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3855 |  |  |  | HR3854 (Lo-16bits)
3856 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3857 |  |  |  | HR3856 (Lo-16bits)
3858 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3859 |  |  |  | HR3858 (Lo-16bits)
3860 | NEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
3861 |  |  |  | HR3860 (Lo-16bits)
3862 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3863 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3864 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3865 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3866 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3867 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3868 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3869 | NEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
3870 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3871 |  |  |  | HR3870 (Lo-16bits)
3872 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3873 |  |  |  | HR3872 (Lo-16bits)
3874 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3875 |  |  |  | HR3874 (Lo-16bits)
3876 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3877 |  |  |  | HR3876 (Lo-16bits)
3878 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3879 |  |  |  | HR3878 (Lo-16bits)
3880 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3881 |  |  |  | HR3880 (Lo-16bits)
3882 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3883 |  |  |  | HR3882 (Lo-16bits)
3884 | NEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
3885 |  |  |  | HR3884 (Lo-16bits)
3886 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3887 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3888 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3889 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3890 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3891 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3892 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3893 | NEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
3894 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3895 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3896 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3897 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3898 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3899 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3900 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3901 | NEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
3902 | NEF1:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
3903 |  |  |  | HR3902 (Lo-16bits)
3904 | NEF1:Delay type | RW | 1 | 0=DT;1=IDMT
3905 | NEF1:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
3906 |  |  |  | HR3905 (Lo-16bits)
3907 | NEF1:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
3908 | NEF1:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3909 | NEF1:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3910 | NEF1:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
3911 | NEF1:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
3912 |  |  |  | HR3911 (Lo-16bits)
3913 | NEF1:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
3914 |  |  |  | HR3913 (Lo-16bits)
3915 | NEF1:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
3916 |  |  |  | HR3915 (Lo-16bits)
3917 | NEF1:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
3918 |  |  |  | HR3917 (Lo-16bits)
3919 | NEF1:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
3920 | NEF1:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
3921 | NEF2:I0>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
3922 | NEF2:I0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
3923 | NEF2:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
3924 | NEF2:I0>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
3925 | NEF2:I0>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
3926 |  |  |  | HR3925 (Lo-16bits)
3927 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3928 |  |  |  | HR3927 (Lo-16bits)
3929 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3930 |  |  |  | HR3929 (Lo-16bits)
3931 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3932 |  |  |  | HR3931 (Lo-16bits)
3933 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3934 |  |  |  | HR3933 (Lo-16bits)
3935 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3936 |  |  |  | HR3935 (Lo-16bits)
3937 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3938 |  |  |  | HR3937 (Lo-16bits)
3939 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3940 |  |  |  | HR3939 (Lo-16bits)
3941 | NEF2:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
3942 |  |  |  | HR3941 (Lo-16bits)
3943 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3944 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3945 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3946 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3947 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3948 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3949 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3950 | NEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
3951 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3952 |  |  |  | HR3951 (Lo-16bits)
3953 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3954 |  |  |  | HR3953 (Lo-16bits)
3955 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3956 |  |  |  | HR3955 (Lo-16bits)
3957 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3958 |  |  |  | HR3957 (Lo-16bits)
3959 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3960 |  |  |  | HR3959 (Lo-16bits)
3961 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3962 |  |  |  | HR3961 (Lo-16bits)
3963 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3964 |  |  |  | HR3963 (Lo-16bits)
3965 | NEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
3966 |  |  |  | HR3965 (Lo-16bits)
3967 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3968 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3969 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3970 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3971 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3972 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3973 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3974 | NEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
3975 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3976 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3977 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3978 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3979 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3980 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3981 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3982 | NEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
3983 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3984 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3985 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3986 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3987 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3988 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3989 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3990 | NEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
3991 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3992 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3993 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3994 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3995 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3996 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3997 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3998 | NEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
3999 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4000 |  |  |  | HR3999 (Lo-16bits)
4001 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4002 |  |  |  | HR4001 (Lo-16bits)
4003 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4004 |  |  |  | HR4003 (Lo-16bits)
4005 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4006 |  |  |  | HR4005 (Lo-16bits)
4007 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4008 |  |  |  | HR4007 (Lo-16bits)
4009 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4010 |  |  |  | HR4009 (Lo-16bits)
4011 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4012 |  |  |  | HR4011 (Lo-16bits)
4013 | NEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4014 |  |  |  | HR4013 (Lo-16bits)
4015 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4016 |  |  |  | HR4015 (Lo-16bits)
4017 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4018 |  |  |  | HR4017 (Lo-16bits)
4019 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4020 |  |  |  | HR4019 (Lo-16bits)
4021 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4022 |  |  |  | HR4021 (Lo-16bits)
4023 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4024 |  |  |  | HR4023 (Lo-16bits)
4025 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4026 |  |  |  | HR4025 (Lo-16bits)
4027 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4028 |  |  |  | HR4027 (Lo-16bits)
4029 | NEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4030 |  |  |  | HR4029 (Lo-16bits)
4031 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4032 |  |  |  | HR4031 (Lo-16bits)
4033 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4034 |  |  |  | HR4033 (Lo-16bits)
4035 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4036 |  |  |  | HR4035 (Lo-16bits)
4037 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4038 |  |  |  | HR4037 (Lo-16bits)
4039 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4040 |  |  |  | HR4039 (Lo-16bits)
4041 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4042 |  |  |  | HR4041 (Lo-16bits)
4043 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4044 |  |  |  | HR4043 (Lo-16bits)
4045 | NEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4046 |  |  |  | HR4045 (Lo-16bits)
4047 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4048 |  |  |  | HR4047 (Lo-16bits)
4049 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4050 |  |  |  | HR4049 (Lo-16bits)
4051 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4052 |  |  |  | HR4051 (Lo-16bits)
4053 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4054 |  |  |  | HR4053 (Lo-16bits)
4055 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4056 |  |  |  | HR4055 (Lo-16bits)
4057 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4058 |  |  |  | HR4057 (Lo-16bits)
4059 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4060 |  |  |  | HR4059 (Lo-16bits)
4061 | NEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4062 |  |  |  | HR4061 (Lo-16bits)
4063 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4064 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4065 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4066 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4067 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4068 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4069 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4070 | NEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4071 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4072 |  |  |  | HR4071 (Lo-16bits)
4073 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4074 |  |  |  | HR4073 (Lo-16bits)
4075 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4076 |  |  |  | HR4075 (Lo-16bits)
4077 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4078 |  |  |  | HR4077 (Lo-16bits)
4079 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4080 |  |  |  | HR4079 (Lo-16bits)
4081 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4082 |  |  |  | HR4081 (Lo-16bits)
4083 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4084 |  |  |  | HR4083 (Lo-16bits)
4085 | NEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4086 |  |  |  | HR4085 (Lo-16bits)
4087 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4088 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4089 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4090 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4091 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4092 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4093 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4094 | NEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4095 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4096 |  |  |  | HR4095 (Lo-16bits)
4097 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4098 |  |  |  | HR4097 (Lo-16bits)
4099 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4100 |  |  |  | HR4099 (Lo-16bits)
4101 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4102 |  |  |  | HR4101 (Lo-16bits)
4103 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4104 |  |  |  | HR4103 (Lo-16bits)
4105 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4106 |  |  |  | HR4105 (Lo-16bits)
4107 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4108 |  |  |  | HR4107 (Lo-16bits)
4109 | NEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4110 |  |  |  | HR4109 (Lo-16bits)
4111 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4112 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4113 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4114 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4115 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4116 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4117 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4118 | NEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4119 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4120 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4121 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4122 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4123 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4124 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4125 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4126 | NEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4127 | NEF2:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4128 |  |  |  | HR4127 (Lo-16bits)
4129 | NEF2:Delay type | RW | 1 | 0=DT;1=IDMT
4130 | NEF2:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4131 |  |  |  | HR4130 (Lo-16bits)
4132 | NEF2:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4133 | NEF2:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4134 | NEF2:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4135 | NEF2:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4136 | NEF2:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4137 |  |  |  | HR4136 (Lo-16bits)
4138 | NEF2:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4139 |  |  |  | HR4138 (Lo-16bits)
4140 | NEF2:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4141 |  |  |  | HR4140 (Lo-16bits)
4142 | NEF2:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4143 |  |  |  | HR4142 (Lo-16bits)
4144 | NEF2:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4145 | NEF2:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4146 | NEF3:I0>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4147 | NEF3:I0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4148 | NEF3:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4149 | NEF3:I0>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4150 | NEF3:I0>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4151 |  |  |  | HR4150 (Lo-16bits)
4152 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4153 |  |  |  | HR4152 (Lo-16bits)
4154 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4155 |  |  |  | HR4154 (Lo-16bits)
4156 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4157 |  |  |  | HR4156 (Lo-16bits)
4158 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4159 |  |  |  | HR4158 (Lo-16bits)
4160 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4161 |  |  |  | HR4160 (Lo-16bits)
4162 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4163 |  |  |  | HR4162 (Lo-16bits)
4164 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4165 |  |  |  | HR4164 (Lo-16bits)
4166 | NEF3:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4167 |  |  |  | HR4166 (Lo-16bits)
4168 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4169 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4170 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4171 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4172 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4173 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4174 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4175 | NEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
4176 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4177 |  |  |  | HR4176 (Lo-16bits)
4178 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4179 |  |  |  | HR4178 (Lo-16bits)
4180 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4181 |  |  |  | HR4180 (Lo-16bits)
4182 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4183 |  |  |  | HR4182 (Lo-16bits)
4184 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4185 |  |  |  | HR4184 (Lo-16bits)
4186 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4187 |  |  |  | HR4186 (Lo-16bits)
4188 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4189 |  |  |  | HR4188 (Lo-16bits)
4190 | NEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4191 |  |  |  | HR4190 (Lo-16bits)
4192 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4193 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4194 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4195 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4196 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4197 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4198 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4199 | NEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4200 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4201 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4202 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4203 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4204 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4205 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4206 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4207 | NEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4208 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4209 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4210 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4211 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4212 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4213 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4214 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4215 | NEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4216 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4217 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4218 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4219 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4220 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4221 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4222 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4223 | NEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4224 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4225 |  |  |  | HR4224 (Lo-16bits)
4226 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4227 |  |  |  | HR4226 (Lo-16bits)
4228 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4229 |  |  |  | HR4228 (Lo-16bits)
4230 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4231 |  |  |  | HR4230 (Lo-16bits)
4232 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4233 |  |  |  | HR4232 (Lo-16bits)
4234 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4235 |  |  |  | HR4234 (Lo-16bits)
4236 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4237 |  |  |  | HR4236 (Lo-16bits)
4238 | NEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4239 |  |  |  | HR4238 (Lo-16bits)
4240 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4241 |  |  |  | HR4240 (Lo-16bits)
4242 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4243 |  |  |  | HR4242 (Lo-16bits)
4244 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4245 |  |  |  | HR4244 (Lo-16bits)
4246 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4247 |  |  |  | HR4246 (Lo-16bits)
4248 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4249 |  |  |  | HR4248 (Lo-16bits)
4250 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4251 |  |  |  | HR4250 (Lo-16bits)
4252 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4253 |  |  |  | HR4252 (Lo-16bits)
4254 | NEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4255 |  |  |  | HR4254 (Lo-16bits)
4256 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4257 |  |  |  | HR4256 (Lo-16bits)
4258 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4259 |  |  |  | HR4258 (Lo-16bits)
4260 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4261 |  |  |  | HR4260 (Lo-16bits)
4262 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4263 |  |  |  | HR4262 (Lo-16bits)
4264 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4265 |  |  |  | HR4264 (Lo-16bits)
4266 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4267 |  |  |  | HR4266 (Lo-16bits)
4268 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4269 |  |  |  | HR4268 (Lo-16bits)
4270 | NEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4271 |  |  |  | HR4270 (Lo-16bits)
4272 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4273 |  |  |  | HR4272 (Lo-16bits)
4274 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4275 |  |  |  | HR4274 (Lo-16bits)
4276 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4277 |  |  |  | HR4276 (Lo-16bits)
4278 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4279 |  |  |  | HR4278 (Lo-16bits)
4280 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4281 |  |  |  | HR4280 (Lo-16bits)
4282 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4283 |  |  |  | HR4282 (Lo-16bits)
4284 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4285 |  |  |  | HR4284 (Lo-16bits)
4286 | NEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4287 |  |  |  | HR4286 (Lo-16bits)
4288 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4289 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4290 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4291 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4292 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4293 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4294 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4295 | NEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4296 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4297 |  |  |  | HR4296 (Lo-16bits)
4298 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4299 |  |  |  | HR4298 (Lo-16bits)
4300 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4301 |  |  |  | HR4300 (Lo-16bits)
4302 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4303 |  |  |  | HR4302 (Lo-16bits)
4304 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4305 |  |  |  | HR4304 (Lo-16bits)
4306 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4307 |  |  |  | HR4306 (Lo-16bits)
4308 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4309 |  |  |  | HR4308 (Lo-16bits)
4310 | NEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4311 |  |  |  | HR4310 (Lo-16bits)
4312 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4313 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4314 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4315 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4316 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4317 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4318 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4319 | NEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4320 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4321 |  |  |  | HR4320 (Lo-16bits)
4322 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4323 |  |  |  | HR4322 (Lo-16bits)
4324 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4325 |  |  |  | HR4324 (Lo-16bits)
4326 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4327 |  |  |  | HR4326 (Lo-16bits)
4328 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4329 |  |  |  | HR4328 (Lo-16bits)
4330 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4331 |  |  |  | HR4330 (Lo-16bits)
4332 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4333 |  |  |  | HR4332 (Lo-16bits)
4334 | NEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4335 |  |  |  | HR4334 (Lo-16bits)
4336 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4337 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4338 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4339 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4340 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4341 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4342 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4343 | NEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4344 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4345 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4346 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4347 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4348 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4349 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4350 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4351 | NEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4352 | NEF3:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4353 |  |  |  | HR4352 (Lo-16bits)
4354 | NEF3:Delay type | RW | 1 | 0=DT;1=IDMT
4355 | NEF3:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4356 |  |  |  | HR4355 (Lo-16bits)
4357 | NEF3:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4358 | NEF3:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4359 | NEF3:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4360 | NEF3:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4361 | NEF3:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4362 |  |  |  | HR4361 (Lo-16bits)
4363 | NEF3:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4364 |  |  |  | HR4363 (Lo-16bits)
4365 | NEF3:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4366 |  |  |  | HR4365 (Lo-16bits)
4367 | NEF3:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4368 |  |  |  | HR4367 (Lo-16bits)
4369 | NEF3:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4370 | NEF3:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4371 | NEF4:I0>>>> [50N/51N] mode | R(W) | 1 | 0=Disabled;1=Activated
4372 | NEF4:I0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
4373 | NEF4:Detected fault type | R | 1 | 0=-;1=A-G-R;2=B-G-F;3=C-G-R;4=A-G-F;5=B-G-R;6=C-G-F
4374 | NEF4:I0>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4375 | NEF4:I0>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4376 |  |  |  | HR4375 (Lo-16bits)
4377 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4378 |  |  |  | HR4377 (Lo-16bits)
4379 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4380 |  |  |  | HR4379 (Lo-16bits)
4381 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4382 |  |  |  | HR4381 (Lo-16bits)
4383 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4384 |  |  |  | HR4383 (Lo-16bits)
4385 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4386 |  |  |  | HR4385 (Lo-16bits)
4387 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4388 |  |  |  | HR4387 (Lo-16bits)
4389 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4390 |  |  |  | HR4389 (Lo-16bits)
4391 | NEF4:Pick-up setting I0set | R(W) | 2 | FLOAT [0.0001...40] (Hi-16bits)
4392 |  |  |  | HR4391 (Lo-16bits)
4393 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4394 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4395 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4396 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4397 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4398 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4399 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4400 | NEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
4401 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4402 |  |  |  | HR4401 (Lo-16bits)
4403 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4404 |  |  |  | HR4403 (Lo-16bits)
4405 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4406 |  |  |  | HR4405 (Lo-16bits)
4407 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4408 |  |  |  | HR4407 (Lo-16bits)
4409 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4410 |  |  |  | HR4409 (Lo-16bits)
4411 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4412 |  |  |  | HR4411 (Lo-16bits)
4413 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4414 |  |  |  | HR4413 (Lo-16bits)
4415 | NEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4416 |  |  |  | HR4415 (Lo-16bits)
4417 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4418 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4419 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4420 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4421 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4422 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4423 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4424 | NEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4425 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4426 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4427 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4428 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4429 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4430 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4431 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4432 | NEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4433 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4434 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4435 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4436 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4437 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4438 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4439 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4440 | NEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4441 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4442 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4443 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4444 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4445 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4446 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4447 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4448 | NEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4449 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4450 |  |  |  | HR4449 (Lo-16bits)
4451 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4452 |  |  |  | HR4451 (Lo-16bits)
4453 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4454 |  |  |  | HR4453 (Lo-16bits)
4455 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4456 |  |  |  | HR4455 (Lo-16bits)
4457 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4458 |  |  |  | HR4457 (Lo-16bits)
4459 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4460 |  |  |  | HR4459 (Lo-16bits)
4461 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4462 |  |  |  | HR4461 (Lo-16bits)
4463 | NEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4464 |  |  |  | HR4463 (Lo-16bits)
4465 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4466 |  |  |  | HR4465 (Lo-16bits)
4467 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4468 |  |  |  | HR4467 (Lo-16bits)
4469 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4470 |  |  |  | HR4469 (Lo-16bits)
4471 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4472 |  |  |  | HR4471 (Lo-16bits)
4473 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4474 |  |  |  | HR4473 (Lo-16bits)
4475 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4476 |  |  |  | HR4475 (Lo-16bits)
4477 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4478 |  |  |  | HR4477 (Lo-16bits)
4479 | NEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4480 |  |  |  | HR4479 (Lo-16bits)
4481 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4482 |  |  |  | HR4481 (Lo-16bits)
4483 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4484 |  |  |  | HR4483 (Lo-16bits)
4485 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4486 |  |  |  | HR4485 (Lo-16bits)
4487 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4488 |  |  |  | HR4487 (Lo-16bits)
4489 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4490 |  |  |  | HR4489 (Lo-16bits)
4491 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4492 |  |  |  | HR4491 (Lo-16bits)
4493 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4494 |  |  |  | HR4493 (Lo-16bits)
4495 | NEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4496 |  |  |  | HR4495 (Lo-16bits)
4497 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4498 |  |  |  | HR4497 (Lo-16bits)
4499 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4500 |  |  |  | HR4499 (Lo-16bits)
4501 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4502 |  |  |  | HR4501 (Lo-16bits)
4503 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4504 |  |  |  | HR4503 (Lo-16bits)
4505 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4506 |  |  |  | HR4505 (Lo-16bits)
4507 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4508 |  |  |  | HR4507 (Lo-16bits)
4509 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4510 |  |  |  | HR4509 (Lo-16bits)
4511 | NEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4512 |  |  |  | HR4511 (Lo-16bits)
4513 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4514 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4515 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4516 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4517 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4518 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4519 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4520 | NEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4521 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4522 |  |  |  | HR4521 (Lo-16bits)
4523 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4524 |  |  |  | HR4523 (Lo-16bits)
4525 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4526 |  |  |  | HR4525 (Lo-16bits)
4527 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4528 |  |  |  | HR4527 (Lo-16bits)
4529 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4530 |  |  |  | HR4529 (Lo-16bits)
4531 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4532 |  |  |  | HR4531 (Lo-16bits)
4533 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4534 |  |  |  | HR4533 (Lo-16bits)
4535 | NEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4536 |  |  |  | HR4535 (Lo-16bits)
4537 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4538 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4539 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4540 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4541 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4542 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4543 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4544 | NEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4545 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4546 |  |  |  | HR4545 (Lo-16bits)
4547 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4548 |  |  |  | HR4547 (Lo-16bits)
4549 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4550 |  |  |  | HR4549 (Lo-16bits)
4551 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4552 |  |  |  | HR4551 (Lo-16bits)
4553 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4554 |  |  |  | HR4553 (Lo-16bits)
4555 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4556 |  |  |  | HR4555 (Lo-16bits)
4557 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4558 |  |  |  | HR4557 (Lo-16bits)
4559 | NEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4560 |  |  |  | HR4559 (Lo-16bits)
4561 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4562 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4563 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4564 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4565 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4566 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4567 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4568 | NEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
4569 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4570 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4571 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4572 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4573 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4574 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4575 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4576 | NEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
4577 | NEF4:Pick-up setting Iset | RW | 2 | FLOAT [0.1...50] (Hi-16bits)
4578 |  |  |  | HR4577 (Lo-16bits)
4579 | NEF4:Delay type | RW | 1 | 0=DT;1=IDMT
4580 | NEF4:Definite (minimum) operating time delay | RW | 2 | FLOAT [0...1800] (Hi-16bits)
4581 |  |  |  | HR4580 (Lo-16bits)
4582 | NEF4:Delay curve series | RW | 1 | 0=IEC;1=IEEE;2=Non standard
4583 | NEF4:Delay characteristics IEC | RW | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4584 | NEF4:Delay char. ANSI/IEEE | RW | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4585 | NEF4:Non standard Delay char. | RW | 1 | 0=RI-type;1=RD-type
4586 | NEF4:Time dial setting k | RW | 2 | FLOAT [0.01...25] (Hi-16bits)
4587 |  |  |  | HR4586 (Lo-16bits)
4588 | NEF4:IDMT Const. A | RW | 2 | FLOAT [0...250] (Hi-16bits)
4589 |  |  |  | HR4588 (Lo-16bits)
4590 | NEF4:IDMT Const. B | RW | 2 | FLOAT [0...250] (Hi-16bits)
4591 |  |  |  | HR4590 (Lo-16bits)
4592 | NEF4:IDMT Const. C | RW | 2 | FLOAT [0...250] (Hi-16bits)
4593 |  |  |  | HR4592 (Lo-16bits)
4594 | NEF4:Select SG | RW | 1 | 0=SG1;1=SG2;2=SG3;3=SG4;4=SG5;5=SG6;6=SG7;7=SG8;8=Edit Active SG
4595 | NEF4:Write settings to selected SG | RW | 1 | 0=-;1=Write (autoreset)
4596 | DEF1:I0dir> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
4597 | DEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
4598 | DEF1:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
4599 | DEF1:I0dir> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
4600 | DEF1:I0dir> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
4601 |  |  |  | HR4600 (Lo-16bits)
4602 | DEF1:I0dir> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4603 |  |  |  | HR4602 (Lo-16bits)
4604 | DEF1:I0dir> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
4605 |  |  |  | HR4604 (Lo-16bits)
4606 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4607 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4608 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4609 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4610 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4611 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4612 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4613 | DEF1:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
4614 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4615 |  |  |  | HR4614 (Lo-16bits)
4616 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4617 |  |  |  | HR4616 (Lo-16bits)
4618 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4619 |  |  |  | HR4618 (Lo-16bits)
4620 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4621 |  |  |  | HR4620 (Lo-16bits)
4622 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4623 |  |  |  | HR4622 (Lo-16bits)
4624 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4625 |  |  |  | HR4624 (Lo-16bits)
4626 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4627 |  |  |  | HR4626 (Lo-16bits)
4628 | DEF1:Pick-up setting I0set> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4629 |  |  |  | HR4628 (Lo-16bits)
4630 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4631 |  |  |  | HR4630 (Lo-16bits)
4632 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4633 |  |  |  | HR4632 (Lo-16bits)
4634 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4635 |  |  |  | HR4634 (Lo-16bits)
4636 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4637 |  |  |  | HR4636 (Lo-16bits)
4638 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4639 |  |  |  | HR4638 (Lo-16bits)
4640 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4641 |  |  |  | HR4640 (Lo-16bits)
4642 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4643 |  |  |  | HR4642 (Lo-16bits)
4644 | DEF1:Pick-up setting U0set> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4645 |  |  |  | HR4644 (Lo-16bits)
4646 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4647 |  |  |  | HR4646 (Lo-16bits)
4648 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4649 |  |  |  | HR4648 (Lo-16bits)
4650 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4651 |  |  |  | HR4650 (Lo-16bits)
4652 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4653 |  |  |  | HR4652 (Lo-16bits)
4654 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4655 |  |  |  | HR4654 (Lo-16bits)
4656 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4657 |  |  |  | HR4656 (Lo-16bits)
4658 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4659 |  |  |  | HR4658 (Lo-16bits)
4660 | DEF1:Comp. Pick-up setting I0set (I0Cosfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4661 |  |  |  | HR4660 (Lo-16bits)
4662 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4663 |  |  |  | HR4662 (Lo-16bits)
4664 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4665 |  |  |  | HR4664 (Lo-16bits)
4666 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4667 |  |  |  | HR4666 (Lo-16bits)
4668 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4669 |  |  |  | HR4668 (Lo-16bits)
4670 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4671 |  |  |  | HR4670 (Lo-16bits)
4672 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4673 |  |  |  | HR4672 (Lo-16bits)
4674 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4675 |  |  |  | HR4674 (Lo-16bits)
4676 | DEF1:Comp. Pick-up setting U0set(I0Cosfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4677 |  |  |  | HR4676 (Lo-16bits)
4678 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4679 |  |  |  | HR4678 (Lo-16bits)
4680 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4681 |  |  |  | HR4680 (Lo-16bits)
4682 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4683 |  |  |  | HR4682 (Lo-16bits)
4684 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4685 |  |  |  | HR4684 (Lo-16bits)
4686 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4687 |  |  |  | HR4686 (Lo-16bits)
4688 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4689 |  |  |  | HR4688 (Lo-16bits)
4690 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4691 |  |  |  | HR4690 (Lo-16bits)
4692 | DEF1:Unearthed / Compensated border angle (0 = not in use) | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
4693 |  |  |  | HR4692 (Lo-16bits)
4694 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4695 |  |  |  | HR4694 (Lo-16bits)
4696 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4697 |  |  |  | HR4696 (Lo-16bits)
4698 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4699 |  |  |  | HR4698 (Lo-16bits)
4700 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4701 |  |  |  | HR4700 (Lo-16bits)
4702 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4703 |  |  |  | HR4702 (Lo-16bits)
4704 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4705 |  |  |  | HR4704 (Lo-16bits)
4706 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4707 |  |  |  | HR4706 (Lo-16bits)
4708 | DEF1:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
4709 |  |  |  | HR4708 (Lo-16bits)
4710 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4711 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4712 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4713 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4714 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4715 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4716 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4717 | DEF1:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
4718 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4719 |  |  |  | HR4718 (Lo-16bits)
4720 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4721 |  |  |  | HR4720 (Lo-16bits)
4722 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4723 |  |  |  | HR4722 (Lo-16bits)
4724 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4725 |  |  |  | HR4724 (Lo-16bits)
4726 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4727 |  |  |  | HR4726 (Lo-16bits)
4728 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4729 |  |  |  | HR4728 (Lo-16bits)
4730 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4731 |  |  |  | HR4730 (Lo-16bits)
4732 | DEF1:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
4733 |  |  |  | HR4732 (Lo-16bits)
4734 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4735 |  |  |  | HR4734 (Lo-16bits)
4736 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4737 |  |  |  | HR4736 (Lo-16bits)
4738 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4739 |  |  |  | HR4738 (Lo-16bits)
4740 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4741 |  |  |  | HR4740 (Lo-16bits)
4742 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4743 |  |  |  | HR4742 (Lo-16bits)
4744 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4745 |  |  |  | HR4744 (Lo-16bits)
4746 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4747 |  |  |  | HR4746 (Lo-16bits)
4748 | DEF1:Unearth. Pick-up setting I0set (I0Sinfi)> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
4749 |  |  |  | HR4748 (Lo-16bits)
4750 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4751 |  |  |  | HR4750 (Lo-16bits)
4752 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4753 |  |  |  | HR4752 (Lo-16bits)
4754 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4755 |  |  |  | HR4754 (Lo-16bits)
4756 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4757 |  |  |  | HR4756 (Lo-16bits)
4758 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4759 |  |  |  | HR4758 (Lo-16bits)
4760 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4761 |  |  |  | HR4760 (Lo-16bits)
4762 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4763 |  |  |  | HR4762 (Lo-16bits)
4764 | DEF1:Unearth. Pick-up setting U0set(I0Sinfi)> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
4765 |  |  |  | HR4764 (Lo-16bits)
4766 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4767 |  |  |  | HR4766 (Lo-16bits)
4768 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4769 |  |  |  | HR4768 (Lo-16bits)
4770 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4771 |  |  |  | HR4770 (Lo-16bits)
4772 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4773 |  |  |  | HR4772 (Lo-16bits)
4774 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4775 |  |  |  | HR4774 (Lo-16bits)
4776 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4777 |  |  |  | HR4776 (Lo-16bits)
4778 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4779 |  |  |  | HR4778 (Lo-16bits)
4780 | DEF1:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
4781 |  |  |  | HR4780 (Lo-16bits)
4782 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4783 |  |  |  | HR4782 (Lo-16bits)
4784 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4785 |  |  |  | HR4784 (Lo-16bits)
4786 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4787 |  |  |  | HR4786 (Lo-16bits)
4788 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4789 |  |  |  | HR4788 (Lo-16bits)
4790 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4791 |  |  |  | HR4790 (Lo-16bits)
4792 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4793 |  |  |  | HR4792 (Lo-16bits)
4794 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4795 |  |  |  | HR4794 (Lo-16bits)
4796 | DEF1:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
4797 |  |  |  | HR4796 (Lo-16bits)
4798 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4799 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4800 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4801 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4802 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4803 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4804 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4805 | DEF1:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
4806 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4807 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4808 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4809 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4810 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4811 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4812 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4813 | DEF1:Delay type | R(W) | 1 | 0=DT;1=IDMT
4814 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4815 |  |  |  | HR4814 (Lo-16bits)
4816 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4817 |  |  |  | HR4816 (Lo-16bits)
4818 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4819 |  |  |  | HR4818 (Lo-16bits)
4820 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4821 |  |  |  | HR4820 (Lo-16bits)
4822 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4823 |  |  |  | HR4822 (Lo-16bits)
4824 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4825 |  |  |  | HR4824 (Lo-16bits)
4826 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4827 |  |  |  | HR4826 (Lo-16bits)
4828 | DEF1:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4829 |  |  |  | HR4828 (Lo-16bits)
4830 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4831 |  |  |  | HR4830 (Lo-16bits)
4832 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4833 |  |  |  | HR4832 (Lo-16bits)
4834 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4835 |  |  |  | HR4834 (Lo-16bits)
4836 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4837 |  |  |  | HR4836 (Lo-16bits)
4838 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4839 |  |  |  | HR4838 (Lo-16bits)
4840 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4841 |  |  |  | HR4840 (Lo-16bits)
4842 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4843 |  |  |  | HR4842 (Lo-16bits)
4844 | DEF1:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4845 |  |  |  | HR4844 (Lo-16bits)
4846 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4847 |  |  |  | HR4846 (Lo-16bits)
4848 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4849 |  |  |  | HR4848 (Lo-16bits)
4850 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4851 |  |  |  | HR4850 (Lo-16bits)
4852 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4853 |  |  |  | HR4852 (Lo-16bits)
4854 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4855 |  |  |  | HR4854 (Lo-16bits)
4856 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4857 |  |  |  | HR4856 (Lo-16bits)
4858 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4859 |  |  |  | HR4858 (Lo-16bits)
4860 | DEF1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
4861 |  |  |  | HR4860 (Lo-16bits)
4862 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4863 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4864 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4865 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4866 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4867 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4868 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4869 | DEF1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
4870 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4871 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4872 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4873 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4874 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4875 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4876 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4877 | DEF1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
4878 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4879 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4880 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4881 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4882 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4883 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4884 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4885 | DEF1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
4886 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4887 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4888 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4889 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4890 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4891 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4892 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4893 | DEF1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
4894 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4895 |  |  |  | HR4894 (Lo-16bits)
4896 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4897 |  |  |  | HR4896 (Lo-16bits)
4898 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4899 |  |  |  | HR4898 (Lo-16bits)
4900 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4901 |  |  |  | HR4900 (Lo-16bits)
4902 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4903 |  |  |  | HR4902 (Lo-16bits)
4904 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4905 |  |  |  | HR4904 (Lo-16bits)
4906 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4907 |  |  |  | HR4906 (Lo-16bits)
4908 | DEF1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
4909 |  |  |  | HR4908 (Lo-16bits)
4910 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4911 |  |  |  | HR4910 (Lo-16bits)
4912 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4913 |  |  |  | HR4912 (Lo-16bits)
4914 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4915 |  |  |  | HR4914 (Lo-16bits)
4916 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4917 |  |  |  | HR4916 (Lo-16bits)
4918 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4919 |  |  |  | HR4918 (Lo-16bits)
4920 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4921 |  |  |  | HR4920 (Lo-16bits)
4922 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4923 |  |  |  | HR4922 (Lo-16bits)
4924 | DEF1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4925 |  |  |  | HR4924 (Lo-16bits)
4926 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4927 |  |  |  | HR4926 (Lo-16bits)
4928 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4929 |  |  |  | HR4928 (Lo-16bits)
4930 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4931 |  |  |  | HR4930 (Lo-16bits)
4932 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4933 |  |  |  | HR4932 (Lo-16bits)
4934 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4935 |  |  |  | HR4934 (Lo-16bits)
4936 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4937 |  |  |  | HR4936 (Lo-16bits)
4938 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4939 |  |  |  | HR4938 (Lo-16bits)
4940 | DEF1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4941 |  |  |  | HR4940 (Lo-16bits)
4942 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4943 |  |  |  | HR4942 (Lo-16bits)
4944 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4945 |  |  |  | HR4944 (Lo-16bits)
4946 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4947 |  |  |  | HR4946 (Lo-16bits)
4948 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4949 |  |  |  | HR4948 (Lo-16bits)
4950 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4951 |  |  |  | HR4950 (Lo-16bits)
4952 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4953 |  |  |  | HR4952 (Lo-16bits)
4954 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4955 |  |  |  | HR4954 (Lo-16bits)
4956 | DEF1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
4957 |  |  |  | HR4956 (Lo-16bits)
4958 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4959 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4960 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4961 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4962 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4963 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4964 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4965 | DEF1:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
4966 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4967 |  |  |  | HR4966 (Lo-16bits)
4968 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4969 |  |  |  | HR4968 (Lo-16bits)
4970 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4971 |  |  |  | HR4970 (Lo-16bits)
4972 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4973 |  |  |  | HR4972 (Lo-16bits)
4974 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4975 |  |  |  | HR4974 (Lo-16bits)
4976 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4977 |  |  |  | HR4976 (Lo-16bits)
4978 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4979 |  |  |  | HR4978 (Lo-16bits)
4980 | DEF1:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
4981 |  |  |  | HR4980 (Lo-16bits)
4982 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4983 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4984 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4985 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4986 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4987 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4988 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4989 | DEF1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
4990 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4991 |  |  |  | HR4990 (Lo-16bits)
4992 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4993 |  |  |  | HR4992 (Lo-16bits)
4994 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4995 |  |  |  | HR4994 (Lo-16bits)
4996 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4997 |  |  |  | HR4996 (Lo-16bits)
4998 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
4999 |  |  |  | HR4998 (Lo-16bits)
5000 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5001 |  |  |  | HR5000 (Lo-16bits)
5002 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5003 |  |  |  | HR5002 (Lo-16bits)
5004 | DEF1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5005 |  |  |  | HR5004 (Lo-16bits)
5006 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5007 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5008 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5009 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5010 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5011 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5012 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5013 | DEF1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5014 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5015 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5016 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5017 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5018 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5019 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5020 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5021 | DEF1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5022 | DEF2:I0dir>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5023 | DEF2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5024 | DEF2:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5025 | DEF2:I0dir>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5026 | DEF2:I0dir>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5027 |  |  |  | HR5026 (Lo-16bits)
5028 | DEF2:I0dir>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5029 |  |  |  | HR5028 (Lo-16bits)
5030 | DEF2:I0dir>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5031 |  |  |  | HR5030 (Lo-16bits)
5032 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5033 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5034 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5035 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5036 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5037 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5038 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5039 | DEF2:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5040 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5041 |  |  |  | HR5040 (Lo-16bits)
5042 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5043 |  |  |  | HR5042 (Lo-16bits)
5044 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5045 |  |  |  | HR5044 (Lo-16bits)
5046 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5047 |  |  |  | HR5046 (Lo-16bits)
5048 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5049 |  |  |  | HR5048 (Lo-16bits)
5050 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5051 |  |  |  | HR5050 (Lo-16bits)
5052 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5053 |  |  |  | HR5052 (Lo-16bits)
5054 | DEF2:Pick-up setting I0set>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5055 |  |  |  | HR5054 (Lo-16bits)
5056 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5057 |  |  |  | HR5056 (Lo-16bits)
5058 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5059 |  |  |  | HR5058 (Lo-16bits)
5060 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5061 |  |  |  | HR5060 (Lo-16bits)
5062 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5063 |  |  |  | HR5062 (Lo-16bits)
5064 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5065 |  |  |  | HR5064 (Lo-16bits)
5066 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5067 |  |  |  | HR5066 (Lo-16bits)
5068 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5069 |  |  |  | HR5068 (Lo-16bits)
5070 | DEF2:Pick-up setting U0set>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5071 |  |  |  | HR5070 (Lo-16bits)
5072 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5073 |  |  |  | HR5072 (Lo-16bits)
5074 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5075 |  |  |  | HR5074 (Lo-16bits)
5076 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5077 |  |  |  | HR5076 (Lo-16bits)
5078 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5079 |  |  |  | HR5078 (Lo-16bits)
5080 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5081 |  |  |  | HR5080 (Lo-16bits)
5082 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5083 |  |  |  | HR5082 (Lo-16bits)
5084 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5085 |  |  |  | HR5084 (Lo-16bits)
5086 | DEF2:Comp. Pick-up setting I0set (I0Cosfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5087 |  |  |  | HR5086 (Lo-16bits)
5088 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5089 |  |  |  | HR5088 (Lo-16bits)
5090 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5091 |  |  |  | HR5090 (Lo-16bits)
5092 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5093 |  |  |  | HR5092 (Lo-16bits)
5094 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5095 |  |  |  | HR5094 (Lo-16bits)
5096 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5097 |  |  |  | HR5096 (Lo-16bits)
5098 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5099 |  |  |  | HR5098 (Lo-16bits)
5100 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5101 |  |  |  | HR5100 (Lo-16bits)
5102 | DEF2:Comp. Pick-up setting U0set(I0Cosfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5103 |  |  |  | HR5102 (Lo-16bits)
5104 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5105 |  |  |  | HR5104 (Lo-16bits)
5106 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5107 |  |  |  | HR5106 (Lo-16bits)
5108 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5109 |  |  |  | HR5108 (Lo-16bits)
5110 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5111 |  |  |  | HR5110 (Lo-16bits)
5112 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5113 |  |  |  | HR5112 (Lo-16bits)
5114 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5115 |  |  |  | HR5114 (Lo-16bits)
5116 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5117 |  |  |  | HR5116 (Lo-16bits)
5118 | DEF2:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5119 |  |  |  | HR5118 (Lo-16bits)
5120 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5121 |  |  |  | HR5120 (Lo-16bits)
5122 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5123 |  |  |  | HR5122 (Lo-16bits)
5124 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5125 |  |  |  | HR5124 (Lo-16bits)
5126 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5127 |  |  |  | HR5126 (Lo-16bits)
5128 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5129 |  |  |  | HR5128 (Lo-16bits)
5130 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5131 |  |  |  | HR5130 (Lo-16bits)
5132 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5133 |  |  |  | HR5132 (Lo-16bits)
5134 | DEF2:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5135 |  |  |  | HR5134 (Lo-16bits)
5136 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5137 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5138 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5139 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5140 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5141 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5142 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5143 | DEF2:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5144 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5145 |  |  |  | HR5144 (Lo-16bits)
5146 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5147 |  |  |  | HR5146 (Lo-16bits)
5148 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5149 |  |  |  | HR5148 (Lo-16bits)
5150 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5151 |  |  |  | HR5150 (Lo-16bits)
5152 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5153 |  |  |  | HR5152 (Lo-16bits)
5154 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5155 |  |  |  | HR5154 (Lo-16bits)
5156 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5157 |  |  |  | HR5156 (Lo-16bits)
5158 | DEF2:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5159 |  |  |  | HR5158 (Lo-16bits)
5160 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5161 |  |  |  | HR5160 (Lo-16bits)
5162 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5163 |  |  |  | HR5162 (Lo-16bits)
5164 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5165 |  |  |  | HR5164 (Lo-16bits)
5166 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5167 |  |  |  | HR5166 (Lo-16bits)
5168 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5169 |  |  |  | HR5168 (Lo-16bits)
5170 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5171 |  |  |  | HR5170 (Lo-16bits)
5172 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5173 |  |  |  | HR5172 (Lo-16bits)
5174 | DEF2:Unearth. Pick-up setting I0set (I0Sinfi)>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5175 |  |  |  | HR5174 (Lo-16bits)
5176 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5177 |  |  |  | HR5176 (Lo-16bits)
5178 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5179 |  |  |  | HR5178 (Lo-16bits)
5180 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5181 |  |  |  | HR5180 (Lo-16bits)
5182 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5183 |  |  |  | HR5182 (Lo-16bits)
5184 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5185 |  |  |  | HR5184 (Lo-16bits)
5186 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5187 |  |  |  | HR5186 (Lo-16bits)
5188 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5189 |  |  |  | HR5188 (Lo-16bits)
5190 | DEF2:Unearth. Pick-up setting U0set(I0Sinfi)>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5191 |  |  |  | HR5190 (Lo-16bits)
5192 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5193 |  |  |  | HR5192 (Lo-16bits)
5194 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5195 |  |  |  | HR5194 (Lo-16bits)
5196 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5197 |  |  |  | HR5196 (Lo-16bits)
5198 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5199 |  |  |  | HR5198 (Lo-16bits)
5200 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5201 |  |  |  | HR5200 (Lo-16bits)
5202 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5203 |  |  |  | HR5202 (Lo-16bits)
5204 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5205 |  |  |  | HR5204 (Lo-16bits)
5206 | DEF2:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5207 |  |  |  | HR5206 (Lo-16bits)
5208 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5209 |  |  |  | HR5208 (Lo-16bits)
5210 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5211 |  |  |  | HR5210 (Lo-16bits)
5212 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5213 |  |  |  | HR5212 (Lo-16bits)
5214 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5215 |  |  |  | HR5214 (Lo-16bits)
5216 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5217 |  |  |  | HR5216 (Lo-16bits)
5218 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5219 |  |  |  | HR5218 (Lo-16bits)
5220 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5221 |  |  |  | HR5220 (Lo-16bits)
5222 | DEF2:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5223 |  |  |  | HR5222 (Lo-16bits)
5224 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5225 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5226 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5227 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5228 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5229 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5230 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5231 | DEF2:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5232 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5233 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5234 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5235 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5236 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5237 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5238 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5239 | DEF2:Delay type | R(W) | 1 | 0=DT;1=IDMT
5240 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5241 |  |  |  | HR5240 (Lo-16bits)
5242 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5243 |  |  |  | HR5242 (Lo-16bits)
5244 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5245 |  |  |  | HR5244 (Lo-16bits)
5246 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5247 |  |  |  | HR5246 (Lo-16bits)
5248 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5249 |  |  |  | HR5248 (Lo-16bits)
5250 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5251 |  |  |  | HR5250 (Lo-16bits)
5252 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5253 |  |  |  | HR5252 (Lo-16bits)
5254 | DEF2:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5255 |  |  |  | HR5254 (Lo-16bits)
5256 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5257 |  |  |  | HR5256 (Lo-16bits)
5258 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5259 |  |  |  | HR5258 (Lo-16bits)
5260 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5261 |  |  |  | HR5260 (Lo-16bits)
5262 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5263 |  |  |  | HR5262 (Lo-16bits)
5264 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5265 |  |  |  | HR5264 (Lo-16bits)
5266 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5267 |  |  |  | HR5266 (Lo-16bits)
5268 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5269 |  |  |  | HR5268 (Lo-16bits)
5270 | DEF2:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5271 |  |  |  | HR5270 (Lo-16bits)
5272 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5273 |  |  |  | HR5272 (Lo-16bits)
5274 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5275 |  |  |  | HR5274 (Lo-16bits)
5276 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5277 |  |  |  | HR5276 (Lo-16bits)
5278 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5279 |  |  |  | HR5278 (Lo-16bits)
5280 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5281 |  |  |  | HR5280 (Lo-16bits)
5282 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5283 |  |  |  | HR5282 (Lo-16bits)
5284 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5285 |  |  |  | HR5284 (Lo-16bits)
5286 | DEF2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5287 |  |  |  | HR5286 (Lo-16bits)
5288 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5289 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5290 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5291 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5292 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5293 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5294 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5295 | DEF2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5296 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5297 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5298 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5299 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5300 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5301 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5302 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5303 | DEF2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5304 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5305 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5306 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5307 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5308 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5309 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5310 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5311 | DEF2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5312 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5313 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5314 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5315 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5316 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5317 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5318 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5319 | DEF2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5320 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5321 |  |  |  | HR5320 (Lo-16bits)
5322 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5323 |  |  |  | HR5322 (Lo-16bits)
5324 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5325 |  |  |  | HR5324 (Lo-16bits)
5326 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5327 |  |  |  | HR5326 (Lo-16bits)
5328 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5329 |  |  |  | HR5328 (Lo-16bits)
5330 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5331 |  |  |  | HR5330 (Lo-16bits)
5332 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5333 |  |  |  | HR5332 (Lo-16bits)
5334 | DEF2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5335 |  |  |  | HR5334 (Lo-16bits)
5336 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5337 |  |  |  | HR5336 (Lo-16bits)
5338 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5339 |  |  |  | HR5338 (Lo-16bits)
5340 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5341 |  |  |  | HR5340 (Lo-16bits)
5342 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5343 |  |  |  | HR5342 (Lo-16bits)
5344 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5345 |  |  |  | HR5344 (Lo-16bits)
5346 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5347 |  |  |  | HR5346 (Lo-16bits)
5348 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5349 |  |  |  | HR5348 (Lo-16bits)
5350 | DEF2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5351 |  |  |  | HR5350 (Lo-16bits)
5352 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5353 |  |  |  | HR5352 (Lo-16bits)
5354 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5355 |  |  |  | HR5354 (Lo-16bits)
5356 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5357 |  |  |  | HR5356 (Lo-16bits)
5358 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5359 |  |  |  | HR5358 (Lo-16bits)
5360 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5361 |  |  |  | HR5360 (Lo-16bits)
5362 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5363 |  |  |  | HR5362 (Lo-16bits)
5364 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5365 |  |  |  | HR5364 (Lo-16bits)
5366 | DEF2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5367 |  |  |  | HR5366 (Lo-16bits)
5368 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5369 |  |  |  | HR5368 (Lo-16bits)
5370 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5371 |  |  |  | HR5370 (Lo-16bits)
5372 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5373 |  |  |  | HR5372 (Lo-16bits)
5374 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5375 |  |  |  | HR5374 (Lo-16bits)
5376 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5377 |  |  |  | HR5376 (Lo-16bits)
5378 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5379 |  |  |  | HR5378 (Lo-16bits)
5380 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5381 |  |  |  | HR5380 (Lo-16bits)
5382 | DEF2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5383 |  |  |  | HR5382 (Lo-16bits)
5384 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5385 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5386 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5387 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5388 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5389 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5390 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5391 | DEF2:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5392 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5393 |  |  |  | HR5392 (Lo-16bits)
5394 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5395 |  |  |  | HR5394 (Lo-16bits)
5396 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5397 |  |  |  | HR5396 (Lo-16bits)
5398 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5399 |  |  |  | HR5398 (Lo-16bits)
5400 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5401 |  |  |  | HR5400 (Lo-16bits)
5402 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5403 |  |  |  | HR5402 (Lo-16bits)
5404 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5405 |  |  |  | HR5404 (Lo-16bits)
5406 | DEF2:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5407 |  |  |  | HR5406 (Lo-16bits)
5408 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5409 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5410 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5411 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5412 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5413 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5414 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5415 | DEF2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5416 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5417 |  |  |  | HR5416 (Lo-16bits)
5418 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5419 |  |  |  | HR5418 (Lo-16bits)
5420 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5421 |  |  |  | HR5420 (Lo-16bits)
5422 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5423 |  |  |  | HR5422 (Lo-16bits)
5424 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5425 |  |  |  | HR5424 (Lo-16bits)
5426 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5427 |  |  |  | HR5426 (Lo-16bits)
5428 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5429 |  |  |  | HR5428 (Lo-16bits)
5430 | DEF2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5431 |  |  |  | HR5430 (Lo-16bits)
5432 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5433 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5434 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5435 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5436 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5437 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5438 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5439 | DEF2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5440 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5441 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5442 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5443 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5444 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5445 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5446 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5447 | DEF2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5448 | DEF3:I0dir>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5449 | DEF3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5450 | DEF3:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5451 | DEF3:I0dir>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5452 | DEF3:I0dir>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5453 |  |  |  | HR5452 (Lo-16bits)
5454 | DEF3:I0dir>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5455 |  |  |  | HR5454 (Lo-16bits)
5456 | DEF3:I0dir>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5457 |  |  |  | HR5456 (Lo-16bits)
5458 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5459 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5460 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5461 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5462 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5463 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5464 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5465 | DEF3:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5466 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5467 |  |  |  | HR5466 (Lo-16bits)
5468 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5469 |  |  |  | HR5468 (Lo-16bits)
5470 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5471 |  |  |  | HR5470 (Lo-16bits)
5472 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5473 |  |  |  | HR5472 (Lo-16bits)
5474 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5475 |  |  |  | HR5474 (Lo-16bits)
5476 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5477 |  |  |  | HR5476 (Lo-16bits)
5478 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5479 |  |  |  | HR5478 (Lo-16bits)
5480 | DEF3:Pick-up setting I0set>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5481 |  |  |  | HR5480 (Lo-16bits)
5482 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5483 |  |  |  | HR5482 (Lo-16bits)
5484 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5485 |  |  |  | HR5484 (Lo-16bits)
5486 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5487 |  |  |  | HR5486 (Lo-16bits)
5488 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5489 |  |  |  | HR5488 (Lo-16bits)
5490 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5491 |  |  |  | HR5490 (Lo-16bits)
5492 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5493 |  |  |  | HR5492 (Lo-16bits)
5494 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5495 |  |  |  | HR5494 (Lo-16bits)
5496 | DEF3:Pick-up setting U0set>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5497 |  |  |  | HR5496 (Lo-16bits)
5498 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5499 |  |  |  | HR5498 (Lo-16bits)
5500 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5501 |  |  |  | HR5500 (Lo-16bits)
5502 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5503 |  |  |  | HR5502 (Lo-16bits)
5504 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5505 |  |  |  | HR5504 (Lo-16bits)
5506 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5507 |  |  |  | HR5506 (Lo-16bits)
5508 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5509 |  |  |  | HR5508 (Lo-16bits)
5510 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5511 |  |  |  | HR5510 (Lo-16bits)
5512 | DEF3:Comp. Pick-up setting I0set (I0Cosfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5513 |  |  |  | HR5512 (Lo-16bits)
5514 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5515 |  |  |  | HR5514 (Lo-16bits)
5516 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5517 |  |  |  | HR5516 (Lo-16bits)
5518 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5519 |  |  |  | HR5518 (Lo-16bits)
5520 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5521 |  |  |  | HR5520 (Lo-16bits)
5522 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5523 |  |  |  | HR5522 (Lo-16bits)
5524 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5525 |  |  |  | HR5524 (Lo-16bits)
5526 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5527 |  |  |  | HR5526 (Lo-16bits)
5528 | DEF3:Comp. Pick-up setting U0set(I0Cosfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5529 |  |  |  | HR5528 (Lo-16bits)
5530 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5531 |  |  |  | HR5530 (Lo-16bits)
5532 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5533 |  |  |  | HR5532 (Lo-16bits)
5534 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5535 |  |  |  | HR5534 (Lo-16bits)
5536 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5537 |  |  |  | HR5536 (Lo-16bits)
5538 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5539 |  |  |  | HR5538 (Lo-16bits)
5540 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5541 |  |  |  | HR5540 (Lo-16bits)
5542 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5543 |  |  |  | HR5542 (Lo-16bits)
5544 | DEF3:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5545 |  |  |  | HR5544 (Lo-16bits)
5546 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5547 |  |  |  | HR5546 (Lo-16bits)
5548 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5549 |  |  |  | HR5548 (Lo-16bits)
5550 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5551 |  |  |  | HR5550 (Lo-16bits)
5552 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5553 |  |  |  | HR5552 (Lo-16bits)
5554 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5555 |  |  |  | HR5554 (Lo-16bits)
5556 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5557 |  |  |  | HR5556 (Lo-16bits)
5558 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5559 |  |  |  | HR5558 (Lo-16bits)
5560 | DEF3:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5561 |  |  |  | HR5560 (Lo-16bits)
5562 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5563 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5564 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5565 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5566 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5567 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5568 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5569 | DEF3:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5570 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5571 |  |  |  | HR5570 (Lo-16bits)
5572 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5573 |  |  |  | HR5572 (Lo-16bits)
5574 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5575 |  |  |  | HR5574 (Lo-16bits)
5576 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5577 |  |  |  | HR5576 (Lo-16bits)
5578 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5579 |  |  |  | HR5578 (Lo-16bits)
5580 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5581 |  |  |  | HR5580 (Lo-16bits)
5582 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5583 |  |  |  | HR5582 (Lo-16bits)
5584 | DEF3:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5585 |  |  |  | HR5584 (Lo-16bits)
5586 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5587 |  |  |  | HR5586 (Lo-16bits)
5588 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5589 |  |  |  | HR5588 (Lo-16bits)
5590 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5591 |  |  |  | HR5590 (Lo-16bits)
5592 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5593 |  |  |  | HR5592 (Lo-16bits)
5594 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5595 |  |  |  | HR5594 (Lo-16bits)
5596 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5597 |  |  |  | HR5596 (Lo-16bits)
5598 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5599 |  |  |  | HR5598 (Lo-16bits)
5600 | DEF3:Unearth. Pick-up setting I0set (I0Sinfi)>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5601 |  |  |  | HR5600 (Lo-16bits)
5602 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5603 |  |  |  | HR5602 (Lo-16bits)
5604 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5605 |  |  |  | HR5604 (Lo-16bits)
5606 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5607 |  |  |  | HR5606 (Lo-16bits)
5608 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5609 |  |  |  | HR5608 (Lo-16bits)
5610 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5611 |  |  |  | HR5610 (Lo-16bits)
5612 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5613 |  |  |  | HR5612 (Lo-16bits)
5614 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5615 |  |  |  | HR5614 (Lo-16bits)
5616 | DEF3:Unearth. Pick-up setting U0set(I0Sinfi)>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5617 |  |  |  | HR5616 (Lo-16bits)
5618 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5619 |  |  |  | HR5618 (Lo-16bits)
5620 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5621 |  |  |  | HR5620 (Lo-16bits)
5622 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5623 |  |  |  | HR5622 (Lo-16bits)
5624 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5625 |  |  |  | HR5624 (Lo-16bits)
5626 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5627 |  |  |  | HR5626 (Lo-16bits)
5628 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5629 |  |  |  | HR5628 (Lo-16bits)
5630 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5631 |  |  |  | HR5630 (Lo-16bits)
5632 | DEF3:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
5633 |  |  |  | HR5632 (Lo-16bits)
5634 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5635 |  |  |  | HR5634 (Lo-16bits)
5636 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5637 |  |  |  | HR5636 (Lo-16bits)
5638 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5639 |  |  |  | HR5638 (Lo-16bits)
5640 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5641 |  |  |  | HR5640 (Lo-16bits)
5642 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5643 |  |  |  | HR5642 (Lo-16bits)
5644 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5645 |  |  |  | HR5644 (Lo-16bits)
5646 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5647 |  |  |  | HR5646 (Lo-16bits)
5648 | DEF3:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
5649 |  |  |  | HR5648 (Lo-16bits)
5650 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5651 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5652 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5653 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5654 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5655 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5656 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5657 | DEF3:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
5658 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5659 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5660 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5661 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5662 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5663 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5664 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5665 | DEF3:Delay type | R(W) | 1 | 0=DT;1=IDMT
5666 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5667 |  |  |  | HR5666 (Lo-16bits)
5668 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5669 |  |  |  | HR5668 (Lo-16bits)
5670 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5671 |  |  |  | HR5670 (Lo-16bits)
5672 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5673 |  |  |  | HR5672 (Lo-16bits)
5674 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5675 |  |  |  | HR5674 (Lo-16bits)
5676 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5677 |  |  |  | HR5676 (Lo-16bits)
5678 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5679 |  |  |  | HR5678 (Lo-16bits)
5680 | DEF3:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5681 |  |  |  | HR5680 (Lo-16bits)
5682 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5683 |  |  |  | HR5682 (Lo-16bits)
5684 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5685 |  |  |  | HR5684 (Lo-16bits)
5686 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5687 |  |  |  | HR5686 (Lo-16bits)
5688 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5689 |  |  |  | HR5688 (Lo-16bits)
5690 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5691 |  |  |  | HR5690 (Lo-16bits)
5692 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5693 |  |  |  | HR5692 (Lo-16bits)
5694 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5695 |  |  |  | HR5694 (Lo-16bits)
5696 | DEF3:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5697 |  |  |  | HR5696 (Lo-16bits)
5698 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5699 |  |  |  | HR5698 (Lo-16bits)
5700 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5701 |  |  |  | HR5700 (Lo-16bits)
5702 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5703 |  |  |  | HR5702 (Lo-16bits)
5704 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5705 |  |  |  | HR5704 (Lo-16bits)
5706 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5707 |  |  |  | HR5706 (Lo-16bits)
5708 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5709 |  |  |  | HR5708 (Lo-16bits)
5710 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5711 |  |  |  | HR5710 (Lo-16bits)
5712 | DEF3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
5713 |  |  |  | HR5712 (Lo-16bits)
5714 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5715 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5716 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5717 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5718 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5719 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5720 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5721 | DEF3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
5722 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5723 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5724 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5725 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5726 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5727 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5728 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5729 | DEF3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
5730 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5731 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5732 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5733 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5734 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5735 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5736 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5737 | DEF3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
5738 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5739 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5740 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5741 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5742 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5743 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5744 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5745 | DEF3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
5746 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5747 |  |  |  | HR5746 (Lo-16bits)
5748 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5749 |  |  |  | HR5748 (Lo-16bits)
5750 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5751 |  |  |  | HR5750 (Lo-16bits)
5752 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5753 |  |  |  | HR5752 (Lo-16bits)
5754 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5755 |  |  |  | HR5754 (Lo-16bits)
5756 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5757 |  |  |  | HR5756 (Lo-16bits)
5758 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5759 |  |  |  | HR5758 (Lo-16bits)
5760 | DEF3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
5761 |  |  |  | HR5760 (Lo-16bits)
5762 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5763 |  |  |  | HR5762 (Lo-16bits)
5764 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5765 |  |  |  | HR5764 (Lo-16bits)
5766 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5767 |  |  |  | HR5766 (Lo-16bits)
5768 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5769 |  |  |  | HR5768 (Lo-16bits)
5770 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5771 |  |  |  | HR5770 (Lo-16bits)
5772 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5773 |  |  |  | HR5772 (Lo-16bits)
5774 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5775 |  |  |  | HR5774 (Lo-16bits)
5776 | DEF3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5777 |  |  |  | HR5776 (Lo-16bits)
5778 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5779 |  |  |  | HR5778 (Lo-16bits)
5780 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5781 |  |  |  | HR5780 (Lo-16bits)
5782 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5783 |  |  |  | HR5782 (Lo-16bits)
5784 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5785 |  |  |  | HR5784 (Lo-16bits)
5786 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5787 |  |  |  | HR5786 (Lo-16bits)
5788 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5789 |  |  |  | HR5788 (Lo-16bits)
5790 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5791 |  |  |  | HR5790 (Lo-16bits)
5792 | DEF3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5793 |  |  |  | HR5792 (Lo-16bits)
5794 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5795 |  |  |  | HR5794 (Lo-16bits)
5796 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5797 |  |  |  | HR5796 (Lo-16bits)
5798 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5799 |  |  |  | HR5798 (Lo-16bits)
5800 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5801 |  |  |  | HR5800 (Lo-16bits)
5802 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5803 |  |  |  | HR5802 (Lo-16bits)
5804 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5805 |  |  |  | HR5804 (Lo-16bits)
5806 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5807 |  |  |  | HR5806 (Lo-16bits)
5808 | DEF3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
5809 |  |  |  | HR5808 (Lo-16bits)
5810 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5811 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5812 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5813 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5814 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5815 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5816 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5817 | DEF3:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
5818 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5819 |  |  |  | HR5818 (Lo-16bits)
5820 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5821 |  |  |  | HR5820 (Lo-16bits)
5822 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5823 |  |  |  | HR5822 (Lo-16bits)
5824 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5825 |  |  |  | HR5824 (Lo-16bits)
5826 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5827 |  |  |  | HR5826 (Lo-16bits)
5828 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5829 |  |  |  | HR5828 (Lo-16bits)
5830 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5831 |  |  |  | HR5830 (Lo-16bits)
5832 | DEF3:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
5833 |  |  |  | HR5832 (Lo-16bits)
5834 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5835 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5836 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5837 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5838 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5839 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5840 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5841 | DEF3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
5842 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5843 |  |  |  | HR5842 (Lo-16bits)
5844 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5845 |  |  |  | HR5844 (Lo-16bits)
5846 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5847 |  |  |  | HR5846 (Lo-16bits)
5848 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5849 |  |  |  | HR5848 (Lo-16bits)
5850 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5851 |  |  |  | HR5850 (Lo-16bits)
5852 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5853 |  |  |  | HR5852 (Lo-16bits)
5854 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5855 |  |  |  | HR5854 (Lo-16bits)
5856 | DEF3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
5857 |  |  |  | HR5856 (Lo-16bits)
5858 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5859 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5860 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5861 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5862 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5863 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5864 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5865 | DEF3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
5866 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5867 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5868 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5869 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5870 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5871 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5872 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5873 | DEF3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
5874 | DEF4:I0dir>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Unearthed Start;5=Unearthed Trip;6=Compensated Start;7=Compensated Trip
5875 | DEF4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
5876 | DEF4:I0 Direction now | R | 1 | 0=Reverse;1=Forward;2=Undefined;
5877 | DEF4:I0dir>>>> Last fault end with | R | 1 | 0=No Faults;1=Start;2=Trip
5878 | DEF4:I0dir>>>> Last fault angle | R | 2 | FLOAT [-360...360] (Hi-16bits)
5879 |  |  |  | HR5878 (Lo-16bits)
5880 | DEF4:I0dir>>>> Last fault I0 current (pri) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5881 |  |  |  | HR5880 (Lo-16bits)
5882 | DEF4:I0dir>>>> Last fault U0(%) | R | 2 | FLOAT [0...1000000] (Hi-16bits)
5883 |  |  |  | HR5882 (Lo-16bits)
5884 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5885 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5886 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5887 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5888 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5889 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5890 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5891 | DEF4:Grounding type | R(W) | 1 | 0=Unearthed [32N Var];1=Petersen coil GND [32N Watt];2=Grounded [67N];3=I0Cos&I0Sin Broadrange with MCD [32N Var/Watt]
5892 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5893 |  |  |  | HR5892 (Lo-16bits)
5894 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5895 |  |  |  | HR5894 (Lo-16bits)
5896 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5897 |  |  |  | HR5896 (Lo-16bits)
5898 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5899 |  |  |  | HR5898 (Lo-16bits)
5900 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5901 |  |  |  | HR5900 (Lo-16bits)
5902 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5903 |  |  |  | HR5902 (Lo-16bits)
5904 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5905 |  |  |  | HR5904 (Lo-16bits)
5906 | DEF4:Pick-up setting I0set>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5907 |  |  |  | HR5906 (Lo-16bits)
5908 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5909 |  |  |  | HR5908 (Lo-16bits)
5910 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5911 |  |  |  | HR5910 (Lo-16bits)
5912 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5913 |  |  |  | HR5912 (Lo-16bits)
5914 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5915 |  |  |  | HR5914 (Lo-16bits)
5916 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5917 |  |  |  | HR5916 (Lo-16bits)
5918 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5919 |  |  |  | HR5918 (Lo-16bits)
5920 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5921 |  |  |  | HR5920 (Lo-16bits)
5922 | DEF4:Pick-up setting U0set>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5923 |  |  |  | HR5922 (Lo-16bits)
5924 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5925 |  |  |  | HR5924 (Lo-16bits)
5926 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5927 |  |  |  | HR5926 (Lo-16bits)
5928 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5929 |  |  |  | HR5928 (Lo-16bits)
5930 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5931 |  |  |  | HR5930 (Lo-16bits)
5932 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5933 |  |  |  | HR5932 (Lo-16bits)
5934 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5935 |  |  |  | HR5934 (Lo-16bits)
5936 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5937 |  |  |  | HR5936 (Lo-16bits)
5938 | DEF4:Comp. Pick-up setting I0set (I0Cosfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
5939 |  |  |  | HR5938 (Lo-16bits)
5940 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5941 |  |  |  | HR5940 (Lo-16bits)
5942 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5943 |  |  |  | HR5942 (Lo-16bits)
5944 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5945 |  |  |  | HR5944 (Lo-16bits)
5946 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5947 |  |  |  | HR5946 (Lo-16bits)
5948 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5949 |  |  |  | HR5948 (Lo-16bits)
5950 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5951 |  |  |  | HR5950 (Lo-16bits)
5952 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5953 |  |  |  | HR5952 (Lo-16bits)
5954 | DEF4:Comp. Pick-up setting U0set(I0Cosfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
5955 |  |  |  | HR5954 (Lo-16bits)
5956 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5957 |  |  |  | HR5956 (Lo-16bits)
5958 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5959 |  |  |  | HR5958 (Lo-16bits)
5960 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5961 |  |  |  | HR5960 (Lo-16bits)
5962 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5963 |  |  |  | HR5962 (Lo-16bits)
5964 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5965 |  |  |  | HR5964 (Lo-16bits)
5966 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5967 |  |  |  | HR5966 (Lo-16bits)
5968 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5969 |  |  |  | HR5968 (Lo-16bits)
5970 | DEF4:Unearthed / Compensated border angle | R(W) | 2 | FLOAT [-45...90] (Hi-16bits)
5971 |  |  |  | HR5970 (Lo-16bits)
5972 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5973 |  |  |  | HR5972 (Lo-16bits)
5974 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5975 |  |  |  | HR5974 (Lo-16bits)
5976 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5977 |  |  |  | HR5976 (Lo-16bits)
5978 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5979 |  |  |  | HR5978 (Lo-16bits)
5980 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5981 |  |  |  | HR5980 (Lo-16bits)
5982 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5983 |  |  |  | HR5982 (Lo-16bits)
5984 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5985 |  |  |  | HR5984 (Lo-16bits)
5986 | DEF4:Resistive (I0Cosfi) mode I0 angle blinder | R(W) | 2 | FLOAT [-90...0] (Hi-16bits)
5987 |  |  |  | HR5986 (Lo-16bits)
5988 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5989 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5990 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5991 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5992 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5993 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5994 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5995 | DEF4:Multi-criteria detection | R(W) | 1 | 0=Not Used;1=Is Used
5996 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5997 |  |  |  | HR5996 (Lo-16bits)
5998 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
5999 |  |  |  | HR5998 (Lo-16bits)
6000 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6001 |  |  |  | HR6000 (Lo-16bits)
6002 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6003 |  |  |  | HR6002 (Lo-16bits)
6004 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6005 |  |  |  | HR6004 (Lo-16bits)
6006 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6007 |  |  |  | HR6006 (Lo-16bits)
6008 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6009 |  |  |  | HR6008 (Lo-16bits)
6010 | DEF4:Angle MCD | R(W) | 2 | FLOAT [0...45] (Hi-16bits)
6011 |  |  |  | HR6010 (Lo-16bits)
6012 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6013 |  |  |  | HR6012 (Lo-16bits)
6014 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6015 |  |  |  | HR6014 (Lo-16bits)
6016 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6017 |  |  |  | HR6016 (Lo-16bits)
6018 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6019 |  |  |  | HR6018 (Lo-16bits)
6020 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6021 |  |  |  | HR6020 (Lo-16bits)
6022 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6023 |  |  |  | HR6022 (Lo-16bits)
6024 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6025 |  |  |  | HR6024 (Lo-16bits)
6026 | DEF4:Unearth. Pick-up setting I0set (I0Sinfi)>>>> | R(W) | 2 | FLOAT [0.005...40] (Hi-16bits)
6027 |  |  |  | HR6026 (Lo-16bits)
6028 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6029 |  |  |  | HR6028 (Lo-16bits)
6030 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6031 |  |  |  | HR6030 (Lo-16bits)
6032 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6033 |  |  |  | HR6032 (Lo-16bits)
6034 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6035 |  |  |  | HR6034 (Lo-16bits)
6036 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6037 |  |  |  | HR6036 (Lo-16bits)
6038 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6039 |  |  |  | HR6038 (Lo-16bits)
6040 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6041 |  |  |  | HR6040 (Lo-16bits)
6042 | DEF4:Unearth. Pick-up setting U0set(I0Sinfi)>>>> | R(W) | 2 | FLOAT [1...75] (Hi-16bits)
6043 |  |  |  | HR6042 (Lo-16bits)
6044 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6045 |  |  |  | HR6044 (Lo-16bits)
6046 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6047 |  |  |  | HR6046 (Lo-16bits)
6048 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6049 |  |  |  | HR6048 (Lo-16bits)
6050 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6051 |  |  |  | HR6050 (Lo-16bits)
6052 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6053 |  |  |  | HR6052 (Lo-16bits)
6054 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6055 |  |  |  | HR6054 (Lo-16bits)
6056 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6057 |  |  |  | HR6056 (Lo-16bits)
6058 | DEF4:Trip area size (+/-) | R(W) | 2 | FLOAT [5...135] (Hi-16bits)
6059 |  |  |  | HR6058 (Lo-16bits)
6060 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6061 |  |  |  | HR6060 (Lo-16bits)
6062 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6063 |  |  |  | HR6062 (Lo-16bits)
6064 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6065 |  |  |  | HR6064 (Lo-16bits)
6066 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6067 |  |  |  | HR6066 (Lo-16bits)
6068 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6069 |  |  |  | HR6068 (Lo-16bits)
6070 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6071 |  |  |  | HR6070 (Lo-16bits)
6072 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6073 |  |  |  | HR6072 (Lo-16bits)
6074 | DEF4:Trip area center | R(W) | 2 | FLOAT [-360...360] (Hi-16bits)
6075 |  |  |  | HR6074 (Lo-16bits)
6076 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6077 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6078 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6079 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6080 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6081 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6082 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6083 | DEF4:Delay type of broadrange characteristics | R(W) | 1 | 0=Common time;1=Separate times for I0Cosfi and I0Sinfi
6084 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6085 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6086 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6087 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6088 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6089 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6090 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6091 | DEF4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6092 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6093 |  |  |  | HR6092 (Lo-16bits)
6094 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6095 |  |  |  | HR6094 (Lo-16bits)
6096 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6097 |  |  |  | HR6096 (Lo-16bits)
6098 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6099 |  |  |  | HR6098 (Lo-16bits)
6100 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6101 |  |  |  | HR6100 (Lo-16bits)
6102 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6103 |  |  |  | HR6102 (Lo-16bits)
6104 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6105 |  |  |  | HR6104 (Lo-16bits)
6106 | DEF4:Definite operating time delay(Compensated) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6107 |  |  |  | HR6106 (Lo-16bits)
6108 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6109 |  |  |  | HR6108 (Lo-16bits)
6110 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6111 |  |  |  | HR6110 (Lo-16bits)
6112 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6113 |  |  |  | HR6112 (Lo-16bits)
6114 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6115 |  |  |  | HR6114 (Lo-16bits)
6116 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6117 |  |  |  | HR6116 (Lo-16bits)
6118 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6119 |  |  |  | HR6118 (Lo-16bits)
6120 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6121 |  |  |  | HR6120 (Lo-16bits)
6122 | DEF4:Definite operating time delay(Unearthed) | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6123 |  |  |  | HR6122 (Lo-16bits)
6124 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6125 |  |  |  | HR6124 (Lo-16bits)
6126 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6127 |  |  |  | HR6126 (Lo-16bits)
6128 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6129 |  |  |  | HR6128 (Lo-16bits)
6130 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6131 |  |  |  | HR6130 (Lo-16bits)
6132 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6133 |  |  |  | HR6132 (Lo-16bits)
6134 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6135 |  |  |  | HR6134 (Lo-16bits)
6136 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6137 |  |  |  | HR6136 (Lo-16bits)
6138 | DEF4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6139 |  |  |  | HR6138 (Lo-16bits)
6140 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6141 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6142 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6143 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6144 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6145 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6146 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6147 | DEF4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6148 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6149 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6150 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6151 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6152 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6153 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6154 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6155 | DEF4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6156 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6157 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6158 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6159 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6160 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6161 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6162 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6163 | DEF4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6164 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6165 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6166 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6167 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6168 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6169 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6170 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6171 | DEF4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type
6172 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6173 |  |  |  | HR6172 (Lo-16bits)
6174 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6175 |  |  |  | HR6174 (Lo-16bits)
6176 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6177 |  |  |  | HR6176 (Lo-16bits)
6178 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6179 |  |  |  | HR6178 (Lo-16bits)
6180 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6181 |  |  |  | HR6180 (Lo-16bits)
6182 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6183 |  |  |  | HR6182 (Lo-16bits)
6184 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6185 |  |  |  | HR6184 (Lo-16bits)
6186 | DEF4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6187 |  |  |  | HR6186 (Lo-16bits)
6188 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6189 |  |  |  | HR6188 (Lo-16bits)
6190 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6191 |  |  |  | HR6190 (Lo-16bits)
6192 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6193 |  |  |  | HR6192 (Lo-16bits)
6194 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6195 |  |  |  | HR6194 (Lo-16bits)
6196 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6197 |  |  |  | HR6196 (Lo-16bits)
6198 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6199 |  |  |  | HR6198 (Lo-16bits)
6200 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6201 |  |  |  | HR6200 (Lo-16bits)
6202 | DEF4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6203 |  |  |  | HR6202 (Lo-16bits)
6204 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6205 |  |  |  | HR6204 (Lo-16bits)
6206 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6207 |  |  |  | HR6206 (Lo-16bits)
6208 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6209 |  |  |  | HR6208 (Lo-16bits)
6210 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6211 |  |  |  | HR6210 (Lo-16bits)
6212 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6213 |  |  |  | HR6212 (Lo-16bits)
6214 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6215 |  |  |  | HR6214 (Lo-16bits)
6216 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6217 |  |  |  | HR6216 (Lo-16bits)
6218 | DEF4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6219 |  |  |  | HR6218 (Lo-16bits)
6220 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6221 |  |  |  | HR6220 (Lo-16bits)
6222 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6223 |  |  |  | HR6222 (Lo-16bits)
6224 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6225 |  |  |  | HR6224 (Lo-16bits)
6226 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6227 |  |  |  | HR6226 (Lo-16bits)
6228 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6229 |  |  |  | HR6228 (Lo-16bits)
6230 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6231 |  |  |  | HR6230 (Lo-16bits)
6232 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6233 |  |  |  | HR6232 (Lo-16bits)
6234 | DEF4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6235 |  |  |  | HR6234 (Lo-16bits)
6236 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6237 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6238 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6239 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6240 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6241 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6242 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6243 | DEF4:Inrush Harmonic Blocking (Internal Only Trip) | R(W) | 1 | 0=No;1=Yes
6244 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6245 |  |  |  | HR6244 (Lo-16bits)
6246 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6247 |  |  |  | HR6246 (Lo-16bits)
6248 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6249 |  |  |  | HR6248 (Lo-16bits)
6250 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6251 |  |  |  | HR6250 (Lo-16bits)
6252 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6253 |  |  |  | HR6252 (Lo-16bits)
6254 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6255 |  |  |  | HR6254 (Lo-16bits)
6256 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6257 |  |  |  | HR6256 (Lo-16bits)
6258 | DEF4:2.nd Harmonic Block Limit (Iharm / Ifund) | R(W) | 2 | FLOAT [0.1...50] (Hi-16bits)
6259 |  |  |  | HR6258 (Lo-16bits)
6260 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6261 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6262 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6263 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6264 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6265 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6266 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6267 | DEF4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6268 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6269 |  |  |  | HR6268 (Lo-16bits)
6270 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6271 |  |  |  | HR6270 (Lo-16bits)
6272 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6273 |  |  |  | HR6272 (Lo-16bits)
6274 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6275 |  |  |  | HR6274 (Lo-16bits)
6276 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6277 |  |  |  | HR6276 (Lo-16bits)
6278 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6279 |  |  |  | HR6278 (Lo-16bits)
6280 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6281 |  |  |  | HR6280 (Lo-16bits)
6282 | DEF4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6283 |  |  |  | HR6282 (Lo-16bits)
6284 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6285 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6286 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6287 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6288 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6289 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6290 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6291 | DEF4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6292 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6293 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6294 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6295 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6296 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6297 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6298 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6299 | DEF4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6300 | IEF1:I0Int> condition | R | 1 | 0=Normal;1=StartFWD;2=StartREV;3=Trip;4=Blocked;
6301 | IEF1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
6302 | CUB1:I2> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6303 | CUB1:I2> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6304 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6305 |  |  |  | HR6304 (Lo-16bits)
6306 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6307 |  |  |  | HR6306 (Lo-16bits)
6308 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6309 |  |  |  | HR6308 (Lo-16bits)
6310 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6311 |  |  |  | HR6310 (Lo-16bits)
6312 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6313 |  |  |  | HR6312 (Lo-16bits)
6314 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6315 |  |  |  | HR6314 (Lo-16bits)
6316 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6317 |  |  |  | HR6316 (Lo-16bits)
6318 | CUB1:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6319 |  |  |  | HR6318 (Lo-16bits)
6320 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6321 |  |  |  | HR6320 (Lo-16bits)
6322 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6323 |  |  |  | HR6322 (Lo-16bits)
6324 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6325 |  |  |  | HR6324 (Lo-16bits)
6326 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6327 |  |  |  | HR6326 (Lo-16bits)
6328 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6329 |  |  |  | HR6328 (Lo-16bits)
6330 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6331 |  |  |  | HR6330 (Lo-16bits)
6332 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6333 |  |  |  | HR6332 (Lo-16bits)
6334 | CUB1:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6335 |  |  |  | HR6334 (Lo-16bits)
6336 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6337 |  |  |  | HR6336 (Lo-16bits)
6338 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6339 |  |  |  | HR6338 (Lo-16bits)
6340 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6341 |  |  |  | HR6340 (Lo-16bits)
6342 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6343 |  |  |  | HR6342 (Lo-16bits)
6344 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6345 |  |  |  | HR6344 (Lo-16bits)
6346 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6347 |  |  |  | HR6346 (Lo-16bits)
6348 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6349 |  |  |  | HR6348 (Lo-16bits)
6350 | CUB1:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6351 |  |  |  | HR6350 (Lo-16bits)
6352 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6353 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6354 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6355 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6356 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6357 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6358 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6359 | CUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
6360 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6361 |  |  |  | HR6360 (Lo-16bits)
6362 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6363 |  |  |  | HR6362 (Lo-16bits)
6364 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6365 |  |  |  | HR6364 (Lo-16bits)
6366 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6367 |  |  |  | HR6366 (Lo-16bits)
6368 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6369 |  |  |  | HR6368 (Lo-16bits)
6370 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6371 |  |  |  | HR6370 (Lo-16bits)
6372 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6373 |  |  |  | HR6372 (Lo-16bits)
6374 | CUB1:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6375 |  |  |  | HR6374 (Lo-16bits)
6376 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6377 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6378 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6379 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6380 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6381 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6382 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6383 | CUB1:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6384 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6385 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6386 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6387 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6388 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6389 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6390 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6391 | CUB1:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6392 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6393 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6394 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6395 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6396 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6397 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6398 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6399 | CUB1:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6400 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6401 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6402 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6403 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6404 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6405 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6406 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6407 | CUB1:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6408 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6409 |  |  |  | HR6408 (Lo-16bits)
6410 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6411 |  |  |  | HR6410 (Lo-16bits)
6412 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6413 |  |  |  | HR6412 (Lo-16bits)
6414 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6415 |  |  |  | HR6414 (Lo-16bits)
6416 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6417 |  |  |  | HR6416 (Lo-16bits)
6418 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6419 |  |  |  | HR6418 (Lo-16bits)
6420 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6421 |  |  |  | HR6420 (Lo-16bits)
6422 | CUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6423 |  |  |  | HR6422 (Lo-16bits)
6424 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6425 |  |  |  | HR6424 (Lo-16bits)
6426 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6427 |  |  |  | HR6426 (Lo-16bits)
6428 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6429 |  |  |  | HR6428 (Lo-16bits)
6430 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6431 |  |  |  | HR6430 (Lo-16bits)
6432 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6433 |  |  |  | HR6432 (Lo-16bits)
6434 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6435 |  |  |  | HR6434 (Lo-16bits)
6436 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6437 |  |  |  | HR6436 (Lo-16bits)
6438 | CUB1:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6439 |  |  |  | HR6438 (Lo-16bits)
6440 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6441 |  |  |  | HR6440 (Lo-16bits)
6442 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6443 |  |  |  | HR6442 (Lo-16bits)
6444 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6445 |  |  |  | HR6444 (Lo-16bits)
6446 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6447 |  |  |  | HR6446 (Lo-16bits)
6448 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6449 |  |  |  | HR6448 (Lo-16bits)
6450 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6451 |  |  |  | HR6450 (Lo-16bits)
6452 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6453 |  |  |  | HR6452 (Lo-16bits)
6454 | CUB1:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6455 |  |  |  | HR6454 (Lo-16bits)
6456 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6457 |  |  |  | HR6456 (Lo-16bits)
6458 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6459 |  |  |  | HR6458 (Lo-16bits)
6460 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6461 |  |  |  | HR6460 (Lo-16bits)
6462 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6463 |  |  |  | HR6462 (Lo-16bits)
6464 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6465 |  |  |  | HR6464 (Lo-16bits)
6466 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6467 |  |  |  | HR6466 (Lo-16bits)
6468 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6469 |  |  |  | HR6468 (Lo-16bits)
6470 | CUB1:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6471 |  |  |  | HR6470 (Lo-16bits)
6472 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6473 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6474 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6475 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6476 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6477 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6478 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6479 | CUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6480 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6481 |  |  |  | HR6480 (Lo-16bits)
6482 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6483 |  |  |  | HR6482 (Lo-16bits)
6484 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6485 |  |  |  | HR6484 (Lo-16bits)
6486 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6487 |  |  |  | HR6486 (Lo-16bits)
6488 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6489 |  |  |  | HR6488 (Lo-16bits)
6490 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6491 |  |  |  | HR6490 (Lo-16bits)
6492 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6493 |  |  |  | HR6492 (Lo-16bits)
6494 | CUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6495 |  |  |  | HR6494 (Lo-16bits)
6496 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6497 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6498 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6499 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6500 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6501 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6502 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6503 | CUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6504 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6505 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6506 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6507 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6508 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6509 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6510 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6511 | CUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6512 | CUB2:I2>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6513 | CUB2:I2>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6514 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6515 |  |  |  | HR6514 (Lo-16bits)
6516 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6517 |  |  |  | HR6516 (Lo-16bits)
6518 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6519 |  |  |  | HR6518 (Lo-16bits)
6520 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6521 |  |  |  | HR6520 (Lo-16bits)
6522 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6523 |  |  |  | HR6522 (Lo-16bits)
6524 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6525 |  |  |  | HR6524 (Lo-16bits)
6526 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6527 |  |  |  | HR6526 (Lo-16bits)
6528 | CUB2:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6529 |  |  |  | HR6528 (Lo-16bits)
6530 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6531 |  |  |  | HR6530 (Lo-16bits)
6532 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6533 |  |  |  | HR6532 (Lo-16bits)
6534 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6535 |  |  |  | HR6534 (Lo-16bits)
6536 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6537 |  |  |  | HR6536 (Lo-16bits)
6538 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6539 |  |  |  | HR6538 (Lo-16bits)
6540 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6541 |  |  |  | HR6540 (Lo-16bits)
6542 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6543 |  |  |  | HR6542 (Lo-16bits)
6544 | CUB2:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6545 |  |  |  | HR6544 (Lo-16bits)
6546 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6547 |  |  |  | HR6546 (Lo-16bits)
6548 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6549 |  |  |  | HR6548 (Lo-16bits)
6550 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6551 |  |  |  | HR6550 (Lo-16bits)
6552 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6553 |  |  |  | HR6552 (Lo-16bits)
6554 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6555 |  |  |  | HR6554 (Lo-16bits)
6556 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6557 |  |  |  | HR6556 (Lo-16bits)
6558 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6559 |  |  |  | HR6558 (Lo-16bits)
6560 | CUB2:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6561 |  |  |  | HR6560 (Lo-16bits)
6562 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6563 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6564 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6565 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6566 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6567 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6568 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6569 | CUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
6570 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6571 |  |  |  | HR6570 (Lo-16bits)
6572 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6573 |  |  |  | HR6572 (Lo-16bits)
6574 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6575 |  |  |  | HR6574 (Lo-16bits)
6576 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6577 |  |  |  | HR6576 (Lo-16bits)
6578 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6579 |  |  |  | HR6578 (Lo-16bits)
6580 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6581 |  |  |  | HR6580 (Lo-16bits)
6582 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6583 |  |  |  | HR6582 (Lo-16bits)
6584 | CUB2:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6585 |  |  |  | HR6584 (Lo-16bits)
6586 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6587 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6588 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6589 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6590 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6591 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6592 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6593 | CUB2:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6594 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6595 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6596 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6597 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6598 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6599 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6600 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6601 | CUB2:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6602 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6603 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6604 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6605 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6606 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6607 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6608 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6609 | CUB2:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6610 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6611 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6612 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6613 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6614 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6615 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6616 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6617 | CUB2:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6618 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6619 |  |  |  | HR6618 (Lo-16bits)
6620 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6621 |  |  |  | HR6620 (Lo-16bits)
6622 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6623 |  |  |  | HR6622 (Lo-16bits)
6624 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6625 |  |  |  | HR6624 (Lo-16bits)
6626 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6627 |  |  |  | HR6626 (Lo-16bits)
6628 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6629 |  |  |  | HR6628 (Lo-16bits)
6630 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6631 |  |  |  | HR6630 (Lo-16bits)
6632 | CUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6633 |  |  |  | HR6632 (Lo-16bits)
6634 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6635 |  |  |  | HR6634 (Lo-16bits)
6636 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6637 |  |  |  | HR6636 (Lo-16bits)
6638 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6639 |  |  |  | HR6638 (Lo-16bits)
6640 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6641 |  |  |  | HR6640 (Lo-16bits)
6642 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6643 |  |  |  | HR6642 (Lo-16bits)
6644 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6645 |  |  |  | HR6644 (Lo-16bits)
6646 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6647 |  |  |  | HR6646 (Lo-16bits)
6648 | CUB2:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6649 |  |  |  | HR6648 (Lo-16bits)
6650 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6651 |  |  |  | HR6650 (Lo-16bits)
6652 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6653 |  |  |  | HR6652 (Lo-16bits)
6654 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6655 |  |  |  | HR6654 (Lo-16bits)
6656 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6657 |  |  |  | HR6656 (Lo-16bits)
6658 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6659 |  |  |  | HR6658 (Lo-16bits)
6660 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6661 |  |  |  | HR6660 (Lo-16bits)
6662 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6663 |  |  |  | HR6662 (Lo-16bits)
6664 | CUB2:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6665 |  |  |  | HR6664 (Lo-16bits)
6666 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6667 |  |  |  | HR6666 (Lo-16bits)
6668 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6669 |  |  |  | HR6668 (Lo-16bits)
6670 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6671 |  |  |  | HR6670 (Lo-16bits)
6672 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6673 |  |  |  | HR6672 (Lo-16bits)
6674 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6675 |  |  |  | HR6674 (Lo-16bits)
6676 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6677 |  |  |  | HR6676 (Lo-16bits)
6678 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6679 |  |  |  | HR6678 (Lo-16bits)
6680 | CUB2:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6681 |  |  |  | HR6680 (Lo-16bits)
6682 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6683 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6684 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6685 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6686 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6687 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6688 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6689 | CUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6690 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6691 |  |  |  | HR6690 (Lo-16bits)
6692 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6693 |  |  |  | HR6692 (Lo-16bits)
6694 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6695 |  |  |  | HR6694 (Lo-16bits)
6696 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6697 |  |  |  | HR6696 (Lo-16bits)
6698 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6699 |  |  |  | HR6698 (Lo-16bits)
6700 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6701 |  |  |  | HR6700 (Lo-16bits)
6702 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6703 |  |  |  | HR6702 (Lo-16bits)
6704 | CUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6705 |  |  |  | HR6704 (Lo-16bits)
6706 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6707 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6708 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6709 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6710 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6711 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6712 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6713 | CUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6714 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6715 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6716 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6717 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6718 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6719 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6720 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6721 | CUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6722 | CUB3:I2>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6723 | CUB3:I2>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6724 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6725 |  |  |  | HR6724 (Lo-16bits)
6726 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6727 |  |  |  | HR6726 (Lo-16bits)
6728 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6729 |  |  |  | HR6728 (Lo-16bits)
6730 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6731 |  |  |  | HR6730 (Lo-16bits)
6732 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6733 |  |  |  | HR6732 (Lo-16bits)
6734 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6735 |  |  |  | HR6734 (Lo-16bits)
6736 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6737 |  |  |  | HR6736 (Lo-16bits)
6738 | CUB3:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6739 |  |  |  | HR6738 (Lo-16bits)
6740 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6741 |  |  |  | HR6740 (Lo-16bits)
6742 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6743 |  |  |  | HR6742 (Lo-16bits)
6744 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6745 |  |  |  | HR6744 (Lo-16bits)
6746 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6747 |  |  |  | HR6746 (Lo-16bits)
6748 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6749 |  |  |  | HR6748 (Lo-16bits)
6750 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6751 |  |  |  | HR6750 (Lo-16bits)
6752 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6753 |  |  |  | HR6752 (Lo-16bits)
6754 | CUB3:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6755 |  |  |  | HR6754 (Lo-16bits)
6756 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6757 |  |  |  | HR6756 (Lo-16bits)
6758 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6759 |  |  |  | HR6758 (Lo-16bits)
6760 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6761 |  |  |  | HR6760 (Lo-16bits)
6762 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6763 |  |  |  | HR6762 (Lo-16bits)
6764 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6765 |  |  |  | HR6764 (Lo-16bits)
6766 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6767 |  |  |  | HR6766 (Lo-16bits)
6768 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6769 |  |  |  | HR6768 (Lo-16bits)
6770 | CUB3:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6771 |  |  |  | HR6770 (Lo-16bits)
6772 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6773 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6774 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6775 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6776 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6777 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6778 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6779 | CUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
6780 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6781 |  |  |  | HR6780 (Lo-16bits)
6782 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6783 |  |  |  | HR6782 (Lo-16bits)
6784 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6785 |  |  |  | HR6784 (Lo-16bits)
6786 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6787 |  |  |  | HR6786 (Lo-16bits)
6788 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6789 |  |  |  | HR6788 (Lo-16bits)
6790 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6791 |  |  |  | HR6790 (Lo-16bits)
6792 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6793 |  |  |  | HR6792 (Lo-16bits)
6794 | CUB3:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6795 |  |  |  | HR6794 (Lo-16bits)
6796 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6797 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6798 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6799 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6800 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6801 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6802 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6803 | CUB3:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
6804 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6805 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6806 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6807 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6808 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6809 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6810 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6811 | CUB3:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
6812 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6813 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6814 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6815 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6816 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6817 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6818 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6819 | CUB3:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
6820 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6821 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6822 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6823 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6824 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6825 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6826 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6827 | CUB3:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
6828 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6829 |  |  |  | HR6828 (Lo-16bits)
6830 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6831 |  |  |  | HR6830 (Lo-16bits)
6832 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6833 |  |  |  | HR6832 (Lo-16bits)
6834 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6835 |  |  |  | HR6834 (Lo-16bits)
6836 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6837 |  |  |  | HR6836 (Lo-16bits)
6838 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6839 |  |  |  | HR6838 (Lo-16bits)
6840 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6841 |  |  |  | HR6840 (Lo-16bits)
6842 | CUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
6843 |  |  |  | HR6842 (Lo-16bits)
6844 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6845 |  |  |  | HR6844 (Lo-16bits)
6846 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6847 |  |  |  | HR6846 (Lo-16bits)
6848 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6849 |  |  |  | HR6848 (Lo-16bits)
6850 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6851 |  |  |  | HR6850 (Lo-16bits)
6852 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6853 |  |  |  | HR6852 (Lo-16bits)
6854 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6855 |  |  |  | HR6854 (Lo-16bits)
6856 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6857 |  |  |  | HR6856 (Lo-16bits)
6858 | CUB3:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6859 |  |  |  | HR6858 (Lo-16bits)
6860 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6861 |  |  |  | HR6860 (Lo-16bits)
6862 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6863 |  |  |  | HR6862 (Lo-16bits)
6864 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6865 |  |  |  | HR6864 (Lo-16bits)
6866 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6867 |  |  |  | HR6866 (Lo-16bits)
6868 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6869 |  |  |  | HR6868 (Lo-16bits)
6870 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6871 |  |  |  | HR6870 (Lo-16bits)
6872 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6873 |  |  |  | HR6872 (Lo-16bits)
6874 | CUB3:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6875 |  |  |  | HR6874 (Lo-16bits)
6876 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6877 |  |  |  | HR6876 (Lo-16bits)
6878 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6879 |  |  |  | HR6878 (Lo-16bits)
6880 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6881 |  |  |  | HR6880 (Lo-16bits)
6882 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6883 |  |  |  | HR6882 (Lo-16bits)
6884 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6885 |  |  |  | HR6884 (Lo-16bits)
6886 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6887 |  |  |  | HR6886 (Lo-16bits)
6888 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6889 |  |  |  | HR6888 (Lo-16bits)
6890 | CUB3:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
6891 |  |  |  | HR6890 (Lo-16bits)
6892 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6893 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6894 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6895 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6896 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6897 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6898 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6899 | CUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
6900 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6901 |  |  |  | HR6900 (Lo-16bits)
6902 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6903 |  |  |  | HR6902 (Lo-16bits)
6904 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6905 |  |  |  | HR6904 (Lo-16bits)
6906 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6907 |  |  |  | HR6906 (Lo-16bits)
6908 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6909 |  |  |  | HR6908 (Lo-16bits)
6910 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6911 |  |  |  | HR6910 (Lo-16bits)
6912 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6913 |  |  |  | HR6912 (Lo-16bits)
6914 | CUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
6915 |  |  |  | HR6914 (Lo-16bits)
6916 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6917 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6918 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6919 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6920 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6921 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6922 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6923 | CUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
6924 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6925 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6926 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6927 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6928 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6929 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6930 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6931 | CUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
6932 | CUB4:I2>>>> [46] mode | R(W) | 1 | 0=Disabled;1=Activated
6933 | CUB4:I2>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
6934 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6935 |  |  |  | HR6934 (Lo-16bits)
6936 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6937 |  |  |  | HR6936 (Lo-16bits)
6938 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6939 |  |  |  | HR6938 (Lo-16bits)
6940 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6941 |  |  |  | HR6940 (Lo-16bits)
6942 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6943 |  |  |  | HR6942 (Lo-16bits)
6944 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6945 |  |  |  | HR6944 (Lo-16bits)
6946 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6947 |  |  |  | HR6946 (Lo-16bits)
6948 | CUB4:Pick-up setting I2set pu | R(W) | 2 | FLOAT [0.01...40] (Hi-16bits)
6949 |  |  |  | HR6948 (Lo-16bits)
6950 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6951 |  |  |  | HR6950 (Lo-16bits)
6952 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6953 |  |  |  | HR6952 (Lo-16bits)
6954 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6955 |  |  |  | HR6954 (Lo-16bits)
6956 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6957 |  |  |  | HR6956 (Lo-16bits)
6958 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6959 |  |  |  | HR6958 (Lo-16bits)
6960 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6961 |  |  |  | HR6960 (Lo-16bits)
6962 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6963 |  |  |  | HR6962 (Lo-16bits)
6964 | CUB4:Pick-up setting I2/I1 | R(W) | 2 | FLOAT [1...200] (Hi-16bits)
6965 |  |  |  | HR6964 (Lo-16bits)
6966 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6967 |  |  |  | HR6966 (Lo-16bits)
6968 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6969 |  |  |  | HR6968 (Lo-16bits)
6970 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6971 |  |  |  | HR6970 (Lo-16bits)
6972 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6973 |  |  |  | HR6972 (Lo-16bits)
6974 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6975 |  |  |  | HR6974 (Lo-16bits)
6976 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6977 |  |  |  | HR6976 (Lo-16bits)
6978 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6979 |  |  |  | HR6978 (Lo-16bits)
6980 | CUB4:Minimum phase current | R(W) | 2 | FLOAT [0.01...2] (Hi-16bits)
6981 |  |  |  | HR6980 (Lo-16bits)
6982 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6983 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6984 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6985 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6986 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6987 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6988 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6989 | CUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
6990 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6991 |  |  |  | HR6990 (Lo-16bits)
6992 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6993 |  |  |  | HR6992 (Lo-16bits)
6994 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6995 |  |  |  | HR6994 (Lo-16bits)
6996 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6997 |  |  |  | HR6996 (Lo-16bits)
6998 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
6999 |  |  |  | HR6998 (Lo-16bits)
7000 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7001 |  |  |  | HR7000 (Lo-16bits)
7002 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7003 |  |  |  | HR7002 (Lo-16bits)
7004 | CUB4:Definite (minimum) operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7005 |  |  |  | HR7004 (Lo-16bits)
7006 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7007 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7008 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7009 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7010 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7011 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7012 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7013 | CUB4:Delay curve series | R(W) | 1 | 0=IEC;1=IEEE;2=Non standard
7014 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7015 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7016 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7017 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7018 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7019 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7020 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7021 | CUB4:Delay characteristics IEC | R(W) | 1 | 0=NI;1=EI;2=VI;3=LTI;4=Param
7022 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7023 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7024 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7025 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7026 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7027 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7028 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7029 | CUB4:Delay char. ANSI/IEEE | R(W) | 1 | 0=ANSI NI;1=ANSI VI;2=ANSI EI;3=ANSI LTI;4=IEEE MI;5=IEEE VI;6=IEEE EI;7=Param
7030 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7031 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7032 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7033 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7034 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7035 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7036 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7037 | CUB4:Non standard Delay char. | R(W) | 1 | 0=RI-type;1=RD-type;2=Curve2
7038 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7039 |  |  |  | HR7038 (Lo-16bits)
7040 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7041 |  |  |  | HR7040 (Lo-16bits)
7042 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7043 |  |  |  | HR7042 (Lo-16bits)
7044 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7045 |  |  |  | HR7044 (Lo-16bits)
7046 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7047 |  |  |  | HR7046 (Lo-16bits)
7048 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7049 |  |  |  | HR7048 (Lo-16bits)
7050 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7051 |  |  |  | HR7050 (Lo-16bits)
7052 | CUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7053 |  |  |  | HR7052 (Lo-16bits)
7054 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7055 |  |  |  | HR7054 (Lo-16bits)
7056 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7057 |  |  |  | HR7056 (Lo-16bits)
7058 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7059 |  |  |  | HR7058 (Lo-16bits)
7060 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7061 |  |  |  | HR7060 (Lo-16bits)
7062 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7063 |  |  |  | HR7062 (Lo-16bits)
7064 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7065 |  |  |  | HR7064 (Lo-16bits)
7066 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7067 |  |  |  | HR7066 (Lo-16bits)
7068 | CUB4:IDMT Const. A | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7069 |  |  |  | HR7068 (Lo-16bits)
7070 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7071 |  |  |  | HR7070 (Lo-16bits)
7072 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7073 |  |  |  | HR7072 (Lo-16bits)
7074 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7075 |  |  |  | HR7074 (Lo-16bits)
7076 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7077 |  |  |  | HR7076 (Lo-16bits)
7078 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7079 |  |  |  | HR7078 (Lo-16bits)
7080 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7081 |  |  |  | HR7080 (Lo-16bits)
7082 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7083 |  |  |  | HR7082 (Lo-16bits)
7084 | CUB4:IDMT Const. B | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7085 |  |  |  | HR7084 (Lo-16bits)
7086 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7087 |  |  |  | HR7086 (Lo-16bits)
7088 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7089 |  |  |  | HR7088 (Lo-16bits)
7090 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7091 |  |  |  | HR7090 (Lo-16bits)
7092 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7093 |  |  |  | HR7092 (Lo-16bits)
7094 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7095 |  |  |  | HR7094 (Lo-16bits)
7096 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7097 |  |  |  | HR7096 (Lo-16bits)
7098 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7099 |  |  |  | HR7098 (Lo-16bits)
7100 | CUB4:IDMT Const. C | R(W) | 2 | FLOAT [0...250] (Hi-16bits)
7101 |  |  |  | HR7100 (Lo-16bits)
7102 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7103 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7104 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7105 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7106 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7107 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7108 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7109 | CUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7110 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7111 |  |  |  | HR7110 (Lo-16bits)
7112 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7113 |  |  |  | HR7112 (Lo-16bits)
7114 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7115 |  |  |  | HR7114 (Lo-16bits)
7116 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7117 |  |  |  | HR7116 (Lo-16bits)
7118 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7119 |  |  |  | HR7118 (Lo-16bits)
7120 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7121 |  |  |  | HR7120 (Lo-16bits)
7122 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7123 |  |  |  | HR7122 (Lo-16bits)
7124 | CUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7125 |  |  |  | HR7124 (Lo-16bits)
7126 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7127 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7128 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7129 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7130 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7131 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7132 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7133 | CUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7134 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7135 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7136 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7137 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7138 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7139 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7140 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7141 | CUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7142 | HOC1:Ih> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7143 | HOC1:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7144 |  |  |  | HR7143 (Lo-16bits)
7145 | HOC1:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7146 |  |  |  | HR7145 (Lo-16bits)
7147 | HOC1:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7148 |  |  |  | HR7147 (Lo-16bits)
7149 | HOC1:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7150 |  |  |  | HR7149 (Lo-16bits)
7151 | HOC1:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7152 |  |  |  | HR7151 (Lo-16bits)
7153 | HOC1:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7154 |  |  |  | HR7153 (Lo-16bits)
7155 | HOC1:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7156 |  |  |  | HR7155 (Lo-16bits)
7157 | HOC1:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7158 |  |  |  | HR7157 (Lo-16bits)
7159 | HOC1:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7160 |  |  |  | HR7159 (Lo-16bits)
7161 | HOC1:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7162 |  |  |  | HR7161 (Lo-16bits)
7163 | HOC2:Ih>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7164 | HOC2:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7165 |  |  |  | HR7164 (Lo-16bits)
7166 | HOC2:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7167 |  |  |  | HR7166 (Lo-16bits)
7168 | HOC2:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7169 |  |  |  | HR7168 (Lo-16bits)
7170 | HOC2:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7171 |  |  |  | HR7170 (Lo-16bits)
7172 | HOC2:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7173 |  |  |  | HR7172 (Lo-16bits)
7174 | HOC2:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7175 |  |  |  | HR7174 (Lo-16bits)
7176 | HOC2:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7177 |  |  |  | HR7176 (Lo-16bits)
7178 | HOC2:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7179 |  |  |  | HR7178 (Lo-16bits)
7180 | HOC2:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7181 |  |  |  | HR7180 (Lo-16bits)
7182 | HOC2:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7183 |  |  |  | HR7182 (Lo-16bits)
7184 | HOC3:Ih>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7185 | HOC3:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7186 |  |  |  | HR7185 (Lo-16bits)
7187 | HOC3:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7188 |  |  |  | HR7187 (Lo-16bits)
7189 | HOC3:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7190 |  |  |  | HR7189 (Lo-16bits)
7191 | HOC3:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7192 |  |  |  | HR7191 (Lo-16bits)
7193 | HOC3:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7194 |  |  |  | HR7193 (Lo-16bits)
7195 | HOC3:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7196 |  |  |  | HR7195 (Lo-16bits)
7197 | HOC3:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7198 |  |  |  | HR7197 (Lo-16bits)
7199 | HOC3:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7200 |  |  |  | HR7199 (Lo-16bits)
7201 | HOC3:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7202 |  |  |  | HR7201 (Lo-16bits)
7203 | HOC3:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7204 |  |  |  | HR7203 (Lo-16bits)
7205 | HOC4:Ih>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7206 | HOC4:L1 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7207 |  |  |  | HR7206 (Lo-16bits)
7208 | HOC4:L1 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7209 |  |  |  | HR7208 (Lo-16bits)
7210 | HOC4:L2 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7211 |  |  |  | HR7210 (Lo-16bits)
7212 | HOC4:L2 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7213 |  |  |  | HR7212 (Lo-16bits)
7214 | HOC4:L3 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7215 |  |  |  | HR7214 (Lo-16bits)
7216 | HOC4:L3 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7217 |  |  |  | HR7216 (Lo-16bits)
7218 | HOC4:I01 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7219 |  |  |  | HR7218 (Lo-16bits)
7220 | HOC4:I01 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7221 |  |  |  | HR7220 (Lo-16bits)
7222 | HOC4:I02 Harm p.u. | R | 2 | FLOAT [0...100000] (Hi-16bits)
7223 |  |  |  | HR7222 (Lo-16bits)
7224 | HOC4:I02 Harm per | R | 2 | FLOAT [0...100000] (Hi-16bits)
7225 |  |  |  | HR7224 (Lo-16bits)
7226 | CLP1:CLP condition | R | 1 | 0=Normal;1=Curr low;2=Overcurrent On;3=CLPU On;4=CLPU blocked
7227 | CBF1:CBFP condition | R | 1 | 0=Normal;1=Start;2=ReTrip;3=CBFP On;4=Blocked
7228 | MST1:Motor is now | R | 1 | 0=Stopped;1=Starting;2=Running;3=Stalled
7229 | TRF1:Transformer is now | R | 1 | 0=No/LightLoad;1=Energizing;2=Normal load;3=Overloaded;4=On high overload
7230 | DIF1:Idx> condition | R | 2 | 0b=Idb> Trip;1b=Idb> Blocked;2b=Idi> Trip;3b=Idi> Blocked;4b=2nd Harm block on;5b=5th harm block on;6b=L1 2h On;7b=L2 2h On;8b=L3 2h On;9b=L1 5h On;10b=L2 5h On;11b=L3 5h On (Hi-16bits)
7231 |  |  |  | HR7230 (Lo-16bits)
7232 | DIF1:REFHV> condition | R | 2 | 0b=HV REF Blocked;1b=HV REF Trip (Hi-16bits)
7233 |  |  |  | HR7232 (Lo-16bits)
7234 | DIF1:REFLV> condition | R | 2 | 0b=LV REF Blocked;1b=LV REF Trip (Hi-16bits)
7235 |  |  |  | HR7234 (Lo-16bits)
7236 | DIF1:L1 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7237 | DIF1:L2 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7238 | DIF1:L3 Condition | R | 1 | 0=No Diff;1=Magnitude diff;2=Angle diff;3=Mag.and angle diff
7239 | REF1:I0d> condition | R | 1 | 0=Normal;1=Trip;2=Blocked
7240 | TOLT1:TT> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7241 | TOLT1:TT> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7242 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7243 | TOLT1:TT> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7244 | TOLT1:TT> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7245 | TOLT1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7246 | TOLT1:Temp C or F deg | RW | 1 | 0=C;1=F
7247 | TOLT1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7248 | TOLT1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7249 | TOLT1:TT> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7250 |  |  |  | HR7249 (Lo-16bits)
7251 | TOLF1:TF> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7252 | TOLF1:TF> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7253 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7254 | TOLF1:TF> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7255 | TOLF1:TF> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7256 | TOLF1:Thermal status | R | 1 | 0=Light / No load;1=High overload;2=Overloading;3=Load normal
7257 | TOLF1:Temp C or F deg | RW | 1 | 0=C;1=F
7258 | TOLF1:Ambient Temp Sel | RW | 1 | 0=Manual Set;1=RTD Meas
7259 | TOLF1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7260 | TOLF1:Set or Estimate tau (t const) | RW | 1 | 0=Set;1=Estimate
7261 | TOLF1:TF> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7262 |  |  |  | HR7261 (Lo-16bits)
7263 | TOLM1:TM> condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On;3=Inhibit On;4=Trip On;5=Blocked
7264 | TOLM1:TM> Setting alarm | R | 1 | 0=SF setting ok;1=Service factor set fault. Override to 1.0
7265 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient t setting ok;1=Ambient t set fault. Override to 1.0
7266 | TOLM1:TM> Setting alarm | R | 1 | 0=Nominal current calc ok;1=Nominal current set fault. Override to 1.0
7267 | TOLM1:TM> Setting alarm | R | 1 | 0=Ambient setting ok;1=Inconsistent setting of ambient k
7268 | TOLM1:Motor status | R | 1 | 0=Stopped;1=Stalled;2=JustStopped;3=Overloading;4=Running normal
7269 | TOLM1:Temp C or F deg | RW | 1 | 0=C;1=F
7270 | TOLM1:NPS Biasing in use | RW | 1 | 0=No NPS biasing;1=NPS Biasing in use
7271 | TOLM1:Time constants | RW | 1 | 0=Single;1=Multiple
7272 | TOLM1:Estimate Short TC and timings | RW | 1 | 0=Set manually;1=Estimate (on-line)
7273 | TOLM1:T const dyn. balancing | RW | 1 | 0=Fixed;1=Dynamic
7274 | TOLM1:Dev.Temp (tmax) | RW | 1 | 0=A;1=B;2=F;3=H;4=Manual set
7275 | TOLM1:Amb. T Selection | RW | 1 | 0=Manual set;1=RTD
7276 | TOLM1:RTD Sensor | R | 1 | 0=Invalid;1=OK
7277 | TOLM1:TM> Thermal cap used | R | 2 | FLOAT [0...500] (Hi-16bits)
7278 |  |  |  | HR7277 (Lo-16bits)
7279 | LCR1:ISt> condition | R | 1 | 0=Normal;1=Start; 2=Set time Trip;3=M cap Trip;4=Blocked
7280 | FSP1:N> condition | R | 1 | 0=Normal;1=Alarm On;2=Inhibits;3=Blocked
7281 | NUC1:I< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7282 | MJP1:Im> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
7283 | OV1:U> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7284 | OV1:U> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7285 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7286 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7287 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7288 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7289 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7290 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7291 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7292 | OV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7293 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7294 |  |  |  | HR7293 (Lo-16bits)
7295 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7296 |  |  |  | HR7295 (Lo-16bits)
7297 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7298 |  |  |  | HR7297 (Lo-16bits)
7299 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7300 |  |  |  | HR7299 (Lo-16bits)
7301 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7302 |  |  |  | HR7301 (Lo-16bits)
7303 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7304 |  |  |  | HR7303 (Lo-16bits)
7305 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7306 |  |  |  | HR7305 (Lo-16bits)
7307 | OV1:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7308 |  |  |  | HR7307 (Lo-16bits)
7309 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7310 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7311 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7312 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7313 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7314 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7315 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7316 | OV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7317 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7318 |  |  |  | HR7317 (Lo-16bits)
7319 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7320 |  |  |  | HR7319 (Lo-16bits)
7321 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7322 |  |  |  | HR7321 (Lo-16bits)
7323 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7324 |  |  |  | HR7323 (Lo-16bits)
7325 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7326 |  |  |  | HR7325 (Lo-16bits)
7327 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7328 |  |  |  | HR7327 (Lo-16bits)
7329 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7330 |  |  |  | HR7329 (Lo-16bits)
7331 | OV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7332 |  |  |  | HR7331 (Lo-16bits)
7333 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7334 |  |  |  | HR7333 (Lo-16bits)
7335 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7336 |  |  |  | HR7335 (Lo-16bits)
7337 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7338 |  |  |  | HR7337 (Lo-16bits)
7339 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7340 |  |  |  | HR7339 (Lo-16bits)
7341 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7342 |  |  |  | HR7341 (Lo-16bits)
7343 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7344 |  |  |  | HR7343 (Lo-16bits)
7345 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7346 |  |  |  | HR7345 (Lo-16bits)
7347 | OV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7348 |  |  |  | HR7347 (Lo-16bits)
7349 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7350 |  |  |  | HR7349 (Lo-16bits)
7351 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7352 |  |  |  | HR7351 (Lo-16bits)
7353 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7354 |  |  |  | HR7353 (Lo-16bits)
7355 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7356 |  |  |  | HR7355 (Lo-16bits)
7357 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7358 |  |  |  | HR7357 (Lo-16bits)
7359 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7360 |  |  |  | HR7359 (Lo-16bits)
7361 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7362 |  |  |  | HR7361 (Lo-16bits)
7363 | OV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7364 |  |  |  | HR7363 (Lo-16bits)
7365 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7366 |  |  |  | HR7365 (Lo-16bits)
7367 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7368 |  |  |  | HR7367 (Lo-16bits)
7369 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7370 |  |  |  | HR7369 (Lo-16bits)
7371 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7372 |  |  |  | HR7371 (Lo-16bits)
7373 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7374 |  |  |  | HR7373 (Lo-16bits)
7375 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7376 |  |  |  | HR7375 (Lo-16bits)
7377 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7378 |  |  |  | HR7377 (Lo-16bits)
7379 | OV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7380 |  |  |  | HR7379 (Lo-16bits)
7381 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7382 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7383 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7384 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7385 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7386 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7387 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7388 | OV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7389 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7390 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7391 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7392 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7393 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7394 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7395 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7396 | OV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7397 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7398 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7399 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7400 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7401 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7402 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7403 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7404 | OV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7405 | OV2:U>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7406 | OV2:U>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7407 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7408 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7409 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7410 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7411 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7412 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7413 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7414 | OV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7415 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7416 |  |  |  | HR7415 (Lo-16bits)
7417 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7418 |  |  |  | HR7417 (Lo-16bits)
7419 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7420 |  |  |  | HR7419 (Lo-16bits)
7421 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7422 |  |  |  | HR7421 (Lo-16bits)
7423 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7424 |  |  |  | HR7423 (Lo-16bits)
7425 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7426 |  |  |  | HR7425 (Lo-16bits)
7427 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7428 |  |  |  | HR7427 (Lo-16bits)
7429 | OV2:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7430 |  |  |  | HR7429 (Lo-16bits)
7431 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7432 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7433 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7434 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7435 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7436 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7437 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7438 | OV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7439 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7440 |  |  |  | HR7439 (Lo-16bits)
7441 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7442 |  |  |  | HR7441 (Lo-16bits)
7443 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7444 |  |  |  | HR7443 (Lo-16bits)
7445 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7446 |  |  |  | HR7445 (Lo-16bits)
7447 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7448 |  |  |  | HR7447 (Lo-16bits)
7449 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7450 |  |  |  | HR7449 (Lo-16bits)
7451 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7452 |  |  |  | HR7451 (Lo-16bits)
7453 | OV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7454 |  |  |  | HR7453 (Lo-16bits)
7455 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7456 |  |  |  | HR7455 (Lo-16bits)
7457 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7458 |  |  |  | HR7457 (Lo-16bits)
7459 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7460 |  |  |  | HR7459 (Lo-16bits)
7461 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7462 |  |  |  | HR7461 (Lo-16bits)
7463 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7464 |  |  |  | HR7463 (Lo-16bits)
7465 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7466 |  |  |  | HR7465 (Lo-16bits)
7467 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7468 |  |  |  | HR7467 (Lo-16bits)
7469 | OV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7470 |  |  |  | HR7469 (Lo-16bits)
7471 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7472 |  |  |  | HR7471 (Lo-16bits)
7473 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7474 |  |  |  | HR7473 (Lo-16bits)
7475 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7476 |  |  |  | HR7475 (Lo-16bits)
7477 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7478 |  |  |  | HR7477 (Lo-16bits)
7479 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7480 |  |  |  | HR7479 (Lo-16bits)
7481 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7482 |  |  |  | HR7481 (Lo-16bits)
7483 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7484 |  |  |  | HR7483 (Lo-16bits)
7485 | OV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7486 |  |  |  | HR7485 (Lo-16bits)
7487 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7488 |  |  |  | HR7487 (Lo-16bits)
7489 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7490 |  |  |  | HR7489 (Lo-16bits)
7491 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7492 |  |  |  | HR7491 (Lo-16bits)
7493 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7494 |  |  |  | HR7493 (Lo-16bits)
7495 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7496 |  |  |  | HR7495 (Lo-16bits)
7497 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7498 |  |  |  | HR7497 (Lo-16bits)
7499 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7500 |  |  |  | HR7499 (Lo-16bits)
7501 | OV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7502 |  |  |  | HR7501 (Lo-16bits)
7503 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7504 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7505 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7506 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7507 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7508 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7509 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7510 | OV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7511 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7512 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7513 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7514 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7515 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7516 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7517 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7518 | OV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7519 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7520 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7521 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7522 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7523 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7524 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7525 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7526 | OV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7527 | OV3:U>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7528 | OV3:U>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7529 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7530 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7531 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7532 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7533 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7534 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7535 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7536 | OV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7537 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7538 |  |  |  | HR7537 (Lo-16bits)
7539 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7540 |  |  |  | HR7539 (Lo-16bits)
7541 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7542 |  |  |  | HR7541 (Lo-16bits)
7543 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7544 |  |  |  | HR7543 (Lo-16bits)
7545 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7546 |  |  |  | HR7545 (Lo-16bits)
7547 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7548 |  |  |  | HR7547 (Lo-16bits)
7549 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7550 |  |  |  | HR7549 (Lo-16bits)
7551 | OV3:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7552 |  |  |  | HR7551 (Lo-16bits)
7553 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7554 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7555 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7556 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7557 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7558 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7559 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7560 | OV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
7561 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7562 |  |  |  | HR7561 (Lo-16bits)
7563 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7564 |  |  |  | HR7563 (Lo-16bits)
7565 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7566 |  |  |  | HR7565 (Lo-16bits)
7567 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7568 |  |  |  | HR7567 (Lo-16bits)
7569 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7570 |  |  |  | HR7569 (Lo-16bits)
7571 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7572 |  |  |  | HR7571 (Lo-16bits)
7573 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7574 |  |  |  | HR7573 (Lo-16bits)
7575 | OV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7576 |  |  |  | HR7575 (Lo-16bits)
7577 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7578 |  |  |  | HR7577 (Lo-16bits)
7579 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7580 |  |  |  | HR7579 (Lo-16bits)
7581 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7582 |  |  |  | HR7581 (Lo-16bits)
7583 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7584 |  |  |  | HR7583 (Lo-16bits)
7585 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7586 |  |  |  | HR7585 (Lo-16bits)
7587 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7588 |  |  |  | HR7587 (Lo-16bits)
7589 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7590 |  |  |  | HR7589 (Lo-16bits)
7591 | OV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7592 |  |  |  | HR7591 (Lo-16bits)
7593 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7594 |  |  |  | HR7593 (Lo-16bits)
7595 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7596 |  |  |  | HR7595 (Lo-16bits)
7597 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7598 |  |  |  | HR7597 (Lo-16bits)
7599 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7600 |  |  |  | HR7599 (Lo-16bits)
7601 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7602 |  |  |  | HR7601 (Lo-16bits)
7603 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7604 |  |  |  | HR7603 (Lo-16bits)
7605 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7606 |  |  |  | HR7605 (Lo-16bits)
7607 | OV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7608 |  |  |  | HR7607 (Lo-16bits)
7609 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7610 |  |  |  | HR7609 (Lo-16bits)
7611 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7612 |  |  |  | HR7611 (Lo-16bits)
7613 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7614 |  |  |  | HR7613 (Lo-16bits)
7615 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7616 |  |  |  | HR7615 (Lo-16bits)
7617 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7618 |  |  |  | HR7617 (Lo-16bits)
7619 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7620 |  |  |  | HR7619 (Lo-16bits)
7621 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7622 |  |  |  | HR7621 (Lo-16bits)
7623 | OV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7624 |  |  |  | HR7623 (Lo-16bits)
7625 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7626 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7627 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7628 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7629 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7630 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7631 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7632 | OV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7633 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7634 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7635 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7636 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7637 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7638 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7639 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7640 | OV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7641 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7642 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7643 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7644 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7645 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7646 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7647 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7648 | OV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7649 | OV4:U>>>> [59] mode | R(W) | 1 | 0=Disabled;1=Activated
7650 | OV4:U>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
7651 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7652 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7653 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7654 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7655 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7656 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7657 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7658 | OV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7659 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7660 |  |  |  | HR7659 (Lo-16bits)
7661 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7662 |  |  |  | HR7661 (Lo-16bits)
7663 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7664 |  |  |  | HR7663 (Lo-16bits)
7665 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7666 |  |  |  | HR7665 (Lo-16bits)
7667 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7668 |  |  |  | HR7667 (Lo-16bits)
7669 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7670 |  |  |  | HR7669 (Lo-16bits)
7671 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7672 |  |  |  | HR7671 (Lo-16bits)
7673 | OV4:Pick-up setting Uset | R(W) | 2 | FLOAT [50...150] (Hi-16bits)
7674 |  |  |  | HR7673 (Lo-16bits)
7675 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7676 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7677 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7678 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7679 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7680 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7681 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7682 | OV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
7683 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7684 |  |  |  | HR7683 (Lo-16bits)
7685 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7686 |  |  |  | HR7685 (Lo-16bits)
7687 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7688 |  |  |  | HR7687 (Lo-16bits)
7689 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7690 |  |  |  | HR7689 (Lo-16bits)
7691 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7692 |  |  |  | HR7691 (Lo-16bits)
7693 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7694 |  |  |  | HR7693 (Lo-16bits)
7695 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7696 |  |  |  | HR7695 (Lo-16bits)
7697 | OV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7698 |  |  |  | HR7697 (Lo-16bits)
7699 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7700 |  |  |  | HR7699 (Lo-16bits)
7701 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7702 |  |  |  | HR7701 (Lo-16bits)
7703 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7704 |  |  |  | HR7703 (Lo-16bits)
7705 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7706 |  |  |  | HR7705 (Lo-16bits)
7707 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7708 |  |  |  | HR7707 (Lo-16bits)
7709 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7710 |  |  |  | HR7709 (Lo-16bits)
7711 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7712 |  |  |  | HR7711 (Lo-16bits)
7713 | OV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7714 |  |  |  | HR7713 (Lo-16bits)
7715 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7716 |  |  |  | HR7715 (Lo-16bits)
7717 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7718 |  |  |  | HR7717 (Lo-16bits)
7719 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7720 |  |  |  | HR7719 (Lo-16bits)
7721 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7722 |  |  |  | HR7721 (Lo-16bits)
7723 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7724 |  |  |  | HR7723 (Lo-16bits)
7725 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7726 |  |  |  | HR7725 (Lo-16bits)
7727 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7728 |  |  |  | HR7727 (Lo-16bits)
7729 | OV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7730 |  |  |  | HR7729 (Lo-16bits)
7731 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7732 |  |  |  | HR7731 (Lo-16bits)
7733 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7734 |  |  |  | HR7733 (Lo-16bits)
7735 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7736 |  |  |  | HR7735 (Lo-16bits)
7737 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7738 |  |  |  | HR7737 (Lo-16bits)
7739 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7740 |  |  |  | HR7739 (Lo-16bits)
7741 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7742 |  |  |  | HR7741 (Lo-16bits)
7743 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7744 |  |  |  | HR7743 (Lo-16bits)
7745 | OV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7746 |  |  |  | HR7745 (Lo-16bits)
7747 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7748 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7749 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7750 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7751 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7752 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7753 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7754 | OV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7755 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7756 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7757 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7758 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7759 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7760 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7761 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7762 | OV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7763 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7764 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7765 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7766 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7767 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7768 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7769 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7770 | OV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7771 | UV1:U< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7772 | UV1:U< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7773 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7774 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7775 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7776 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7777 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7778 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7779 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7780 | UV1:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7781 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7782 |  |  |  | HR7781 (Lo-16bits)
7783 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7784 |  |  |  | HR7783 (Lo-16bits)
7785 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7786 |  |  |  | HR7785 (Lo-16bits)
7787 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7788 |  |  |  | HR7787 (Lo-16bits)
7789 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7790 |  |  |  | HR7789 (Lo-16bits)
7791 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7792 |  |  |  | HR7791 (Lo-16bits)
7793 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7794 |  |  |  | HR7793 (Lo-16bits)
7795 | UV1:Pick-up setting Uset< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7796 |  |  |  | HR7795 (Lo-16bits)
7797 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7798 |  |  |  | HR7797 (Lo-16bits)
7799 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7800 |  |  |  | HR7799 (Lo-16bits)
7801 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7802 |  |  |  | HR7801 (Lo-16bits)
7803 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7804 |  |  |  | HR7803 (Lo-16bits)
7805 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7806 |  |  |  | HR7805 (Lo-16bits)
7807 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7808 |  |  |  | HR7807 (Lo-16bits)
7809 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7810 |  |  |  | HR7809 (Lo-16bits)
7811 | UV1:Block setting Uset< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7812 |  |  |  | HR7811 (Lo-16bits)
7813 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7814 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7815 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7816 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7817 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7818 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7819 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7820 | UV1:Delay type | R(W) | 1 | 0=DT;1=IDMT
7821 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7822 |  |  |  | HR7821 (Lo-16bits)
7823 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7824 |  |  |  | HR7823 (Lo-16bits)
7825 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7826 |  |  |  | HR7825 (Lo-16bits)
7827 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7828 |  |  |  | HR7827 (Lo-16bits)
7829 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7830 |  |  |  | HR7829 (Lo-16bits)
7831 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7832 |  |  |  | HR7831 (Lo-16bits)
7833 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7834 |  |  |  | HR7833 (Lo-16bits)
7835 | UV1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7836 |  |  |  | HR7835 (Lo-16bits)
7837 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7838 |  |  |  | HR7837 (Lo-16bits)
7839 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7840 |  |  |  | HR7839 (Lo-16bits)
7841 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7842 |  |  |  | HR7841 (Lo-16bits)
7843 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7844 |  |  |  | HR7843 (Lo-16bits)
7845 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7846 |  |  |  | HR7845 (Lo-16bits)
7847 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7848 |  |  |  | HR7847 (Lo-16bits)
7849 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7850 |  |  |  | HR7849 (Lo-16bits)
7851 | UV1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7852 |  |  |  | HR7851 (Lo-16bits)
7853 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7854 |  |  |  | HR7853 (Lo-16bits)
7855 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7856 |  |  |  | HR7855 (Lo-16bits)
7857 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7858 |  |  |  | HR7857 (Lo-16bits)
7859 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7860 |  |  |  | HR7859 (Lo-16bits)
7861 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7862 |  |  |  | HR7861 (Lo-16bits)
7863 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7864 |  |  |  | HR7863 (Lo-16bits)
7865 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7866 |  |  |  | HR7865 (Lo-16bits)
7867 | UV1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7868 |  |  |  | HR7867 (Lo-16bits)
7869 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7870 |  |  |  | HR7869 (Lo-16bits)
7871 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7872 |  |  |  | HR7871 (Lo-16bits)
7873 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7874 |  |  |  | HR7873 (Lo-16bits)
7875 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7876 |  |  |  | HR7875 (Lo-16bits)
7877 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7878 |  |  |  | HR7877 (Lo-16bits)
7879 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7880 |  |  |  | HR7879 (Lo-16bits)
7881 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7882 |  |  |  | HR7881 (Lo-16bits)
7883 | UV1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
7884 |  |  |  | HR7883 (Lo-16bits)
7885 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7886 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7887 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7888 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7889 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7890 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7891 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7892 | UV1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
7893 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7894 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7895 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7896 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7897 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7898 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7899 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7900 | UV1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
7901 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7902 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7903 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7904 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7905 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7906 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7907 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7908 | UV1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
7909 | UV2:U<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
7910 | UV2:U<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
7911 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7912 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7913 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7914 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7915 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7916 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7917 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7918 | UV2:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
7919 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7920 |  |  |  | HR7919 (Lo-16bits)
7921 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7922 |  |  |  | HR7921 (Lo-16bits)
7923 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7924 |  |  |  | HR7923 (Lo-16bits)
7925 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7926 |  |  |  | HR7925 (Lo-16bits)
7927 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7928 |  |  |  | HR7927 (Lo-16bits)
7929 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7930 |  |  |  | HR7929 (Lo-16bits)
7931 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7932 |  |  |  | HR7931 (Lo-16bits)
7933 | UV2:Pick-up setting Uset<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
7934 |  |  |  | HR7933 (Lo-16bits)
7935 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7936 |  |  |  | HR7935 (Lo-16bits)
7937 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7938 |  |  |  | HR7937 (Lo-16bits)
7939 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7940 |  |  |  | HR7939 (Lo-16bits)
7941 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7942 |  |  |  | HR7941 (Lo-16bits)
7943 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7944 |  |  |  | HR7943 (Lo-16bits)
7945 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7946 |  |  |  | HR7945 (Lo-16bits)
7947 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7948 |  |  |  | HR7947 (Lo-16bits)
7949 | UV2:Block setting Uset<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
7950 |  |  |  | HR7949 (Lo-16bits)
7951 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7952 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7953 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7954 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7955 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7956 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7957 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7958 | UV2:Delay type | R(W) | 1 | 0=DT;1=IDMT
7959 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7960 |  |  |  | HR7959 (Lo-16bits)
7961 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7962 |  |  |  | HR7961 (Lo-16bits)
7963 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7964 |  |  |  | HR7963 (Lo-16bits)
7965 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7966 |  |  |  | HR7965 (Lo-16bits)
7967 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7968 |  |  |  | HR7967 (Lo-16bits)
7969 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7970 |  |  |  | HR7969 (Lo-16bits)
7971 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7972 |  |  |  | HR7971 (Lo-16bits)
7973 | UV2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
7974 |  |  |  | HR7973 (Lo-16bits)
7975 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7976 |  |  |  | HR7975 (Lo-16bits)
7977 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7978 |  |  |  | HR7977 (Lo-16bits)
7979 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7980 |  |  |  | HR7979 (Lo-16bits)
7981 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7982 |  |  |  | HR7981 (Lo-16bits)
7983 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7984 |  |  |  | HR7983 (Lo-16bits)
7985 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7986 |  |  |  | HR7985 (Lo-16bits)
7987 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7988 |  |  |  | HR7987 (Lo-16bits)
7989 | UV2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
7990 |  |  |  | HR7989 (Lo-16bits)
7991 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7992 |  |  |  | HR7991 (Lo-16bits)
7993 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7994 |  |  |  | HR7993 (Lo-16bits)
7995 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7996 |  |  |  | HR7995 (Lo-16bits)
7997 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
7998 |  |  |  | HR7997 (Lo-16bits)
7999 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8000 |  |  |  | HR7999 (Lo-16bits)
8001 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8002 |  |  |  | HR8001 (Lo-16bits)
8003 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8004 |  |  |  | HR8003 (Lo-16bits)
8005 | UV2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8006 |  |  |  | HR8005 (Lo-16bits)
8007 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8008 |  |  |  | HR8007 (Lo-16bits)
8009 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8010 |  |  |  | HR8009 (Lo-16bits)
8011 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8012 |  |  |  | HR8011 (Lo-16bits)
8013 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8014 |  |  |  | HR8013 (Lo-16bits)
8015 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8016 |  |  |  | HR8015 (Lo-16bits)
8017 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8018 |  |  |  | HR8017 (Lo-16bits)
8019 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8020 |  |  |  | HR8019 (Lo-16bits)
8021 | UV2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8022 |  |  |  | HR8021 (Lo-16bits)
8023 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8024 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8025 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8026 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8027 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8028 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8029 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8030 | UV2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8031 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8032 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8033 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8034 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8035 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8036 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8037 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8038 | UV2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8039 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8040 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8041 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8042 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8043 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8044 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8045 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8046 | UV2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8047 | UV3:U<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
8048 | UV3:U<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
8049 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8050 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8051 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8052 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8053 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8054 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8055 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8056 | UV3:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8057 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8058 |  |  |  | HR8057 (Lo-16bits)
8059 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8060 |  |  |  | HR8059 (Lo-16bits)
8061 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8062 |  |  |  | HR8061 (Lo-16bits)
8063 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8064 |  |  |  | HR8063 (Lo-16bits)
8065 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8066 |  |  |  | HR8065 (Lo-16bits)
8067 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8068 |  |  |  | HR8067 (Lo-16bits)
8069 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8070 |  |  |  | HR8069 (Lo-16bits)
8071 | UV3:Pick-up setting Uset<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8072 |  |  |  | HR8071 (Lo-16bits)
8073 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8074 |  |  |  | HR8073 (Lo-16bits)
8075 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8076 |  |  |  | HR8075 (Lo-16bits)
8077 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8078 |  |  |  | HR8077 (Lo-16bits)
8079 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8080 |  |  |  | HR8079 (Lo-16bits)
8081 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8082 |  |  |  | HR8081 (Lo-16bits)
8083 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8084 |  |  |  | HR8083 (Lo-16bits)
8085 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8086 |  |  |  | HR8085 (Lo-16bits)
8087 | UV3:Block setting Uset<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8088 |  |  |  | HR8087 (Lo-16bits)
8089 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8090 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8091 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8092 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8093 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8094 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8095 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8096 | UV3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8097 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8098 |  |  |  | HR8097 (Lo-16bits)
8099 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8100 |  |  |  | HR8099 (Lo-16bits)
8101 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8102 |  |  |  | HR8101 (Lo-16bits)
8103 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8104 |  |  |  | HR8103 (Lo-16bits)
8105 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8106 |  |  |  | HR8105 (Lo-16bits)
8107 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8108 |  |  |  | HR8107 (Lo-16bits)
8109 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8110 |  |  |  | HR8109 (Lo-16bits)
8111 | UV3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8112 |  |  |  | HR8111 (Lo-16bits)
8113 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8114 |  |  |  | HR8113 (Lo-16bits)
8115 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8116 |  |  |  | HR8115 (Lo-16bits)
8117 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8118 |  |  |  | HR8117 (Lo-16bits)
8119 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8120 |  |  |  | HR8119 (Lo-16bits)
8121 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8122 |  |  |  | HR8121 (Lo-16bits)
8123 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8124 |  |  |  | HR8123 (Lo-16bits)
8125 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8126 |  |  |  | HR8125 (Lo-16bits)
8127 | UV3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8128 |  |  |  | HR8127 (Lo-16bits)
8129 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8130 |  |  |  | HR8129 (Lo-16bits)
8131 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8132 |  |  |  | HR8131 (Lo-16bits)
8133 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8134 |  |  |  | HR8133 (Lo-16bits)
8135 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8136 |  |  |  | HR8135 (Lo-16bits)
8137 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8138 |  |  |  | HR8137 (Lo-16bits)
8139 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8140 |  |  |  | HR8139 (Lo-16bits)
8141 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8142 |  |  |  | HR8141 (Lo-16bits)
8143 | UV3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8144 |  |  |  | HR8143 (Lo-16bits)
8145 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8146 |  |  |  | HR8145 (Lo-16bits)
8147 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8148 |  |  |  | HR8147 (Lo-16bits)
8149 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8150 |  |  |  | HR8149 (Lo-16bits)
8151 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8152 |  |  |  | HR8151 (Lo-16bits)
8153 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8154 |  |  |  | HR8153 (Lo-16bits)
8155 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8156 |  |  |  | HR8155 (Lo-16bits)
8157 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8158 |  |  |  | HR8157 (Lo-16bits)
8159 | UV3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8160 |  |  |  | HR8159 (Lo-16bits)
8161 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8162 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8163 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8164 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8165 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8166 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8167 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8168 | UV3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8169 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8170 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8171 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8172 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8173 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8174 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8175 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8176 | UV3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8177 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8178 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8179 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8180 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8181 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8182 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8183 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8184 | UV3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8185 | UV4:U<<<< [27] mode | R(W) | 1 | 0=Disabled;1=Activated
8186 | UV4:U<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Undervolt Blk On
8187 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8188 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8189 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8190 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8191 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8192 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8193 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8194 | UV4:Pick-up terms | R(W) | 1 | 0=1 voltage;1=2 voltages;2=3 voltages
8195 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8196 |  |  |  | HR8195 (Lo-16bits)
8197 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8198 |  |  |  | HR8197 (Lo-16bits)
8199 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8200 |  |  |  | HR8199 (Lo-16bits)
8201 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8202 |  |  |  | HR8201 (Lo-16bits)
8203 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8204 |  |  |  | HR8203 (Lo-16bits)
8205 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8206 |  |  |  | HR8205 (Lo-16bits)
8207 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8208 |  |  |  | HR8207 (Lo-16bits)
8209 | UV4:Pick-up setting Uset<<<< | R(W) | 2 | FLOAT [0...120] (Hi-16bits)
8210 |  |  |  | HR8209 (Lo-16bits)
8211 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8212 |  |  |  | HR8211 (Lo-16bits)
8213 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8214 |  |  |  | HR8213 (Lo-16bits)
8215 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8216 |  |  |  | HR8215 (Lo-16bits)
8217 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8218 |  |  |  | HR8217 (Lo-16bits)
8219 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8220 |  |  |  | HR8219 (Lo-16bits)
8221 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8222 |  |  |  | HR8221 (Lo-16bits)
8223 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8224 |  |  |  | HR8223 (Lo-16bits)
8225 | UV4:Block setting Uset<<<< | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8226 |  |  |  | HR8225 (Lo-16bits)
8227 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8228 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8229 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8230 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8231 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8232 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8233 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8234 | UV4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8235 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8236 |  |  |  | HR8235 (Lo-16bits)
8237 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8238 |  |  |  | HR8237 (Lo-16bits)
8239 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8240 |  |  |  | HR8239 (Lo-16bits)
8241 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8242 |  |  |  | HR8241 (Lo-16bits)
8243 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8244 |  |  |  | HR8243 (Lo-16bits)
8245 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8246 |  |  |  | HR8245 (Lo-16bits)
8247 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8248 |  |  |  | HR8247 (Lo-16bits)
8249 | UV4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8250 |  |  |  | HR8249 (Lo-16bits)
8251 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8252 |  |  |  | HR8251 (Lo-16bits)
8253 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8254 |  |  |  | HR8253 (Lo-16bits)
8255 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8256 |  |  |  | HR8255 (Lo-16bits)
8257 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8258 |  |  |  | HR8257 (Lo-16bits)
8259 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8260 |  |  |  | HR8259 (Lo-16bits)
8261 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8262 |  |  |  | HR8261 (Lo-16bits)
8263 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8264 |  |  |  | HR8263 (Lo-16bits)
8265 | UV4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8266 |  |  |  | HR8265 (Lo-16bits)
8267 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8268 |  |  |  | HR8267 (Lo-16bits)
8269 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8270 |  |  |  | HR8269 (Lo-16bits)
8271 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8272 |  |  |  | HR8271 (Lo-16bits)
8273 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8274 |  |  |  | HR8273 (Lo-16bits)
8275 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8276 |  |  |  | HR8275 (Lo-16bits)
8277 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8278 |  |  |  | HR8277 (Lo-16bits)
8279 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8280 |  |  |  | HR8279 (Lo-16bits)
8281 | UV4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8282 |  |  |  | HR8281 (Lo-16bits)
8283 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8284 |  |  |  | HR8283 (Lo-16bits)
8285 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8286 |  |  |  | HR8285 (Lo-16bits)
8287 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8288 |  |  |  | HR8287 (Lo-16bits)
8289 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8290 |  |  |  | HR8289 (Lo-16bits)
8291 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8292 |  |  |  | HR8291 (Lo-16bits)
8293 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8294 |  |  |  | HR8293 (Lo-16bits)
8295 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8296 |  |  |  | HR8295 (Lo-16bits)
8297 | UV4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8298 |  |  |  | HR8297 (Lo-16bits)
8299 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8300 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8301 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8302 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8303 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8304 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8305 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8306 | UV4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8307 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8308 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8309 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8310 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8311 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8312 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8313 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8314 | UV4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8315 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8316 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8317 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8318 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8319 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8320 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8321 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8322 | UV4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8323 | NOV1:U0> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8324 | NOV1:U0> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8325 | NOV2:U0>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8326 | NOV2:U0>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8327 | NOV3:U0>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8328 | NOV3:U0>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8329 | NOV4:U0>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8330 | NOV4:U0>>>> Measuring now | R | 1 | 0=No U0 avail!;1=U0Calc;2=U3 Input;3=U4 Input
8331 | VUB1:U1/2 >/< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8332 | VUB1:U1/2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8333 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8334 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8335 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8336 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8337 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8338 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8339 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8340 | VUB1:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8341 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8342 |  |  |  | HR8341 (Lo-16bits)
8343 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8344 |  |  |  | HR8343 (Lo-16bits)
8345 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8346 |  |  |  | HR8345 (Lo-16bits)
8347 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8348 |  |  |  | HR8347 (Lo-16bits)
8349 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8350 |  |  |  | HR8349 (Lo-16bits)
8351 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8352 |  |  |  | HR8351 (Lo-16bits)
8353 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8354 |  |  |  | HR8353 (Lo-16bits)
8355 | VUB1:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8356 |  |  |  | HR8355 (Lo-16bits)
8357 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8358 |  |  |  | HR8357 (Lo-16bits)
8359 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8360 |  |  |  | HR8359 (Lo-16bits)
8361 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8362 |  |  |  | HR8361 (Lo-16bits)
8363 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8364 |  |  |  | HR8363 (Lo-16bits)
8365 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8366 |  |  |  | HR8365 (Lo-16bits)
8367 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8368 |  |  |  | HR8367 (Lo-16bits)
8369 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8370 |  |  |  | HR8369 (Lo-16bits)
8371 | VUB1:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8372 |  |  |  | HR8371 (Lo-16bits)
8373 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8374 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8375 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8376 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8377 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8378 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8379 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8380 | VUB1:Delay type | R(W) | 1 | 0=DT;1=IDMT
8381 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8382 |  |  |  | HR8381 (Lo-16bits)
8383 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8384 |  |  |  | HR8383 (Lo-16bits)
8385 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8386 |  |  |  | HR8385 (Lo-16bits)
8387 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8388 |  |  |  | HR8387 (Lo-16bits)
8389 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8390 |  |  |  | HR8389 (Lo-16bits)
8391 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8392 |  |  |  | HR8391 (Lo-16bits)
8393 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8394 |  |  |  | HR8393 (Lo-16bits)
8395 | VUB1:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8396 |  |  |  | HR8395 (Lo-16bits)
8397 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8398 |  |  |  | HR8397 (Lo-16bits)
8399 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8400 |  |  |  | HR8399 (Lo-16bits)
8401 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8402 |  |  |  | HR8401 (Lo-16bits)
8403 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8404 |  |  |  | HR8403 (Lo-16bits)
8405 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8406 |  |  |  | HR8405 (Lo-16bits)
8407 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8408 |  |  |  | HR8407 (Lo-16bits)
8409 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8410 |  |  |  | HR8409 (Lo-16bits)
8411 | VUB1:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8412 |  |  |  | HR8411 (Lo-16bits)
8413 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8414 |  |  |  | HR8413 (Lo-16bits)
8415 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8416 |  |  |  | HR8415 (Lo-16bits)
8417 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8418 |  |  |  | HR8417 (Lo-16bits)
8419 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8420 |  |  |  | HR8419 (Lo-16bits)
8421 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8422 |  |  |  | HR8421 (Lo-16bits)
8423 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8424 |  |  |  | HR8423 (Lo-16bits)
8425 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8426 |  |  |  | HR8425 (Lo-16bits)
8427 | VUB1:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8428 |  |  |  | HR8427 (Lo-16bits)
8429 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8430 |  |  |  | HR8429 (Lo-16bits)
8431 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8432 |  |  |  | HR8431 (Lo-16bits)
8433 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8434 |  |  |  | HR8433 (Lo-16bits)
8435 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8436 |  |  |  | HR8435 (Lo-16bits)
8437 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8438 |  |  |  | HR8437 (Lo-16bits)
8439 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8440 |  |  |  | HR8439 (Lo-16bits)
8441 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8442 |  |  |  | HR8441 (Lo-16bits)
8443 | VUB1:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8444 |  |  |  | HR8443 (Lo-16bits)
8445 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8446 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8447 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8448 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8449 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8450 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8451 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8452 | VUB1:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8453 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8454 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8455 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8456 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8457 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8458 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8459 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8460 | VUB1:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8461 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8462 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8463 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8464 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8465 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8466 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8467 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8468 | VUB1:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8469 | VUB2:U1/2 >>/<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8470 | VUB2:U1/2 >>/<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8471 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8472 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8473 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8474 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8475 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8476 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8477 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8478 | VUB2:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8479 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8480 |  |  |  | HR8479 (Lo-16bits)
8481 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8482 |  |  |  | HR8481 (Lo-16bits)
8483 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8484 |  |  |  | HR8483 (Lo-16bits)
8485 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8486 |  |  |  | HR8485 (Lo-16bits)
8487 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8488 |  |  |  | HR8487 (Lo-16bits)
8489 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8490 |  |  |  | HR8489 (Lo-16bits)
8491 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8492 |  |  |  | HR8491 (Lo-16bits)
8493 | VUB2:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8494 |  |  |  | HR8493 (Lo-16bits)
8495 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8496 |  |  |  | HR8495 (Lo-16bits)
8497 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8498 |  |  |  | HR8497 (Lo-16bits)
8499 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8500 |  |  |  | HR8499 (Lo-16bits)
8501 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8502 |  |  |  | HR8501 (Lo-16bits)
8503 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8504 |  |  |  | HR8503 (Lo-16bits)
8505 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8506 |  |  |  | HR8505 (Lo-16bits)
8507 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8508 |  |  |  | HR8507 (Lo-16bits)
8509 | VUB2:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8510 |  |  |  | HR8509 (Lo-16bits)
8511 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8512 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8513 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8514 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8515 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8516 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8517 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8518 | VUB2:Delay type | R(W) | 1 | 0=DT;1=IDMT
8519 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8520 |  |  |  | HR8519 (Lo-16bits)
8521 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8522 |  |  |  | HR8521 (Lo-16bits)
8523 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8524 |  |  |  | HR8523 (Lo-16bits)
8525 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8526 |  |  |  | HR8525 (Lo-16bits)
8527 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8528 |  |  |  | HR8527 (Lo-16bits)
8529 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8530 |  |  |  | HR8529 (Lo-16bits)
8531 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8532 |  |  |  | HR8531 (Lo-16bits)
8533 | VUB2:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8534 |  |  |  | HR8533 (Lo-16bits)
8535 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8536 |  |  |  | HR8535 (Lo-16bits)
8537 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8538 |  |  |  | HR8537 (Lo-16bits)
8539 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8540 |  |  |  | HR8539 (Lo-16bits)
8541 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8542 |  |  |  | HR8541 (Lo-16bits)
8543 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8544 |  |  |  | HR8543 (Lo-16bits)
8545 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8546 |  |  |  | HR8545 (Lo-16bits)
8547 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8548 |  |  |  | HR8547 (Lo-16bits)
8549 | VUB2:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8550 |  |  |  | HR8549 (Lo-16bits)
8551 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8552 |  |  |  | HR8551 (Lo-16bits)
8553 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8554 |  |  |  | HR8553 (Lo-16bits)
8555 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8556 |  |  |  | HR8555 (Lo-16bits)
8557 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8558 |  |  |  | HR8557 (Lo-16bits)
8559 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8560 |  |  |  | HR8559 (Lo-16bits)
8561 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8562 |  |  |  | HR8561 (Lo-16bits)
8563 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8564 |  |  |  | HR8563 (Lo-16bits)
8565 | VUB2:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8566 |  |  |  | HR8565 (Lo-16bits)
8567 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8568 |  |  |  | HR8567 (Lo-16bits)
8569 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8570 |  |  |  | HR8569 (Lo-16bits)
8571 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8572 |  |  |  | HR8571 (Lo-16bits)
8573 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8574 |  |  |  | HR8573 (Lo-16bits)
8575 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8576 |  |  |  | HR8575 (Lo-16bits)
8577 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8578 |  |  |  | HR8577 (Lo-16bits)
8579 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8580 |  |  |  | HR8579 (Lo-16bits)
8581 | VUB2:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8582 |  |  |  | HR8581 (Lo-16bits)
8583 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8584 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8585 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8586 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8587 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8588 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8589 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8590 | VUB2:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8591 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8592 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8593 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8594 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8595 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8596 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8597 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8598 | VUB2:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8599 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8600 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8601 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8602 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8603 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8604 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8605 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8606 | VUB2:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8607 | VUB3:U1/2 >>>/<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8608 | VUB3:U1/2 >>>/<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8609 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8610 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8611 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8612 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8613 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8614 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8615 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8616 | VUB3:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8617 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8618 |  |  |  | HR8617 (Lo-16bits)
8619 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8620 |  |  |  | HR8619 (Lo-16bits)
8621 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8622 |  |  |  | HR8621 (Lo-16bits)
8623 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8624 |  |  |  | HR8623 (Lo-16bits)
8625 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8626 |  |  |  | HR8625 (Lo-16bits)
8627 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8628 |  |  |  | HR8627 (Lo-16bits)
8629 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8630 |  |  |  | HR8629 (Lo-16bits)
8631 | VUB3:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8632 |  |  |  | HR8631 (Lo-16bits)
8633 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8634 |  |  |  | HR8633 (Lo-16bits)
8635 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8636 |  |  |  | HR8635 (Lo-16bits)
8637 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8638 |  |  |  | HR8637 (Lo-16bits)
8639 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8640 |  |  |  | HR8639 (Lo-16bits)
8641 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8642 |  |  |  | HR8641 (Lo-16bits)
8643 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8644 |  |  |  | HR8643 (Lo-16bits)
8645 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8646 |  |  |  | HR8645 (Lo-16bits)
8647 | VUB3:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8648 |  |  |  | HR8647 (Lo-16bits)
8649 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8650 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8651 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8652 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8653 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8654 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8655 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8656 | VUB3:Delay type | R(W) | 1 | 0=DT;1=IDMT
8657 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8658 |  |  |  | HR8657 (Lo-16bits)
8659 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8660 |  |  |  | HR8659 (Lo-16bits)
8661 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8662 |  |  |  | HR8661 (Lo-16bits)
8663 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8664 |  |  |  | HR8663 (Lo-16bits)
8665 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8666 |  |  |  | HR8665 (Lo-16bits)
8667 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8668 |  |  |  | HR8667 (Lo-16bits)
8669 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8670 |  |  |  | HR8669 (Lo-16bits)
8671 | VUB3:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8672 |  |  |  | HR8671 (Lo-16bits)
8673 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8674 |  |  |  | HR8673 (Lo-16bits)
8675 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8676 |  |  |  | HR8675 (Lo-16bits)
8677 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8678 |  |  |  | HR8677 (Lo-16bits)
8679 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8680 |  |  |  | HR8679 (Lo-16bits)
8681 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8682 |  |  |  | HR8681 (Lo-16bits)
8683 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8684 |  |  |  | HR8683 (Lo-16bits)
8685 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8686 |  |  |  | HR8685 (Lo-16bits)
8687 | VUB3:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8688 |  |  |  | HR8687 (Lo-16bits)
8689 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8690 |  |  |  | HR8689 (Lo-16bits)
8691 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8692 |  |  |  | HR8691 (Lo-16bits)
8693 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8694 |  |  |  | HR8693 (Lo-16bits)
8695 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8696 |  |  |  | HR8695 (Lo-16bits)
8697 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8698 |  |  |  | HR8697 (Lo-16bits)
8699 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8700 |  |  |  | HR8699 (Lo-16bits)
8701 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8702 |  |  |  | HR8701 (Lo-16bits)
8703 | VUB3:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8704 |  |  |  | HR8703 (Lo-16bits)
8705 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8706 |  |  |  | HR8705 (Lo-16bits)
8707 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8708 |  |  |  | HR8707 (Lo-16bits)
8709 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8710 |  |  |  | HR8709 (Lo-16bits)
8711 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8712 |  |  |  | HR8711 (Lo-16bits)
8713 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8714 |  |  |  | HR8713 (Lo-16bits)
8715 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8716 |  |  |  | HR8715 (Lo-16bits)
8717 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8718 |  |  |  | HR8717 (Lo-16bits)
8719 | VUB3:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8720 |  |  |  | HR8719 (Lo-16bits)
8721 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8722 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8723 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8724 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8725 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8726 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8727 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8728 | VUB3:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8729 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8730 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8731 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8732 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8733 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8734 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8735 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8736 | VUB3:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8737 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8738 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8739 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8740 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8741 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8742 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8743 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8744 | VUB3:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8745 | VUB4:U1/2 >>>>/<<<< [47/27PN/59PN] mode | R(W) | 1 | 0=Disabled;1=Activated
8746 | VUB4:U1/2 >>>>/<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8747 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8748 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8749 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8750 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8751 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8752 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8753 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8754 | VUB4:Pick-up terms | R(W) | 1 | 0=Over >;1=Under <
8755 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8756 |  |  |  | HR8755 (Lo-16bits)
8757 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8758 |  |  |  | HR8757 (Lo-16bits)
8759 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8760 |  |  |  | HR8759 (Lo-16bits)
8761 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8762 |  |  |  | HR8761 (Lo-16bits)
8763 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8764 |  |  |  | HR8763 (Lo-16bits)
8765 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8766 |  |  |  | HR8765 (Lo-16bits)
8767 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8768 |  |  |  | HR8767 (Lo-16bits)
8769 | VUB4:Pick-up setting Uset | R(W) | 2 | FLOAT [5...150] (Hi-16bits)
8770 |  |  |  | HR8769 (Lo-16bits)
8771 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8772 |  |  |  | HR8771 (Lo-16bits)
8773 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8774 |  |  |  | HR8773 (Lo-16bits)
8775 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8776 |  |  |  | HR8775 (Lo-16bits)
8777 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8778 |  |  |  | HR8777 (Lo-16bits)
8779 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8780 |  |  |  | HR8779 (Lo-16bits)
8781 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8782 |  |  |  | HR8781 (Lo-16bits)
8783 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8784 |  |  |  | HR8783 (Lo-16bits)
8785 | VUB4:Under block setting Ublk | R(W) | 2 | FLOAT [0...80] (Hi-16bits)
8786 |  |  |  | HR8785 (Lo-16bits)
8787 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8788 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8789 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8790 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8791 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8792 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8793 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8794 | VUB4:Delay type | R(W) | 1 | 0=DT;1=IDMT
8795 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8796 |  |  |  | HR8795 (Lo-16bits)
8797 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8798 |  |  |  | HR8797 (Lo-16bits)
8799 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8800 |  |  |  | HR8799 (Lo-16bits)
8801 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8802 |  |  |  | HR8801 (Lo-16bits)
8803 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8804 |  |  |  | HR8803 (Lo-16bits)
8805 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8806 |  |  |  | HR8805 (Lo-16bits)
8807 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8808 |  |  |  | HR8807 (Lo-16bits)
8809 | VUB4:Definite operating time delay | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8810 |  |  |  | HR8809 (Lo-16bits)
8811 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8812 |  |  |  | HR8811 (Lo-16bits)
8813 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8814 |  |  |  | HR8813 (Lo-16bits)
8815 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8816 |  |  |  | HR8815 (Lo-16bits)
8817 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8818 |  |  |  | HR8817 (Lo-16bits)
8819 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8820 |  |  |  | HR8819 (Lo-16bits)
8821 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8822 |  |  |  | HR8821 (Lo-16bits)
8823 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8824 |  |  |  | HR8823 (Lo-16bits)
8825 | VUB4:Time dial setting k | R(W) | 2 | FLOAT [0.01...60] (Hi-16bits)
8826 |  |  |  | HR8825 (Lo-16bits)
8827 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8828 |  |  |  | HR8827 (Lo-16bits)
8829 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8830 |  |  |  | HR8829 (Lo-16bits)
8831 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8832 |  |  |  | HR8831 (Lo-16bits)
8833 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8834 |  |  |  | HR8833 (Lo-16bits)
8835 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8836 |  |  |  | HR8835 (Lo-16bits)
8837 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8838 |  |  |  | HR8837 (Lo-16bits)
8839 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8840 |  |  |  | HR8839 (Lo-16bits)
8841 | VUB4:IDMT Multiplier | R(W) | 2 | FLOAT [0.01...25] (Hi-16bits)
8842 |  |  |  | HR8841 (Lo-16bits)
8843 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8844 |  |  |  | HR8843 (Lo-16bits)
8845 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8846 |  |  |  | HR8845 (Lo-16bits)
8847 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8848 |  |  |  | HR8847 (Lo-16bits)
8849 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8850 |  |  |  | HR8849 (Lo-16bits)
8851 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8852 |  |  |  | HR8851 (Lo-16bits)
8853 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8854 |  |  |  | HR8853 (Lo-16bits)
8855 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8856 |  |  |  | HR8855 (Lo-16bits)
8857 | VUB4:Release Time delay | R(W) | 2 | FLOAT [0...150] (Hi-16bits)
8858 |  |  |  | HR8857 (Lo-16bits)
8859 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8860 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8861 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8862 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8863 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8864 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8865 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8866 | VUB4:Delayed Pick-up release | R(W) | 1 | 0=No;1=Yes
8867 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8868 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8869 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8870 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8871 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8872 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8873 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8874 | VUB4:Op.Time calc reset after release time | R(W) | 1 | 0=No;1=Yes
8875 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8876 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8877 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8878 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8879 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8880 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8881 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8882 | VUB4:Continue time calculation during release time | R(W) | 1 | 0=No;1=Yes
8883 | PGS1:PS1 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8884 | PGS1:PS2 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8885 | PGS1:PS3 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8886 | PGS1:PS4 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8887 | PGS1:PS5 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8888 | PGS1:PS6 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8889 | PGS1:PS7 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8890 | PGS1:PS8 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8891 | PGS1:PS9 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8892 | PGS1:PS10 >/< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8893 | FRQC1:f> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8894 | FRQC1:f>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8895 | FRQC1:f>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8896 | FRQC1:f>>>> [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8897 | FRQC1:f< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8898 | FRQC1:f<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8899 | FRQC1:f<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8900 | FRQC1:f<<<< [Curr] condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8901 | FRQV1:f</> [81O/81U] mode | R(W) | 1 | 0=Disabled;1=Activated
8902 | FRQV1:f> Enable | R(W) | 1 | 0=No;1=Yes
8903 | FRQV1:f> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8904 | FRQV1:f>> Enable | R(W) | 1 | 0=No;1=Yes
8905 | FRQV1:f>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8906 | FRQV1:f>>> Enable | R(W) | 1 | 0=No;1=Yes
8907 | FRQV1:f>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8908 | FRQV1:f>>>> Enable | R(W) | 1 | 0=No;1=Yes
8909 | FRQV1:f>>>> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8910 | FRQV1:f< Enable | R(W) | 1 | 0=No;1=Yes
8911 | FRQV1:f< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8912 | FRQV1:f<< Enable | R(W) | 1 | 0=No;1=Yes
8913 | FRQV1:f<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8914 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8915 | FRQV1:f<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8916 | FRQV1:f<<< Enable | R(W) | 1 | 0=No;1=Yes
8917 | FRQV1:f<<<< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
8918 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8919 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8920 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8921 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8922 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8923 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8924 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8925 | FRQV1:f> Used in SG | R(W) | 1 | 0=No;1=Yes
8926 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8927 |  |  |  | HR8926 (Lo-16bits)
8928 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8929 |  |  |  | HR8928 (Lo-16bits)
8930 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8931 |  |  |  | HR8930 (Lo-16bits)
8932 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8933 |  |  |  | HR8932 (Lo-16bits)
8934 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8935 |  |  |  | HR8934 (Lo-16bits)
8936 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8937 |  |  |  | HR8936 (Lo-16bits)
8938 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8939 |  |  |  | HR8938 (Lo-16bits)
8940 | FRQV1:f> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8941 |  |  |  | HR8940 (Lo-16bits)
8942 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8943 |  |  |  | HR8942 (Lo-16bits)
8944 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8945 |  |  |  | HR8944 (Lo-16bits)
8946 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8947 |  |  |  | HR8946 (Lo-16bits)
8948 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8949 |  |  |  | HR8948 (Lo-16bits)
8950 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8951 |  |  |  | HR8950 (Lo-16bits)
8952 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8953 |  |  |  | HR8952 (Lo-16bits)
8954 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8955 |  |  |  | HR8954 (Lo-16bits)
8956 | FRQV1:f> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8957 |  |  |  | HR8956 (Lo-16bits)
8958 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8959 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8960 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8961 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8962 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8963 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8964 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8965 | FRQV1:f>> Used in SG | R(W) | 1 | 0=No;1=Yes
8966 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8967 |  |  |  | HR8966 (Lo-16bits)
8968 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8969 |  |  |  | HR8968 (Lo-16bits)
8970 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8971 |  |  |  | HR8970 (Lo-16bits)
8972 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8973 |  |  |  | HR8972 (Lo-16bits)
8974 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8975 |  |  |  | HR8974 (Lo-16bits)
8976 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8977 |  |  |  | HR8976 (Lo-16bits)
8978 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8979 |  |  |  | HR8978 (Lo-16bits)
8980 | FRQV1:f>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
8981 |  |  |  | HR8980 (Lo-16bits)
8982 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8983 |  |  |  | HR8982 (Lo-16bits)
8984 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8985 |  |  |  | HR8984 (Lo-16bits)
8986 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8987 |  |  |  | HR8986 (Lo-16bits)
8988 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8989 |  |  |  | HR8988 (Lo-16bits)
8990 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8991 |  |  |  | HR8990 (Lo-16bits)
8992 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8993 |  |  |  | HR8992 (Lo-16bits)
8994 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8995 |  |  |  | HR8994 (Lo-16bits)
8996 | FRQV1:f>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
8997 |  |  |  | HR8996 (Lo-16bits)
8998 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
8999 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9000 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9001 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9002 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9003 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9004 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9005 | FRQV1:f>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9006 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9007 |  |  |  | HR9006 (Lo-16bits)
9008 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9009 |  |  |  | HR9008 (Lo-16bits)
9010 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9011 |  |  |  | HR9010 (Lo-16bits)
9012 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9013 |  |  |  | HR9012 (Lo-16bits)
9014 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9015 |  |  |  | HR9014 (Lo-16bits)
9016 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9017 |  |  |  | HR9016 (Lo-16bits)
9018 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9019 |  |  |  | HR9018 (Lo-16bits)
9020 | FRQV1:f>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9021 |  |  |  | HR9020 (Lo-16bits)
9022 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9023 |  |  |  | HR9022 (Lo-16bits)
9024 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9025 |  |  |  | HR9024 (Lo-16bits)
9026 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9027 |  |  |  | HR9026 (Lo-16bits)
9028 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9029 |  |  |  | HR9028 (Lo-16bits)
9030 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9031 |  |  |  | HR9030 (Lo-16bits)
9032 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9033 |  |  |  | HR9032 (Lo-16bits)
9034 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9035 |  |  |  | HR9034 (Lo-16bits)
9036 | FRQV1:f>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9037 |  |  |  | HR9036 (Lo-16bits)
9038 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9039 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9040 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9041 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9042 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9043 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9044 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9045 | FRQV1:f>>>> Used in SG | R(W) | 1 | 0=No;1=Yes
9046 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9047 |  |  |  | HR9046 (Lo-16bits)
9048 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9049 |  |  |  | HR9048 (Lo-16bits)
9050 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9051 |  |  |  | HR9050 (Lo-16bits)
9052 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9053 |  |  |  | HR9052 (Lo-16bits)
9054 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9055 |  |  |  | HR9054 (Lo-16bits)
9056 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9057 |  |  |  | HR9056 (Lo-16bits)
9058 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9059 |  |  |  | HR9058 (Lo-16bits)
9060 | FRQV1:f>>>> pick-up | R(W) | 2 | FLOAT [10...70] (Hi-16bits)
9061 |  |  |  | HR9060 (Lo-16bits)
9062 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9063 |  |  |  | HR9062 (Lo-16bits)
9064 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9065 |  |  |  | HR9064 (Lo-16bits)
9066 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9067 |  |  |  | HR9066 (Lo-16bits)
9068 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9069 |  |  |  | HR9068 (Lo-16bits)
9070 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9071 |  |  |  | HR9070 (Lo-16bits)
9072 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9073 |  |  |  | HR9072 (Lo-16bits)
9074 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9075 |  |  |  | HR9074 (Lo-16bits)
9076 | FRQV1:f>>>> Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9077 |  |  |  | HR9076 (Lo-16bits)
9078 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9079 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9080 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9081 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9082 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9083 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9084 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9085 | FRQV1:f< Used in SG | R(W) | 1 | 0=No;1=Yes
9086 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9087 |  |  |  | HR9086 (Lo-16bits)
9088 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9089 |  |  |  | HR9088 (Lo-16bits)
9090 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9091 |  |  |  | HR9090 (Lo-16bits)
9092 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9093 |  |  |  | HR9092 (Lo-16bits)
9094 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9095 |  |  |  | HR9094 (Lo-16bits)
9096 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9097 |  |  |  | HR9096 (Lo-16bits)
9098 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9099 |  |  |  | HR9098 (Lo-16bits)
9100 | FRQV1:f< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9101 |  |  |  | HR9100 (Lo-16bits)
9102 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9103 |  |  |  | HR9102 (Lo-16bits)
9104 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9105 |  |  |  | HR9104 (Lo-16bits)
9106 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9107 |  |  |  | HR9106 (Lo-16bits)
9108 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9109 |  |  |  | HR9108 (Lo-16bits)
9110 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9111 |  |  |  | HR9110 (Lo-16bits)
9112 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9113 |  |  |  | HR9112 (Lo-16bits)
9114 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9115 |  |  |  | HR9114 (Lo-16bits)
9116 | FRQV1:f< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9117 |  |  |  | HR9116 (Lo-16bits)
9118 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9119 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9120 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9121 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9122 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9123 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9124 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9125 | FRQV1:f<< Used in SG | R(W) | 1 | 0=No;1=Yes
9126 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9127 |  |  |  | HR9126 (Lo-16bits)
9128 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9129 |  |  |  | HR9128 (Lo-16bits)
9130 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9131 |  |  |  | HR9130 (Lo-16bits)
9132 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9133 |  |  |  | HR9132 (Lo-16bits)
9134 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9135 |  |  |  | HR9134 (Lo-16bits)
9136 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9137 |  |  |  | HR9136 (Lo-16bits)
9138 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9139 |  |  |  | HR9138 (Lo-16bits)
9140 | FRQV1:f<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9141 |  |  |  | HR9140 (Lo-16bits)
9142 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9143 |  |  |  | HR9142 (Lo-16bits)
9144 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9145 |  |  |  | HR9144 (Lo-16bits)
9146 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9147 |  |  |  | HR9146 (Lo-16bits)
9148 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9149 |  |  |  | HR9148 (Lo-16bits)
9150 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9151 |  |  |  | HR9150 (Lo-16bits)
9152 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9153 |  |  |  | HR9152 (Lo-16bits)
9154 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9155 |  |  |  | HR9154 (Lo-16bits)
9156 | FRQV1:f<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9157 |  |  |  | HR9156 (Lo-16bits)
9158 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9159 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9160 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9161 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9162 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9163 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9164 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9165 | FRQV1:f<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9166 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9167 |  |  |  | HR9166 (Lo-16bits)
9168 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9169 |  |  |  | HR9168 (Lo-16bits)
9170 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9171 |  |  |  | HR9170 (Lo-16bits)
9172 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9173 |  |  |  | HR9172 (Lo-16bits)
9174 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9175 |  |  |  | HR9174 (Lo-16bits)
9176 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9177 |  |  |  | HR9176 (Lo-16bits)
9178 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9179 |  |  |  | HR9178 (Lo-16bits)
9180 | FRQV1:f<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9181 |  |  |  | HR9180 (Lo-16bits)
9182 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9183 |  |  |  | HR9182 (Lo-16bits)
9184 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9185 |  |  |  | HR9184 (Lo-16bits)
9186 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9187 |  |  |  | HR9186 (Lo-16bits)
9188 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9189 |  |  |  | HR9188 (Lo-16bits)
9190 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9191 |  |  |  | HR9190 (Lo-16bits)
9192 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9193 |  |  |  | HR9192 (Lo-16bits)
9194 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9195 |  |  |  | HR9194 (Lo-16bits)
9196 | FRQV1:f<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9197 |  |  |  | HR9196 (Lo-16bits)
9198 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9199 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9200 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9201 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9202 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9203 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9204 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9205 | FRQV1:f<<<< Used in SG | R(W) | 1 | 0=No;1=Yes
9206 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9207 |  |  |  | HR9206 (Lo-16bits)
9208 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9209 |  |  |  | HR9208 (Lo-16bits)
9210 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9211 |  |  |  | HR9210 (Lo-16bits)
9212 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9213 |  |  |  | HR9212 (Lo-16bits)
9214 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9215 |  |  |  | HR9214 (Lo-16bits)
9216 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9217 |  |  |  | HR9216 (Lo-16bits)
9218 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9219 |  |  |  | HR9218 (Lo-16bits)
9220 | FRQV1:f<<<< pick-up | R(W) | 2 | FLOAT [7...65] (Hi-16bits)
9221 |  |  |  | HR9220 (Lo-16bits)
9222 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9223 |  |  |  | HR9222 (Lo-16bits)
9224 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9225 |  |  |  | HR9224 (Lo-16bits)
9226 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9227 |  |  |  | HR9226 (Lo-16bits)
9228 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9229 |  |  |  | HR9228 (Lo-16bits)
9230 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9231 |  |  |  | HR9230 (Lo-16bits)
9232 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9233 |  |  |  | HR9232 (Lo-16bits)
9234 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9235 |  |  |  | HR9234 (Lo-16bits)
9236 | FRQV1:f<<<< Op.time | R(W) | 2 | FLOAT [0...1800] (Hi-16bits)
9237 |  |  |  | HR9236 (Lo-16bits)
9238 | DFT1:df/dt >/< (1) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9239 | DFT1:df/dt >/< (2) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9240 | DFT1:df/dt >/< (3) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9241 | DFT1:df/dt >/< (4) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9242 | DFT1:df/dt >/< (5) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9243 | DFT1:df/dt >/< (6) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9244 | DFT1:df/dt >/< (7) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9245 | DFT1:df/dt >/< (8) condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9246 | RHC1:Counter is now | R | 1 | 0=Idle;1=Counting
9247 | RHC1:Running hours | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9248 |  |  |  | HR9247 (Lo-16bits)
9249 | RHC1:Start count | RW | 2 | UINT32 [0...4294967295] (Hi-16bits)
9250 |  |  |  | HR9249 (Lo-16bits)
9251 | GST1:Generator is now | R | 1 | 0=No/LightLoad;1=Normal load;2=Overloaded;3=On high overload
9252 | PWR1:PQS>/< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9253 | PWR2:PQS>>/<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9254 | PWR3:PQS>>>/<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9255 | PWR4:PQS>>>>/<<<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9256 | OPW1:P> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9257 | UPW1:P< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9258 | RPW1:Prev> condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked
9259 | SEF1:U03rd< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9260 | SEF1:U03rd< Measuring now | R | 1 | 0=No U0 avail!;1=U3 Input;2=U4 Input
9261 | UEX1:Q< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9262 | UIM1:Z< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9263 | UIM2:Z<< condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9264 | VOC1:Iv> condition | R | 1 | 0=Normal;1=Start; 2=Trip; 3=Blocked
9265 | VOC1:Voltage measurement | R | 1 | 0=Invalid U1 not avail.;1=Ok
9266 | VHZ1:V/Hz(1) > condition | R | 1 | 0=Normal;1=VHz(1) Blocked;2=VHz(1) Start;3=VHz(1) Alarm;4=VHz(1) Trip
9267 | VHZ1:V/Hz(2) > condition | R | 1 | 0=Normal;1=VHz(2) Start;2=VHz(2) Alarm;3=VHz(2) Trip;4=VHz(2) Blocked
9268 | UPF1:PF< condition | R | 1 | 0=Normal;1=Start;2=Trip;3=Blocked;4=Alarm Start;5=Alarm
9269 | RTDIN:S1 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9270 |  |  |  | HR9269 (Lo-16bits)
9271 | RTDIN:S1 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9272 |  |  |  | HR9271 (Lo-16bits)
9273 | RTDIN:S1 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9274 | RTDIN:S1 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9275 |  |  |  | HR9274 (Lo-16bits)
9276 | RTDIN:S2 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9277 |  |  |  | HR9276 (Lo-16bits)
9278 | RTDIN:S2 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9279 |  |  |  | HR9278 (Lo-16bits)
9280 | RTDIN:S2 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9281 | RTDIN:S2 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9282 |  |  |  | HR9281 (Lo-16bits)
9283 | RTDIN:S3 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9284 |  |  |  | HR9283 (Lo-16bits)
9285 | RTDIN:S3 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9286 |  |  |  | HR9285 (Lo-16bits)
9287 | RTDIN:S3 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9288 | RTDIN:S3 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9289 |  |  |  | HR9288 (Lo-16bits)
9290 | RTDIN:S4 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9291 |  |  |  | HR9290 (Lo-16bits)
9292 | RTDIN:S4 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9293 |  |  |  | HR9292 (Lo-16bits)
9294 | RTDIN:S4 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9295 | RTDIN:S4 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9296 |  |  |  | HR9295 (Lo-16bits)
9297 | RTDIN:S5 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9298 |  |  |  | HR9297 (Lo-16bits)
9299 | RTDIN:S5 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9300 |  |  |  | HR9299 (Lo-16bits)
9301 | RTDIN:S5 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9302 | RTDIN:S5 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9303 |  |  |  | HR9302 (Lo-16bits)
9304 | RTDIN:S6 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9305 |  |  |  | HR9304 (Lo-16bits)
9306 | RTDIN:S6 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9307 |  |  |  | HR9306 (Lo-16bits)
9308 | RTDIN:S6 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9309 | RTDIN:S6 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9310 |  |  |  | HR9309 (Lo-16bits)
9311 | RTDIN:S7 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9312 |  |  |  | HR9311 (Lo-16bits)
9313 | RTDIN:S7 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9314 |  |  |  | HR9313 (Lo-16bits)
9315 | RTDIN:S7 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9316 |  |  |  | HR9315 (Lo-16bits)
9317 | RTDIN:S7 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9318 | RTDIN:S7 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9319 |  |  |  | HR9318 (Lo-16bits)
9320 | RTDIN:S8 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9321 |  |  |  | HR9320 (Lo-16bits)
9322 | RTDIN:S8 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9323 |  |  |  | HR9322 (Lo-16bits)
9324 | RTDIN:S8 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9325 |  |  |  | HR9324 (Lo-16bits)
9326 | RTDIN:S8 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9327 | RTDIN:S8 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9328 |  |  |  | HR9327 (Lo-16bits)
9329 | RTDIN:S9 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9330 |  |  |  | HR9329 (Lo-16bits)
9331 | RTDIN:S9 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9332 |  |  |  | HR9331 (Lo-16bits)
9333 | RTDIN:S9 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9334 | RTDIN:S9 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9335 |  |  |  | HR9334 (Lo-16bits)
9336 | RTDIN:S10 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9337 |  |  |  | HR9336 (Lo-16bits)
9338 | RTDIN:S10 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9339 |  |  |  | HR9338 (Lo-16bits)
9340 | RTDIN:S10 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9341 | RTDIN:S10 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9342 |  |  |  | HR9341 (Lo-16bits)
9343 | RTDIN:S11 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9344 |  |  |  | HR9343 (Lo-16bits)
9345 | RTDIN:S11 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9346 |  |  |  | HR9345 (Lo-16bits)
9347 | RTDIN:S11 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9348 | RTDIN:S11 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9349 |  |  |  | HR9348 (Lo-16bits)
9350 | RTDIN:S12 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9351 |  |  |  | HR9350 (Lo-16bits)
9352 | RTDIN:S12 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9353 |  |  |  | HR9352 (Lo-16bits)
9354 | RTDIN:S12 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9355 | RTDIN:S12 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9356 |  |  |  | HR9355 (Lo-16bits)
9357 | RTDIN:S13 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9358 |  |  |  | HR9357 (Lo-16bits)
9359 | RTDIN:S13 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9360 |  |  |  | HR9359 (Lo-16bits)
9361 | RTDIN:S13 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9362 | RTDIN:S13 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9363 |  |  |  | HR9362 (Lo-16bits)
9364 | RTDIN:S14 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9365 |  |  |  | HR9364 (Lo-16bits)
9366 | RTDIN:S14 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9367 |  |  |  | HR9366 (Lo-16bits)
9368 | RTDIN:S14 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9369 | RTDIN:S14 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9370 |  |  |  | HR9369 (Lo-16bits)
9371 | RTDIN:S15 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9372 |  |  |  | HR9371 (Lo-16bits)
9373 | RTDIN:S15 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9374 |  |  |  | HR9373 (Lo-16bits)
9375 | RTDIN:S15 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9376 |  |  |  | HR9375 (Lo-16bits)
9377 | RTDIN:S15 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9378 | RTDIN:S15 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9379 |  |  |  | HR9378 (Lo-16bits)
9380 | RTDIN:S16 Measurement(Raw) | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9381 |  |  |  | HR9380 (Lo-16bits)
9382 | RTDIN:S16 Resistance | R | 2 | FLOAT [0...4000.000] (Hi-16bits)
9383 |  |  |  | HR9382 (Lo-16bits)
9384 | RTDIN:S16 Measurement mA | R | 2 | FLOAT [0.000...20.000] (Hi-16bits)
9385 |  |  |  | HR9384 (Lo-16bits)
9386 | RTDIN:S16 Sensor | R | 1 | 0=Invalid Open Circuit;1=OK;2=Invalid Shorted Circuit
9387 | RTDIN:S16 Filtered measurement | R | 2 | FLOAT [-200.0...2000.0] (Hi-16bits)
9388 |  |  |  | HR9387 (Lo-16bits)
9389 | RTD1:S1 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9390 |  |  |  | HR9389 (Lo-16bits)
9391 | RTD1:S2 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9392 |  |  |  | HR9391 (Lo-16bits)
9393 | RTD1:S3 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9394 |  |  |  | HR9393 (Lo-16bits)
9395 | RTD1:S4 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9396 |  |  |  | HR9395 (Lo-16bits)
9397 | RTD1:S5 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9398 |  |  |  | HR9397 (Lo-16bits)
9399 | RTD1:S6 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9400 |  |  |  | HR9399 (Lo-16bits)
9401 | RTD1:S7 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9402 |  |  |  | HR9401 (Lo-16bits)
9403 | RTD1:S8 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9404 |  |  |  | HR9403 (Lo-16bits)
9405 | RTD1:S9 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9406 |  |  |  | HR9405 (Lo-16bits)
9407 | RTD1:S10 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9408 |  |  |  | HR9407 (Lo-16bits)
9409 | RTD1:S11 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9410 |  |  |  | HR9409 (Lo-16bits)
9411 | RTD1:S12 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9412 |  |  |  | HR9411 (Lo-16bits)
9413 | RTD1:S13 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9414 |  |  |  | HR9413 (Lo-16bits)
9415 | RTD1:S14 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9416 |  |  |  | HR9415 (Lo-16bits)
9417 | RTD1:S15 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9418 |  |  |  | HR9417 (Lo-16bits)
9419 | RTD1:S16 Measurement (Protection) | R | 2 | FLOAT [-200...2000] (Hi-16bits)
9420 |  |  |  | HR9419 (Lo-16bits)
9421 | RTD1:S1 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9422 |  |  |  | HR9421 (Lo-16bits)
9423 | RTD1:S1 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9424 |  |  |  | HR9423 (Lo-16bits)
9425 | RTD1:S1 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9426 |  |  |  | HR9425 (Lo-16bits)
9427 | RTD1:S2 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9428 |  |  |  | HR9427 (Lo-16bits)
9429 | RTD1:S2 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9430 |  |  |  | HR9429 (Lo-16bits)
9431 | RTD1:S2 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9432 |  |  |  | HR9431 (Lo-16bits)
9433 | RTD1:S3 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9434 |  |  |  | HR9433 (Lo-16bits)
9435 | RTD1:S3 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9436 |  |  |  | HR9435 (Lo-16bits)
9437 | RTD1:S3 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9438 |  |  |  | HR9437 (Lo-16bits)
9439 | RTD1:S4 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9440 |  |  |  | HR9439 (Lo-16bits)
9441 | RTD1:S4 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9442 |  |  |  | HR9441 (Lo-16bits)
9443 | RTD1:S4 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9444 |  |  |  | HR9443 (Lo-16bits)
9445 | RTD1:S5 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9446 |  |  |  | HR9445 (Lo-16bits)
9447 | RTD1:S5 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9448 |  |  |  | HR9447 (Lo-16bits)
9449 | RTD1:S5 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9450 |  |  |  | HR9449 (Lo-16bits)
9451 | RTD1:S6 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9452 |  |  |  | HR9451 (Lo-16bits)
9453 | RTD1:S6 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9454 |  |  |  | HR9453 (Lo-16bits)
9455 | RTD1:S6 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9456 |  |  |  | HR9455 (Lo-16bits)
9457 | RTD1:S7 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9458 |  |  |  | HR9457 (Lo-16bits)
9459 | RTD1:S7 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9460 |  |  |  | HR9459 (Lo-16bits)
9461 | RTD1:S7 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9462 |  |  |  | HR9461 (Lo-16bits)
9463 | RTD1:S8 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9464 |  |  |  | HR9463 (Lo-16bits)
9465 | RTD1:S8 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9466 |  |  |  | HR9465 (Lo-16bits)
9467 | RTD1:S8 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9468 |  |  |  | HR9467 (Lo-16bits)
9469 | RTD1:S9 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9470 |  |  |  | HR9469 (Lo-16bits)
9471 | RTD1:S9 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9472 |  |  |  | HR9471 (Lo-16bits)
9473 | RTD1:S9 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9474 |  |  |  | HR9473 (Lo-16bits)
9475 | RTD1:S10 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9476 |  |  |  | HR9475 (Lo-16bits)
9477 | RTD1:S10 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9478 |  |  |  | HR9477 (Lo-16bits)
9479 | RTD1:S10 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9480 |  |  |  | HR9479 (Lo-16bits)
9481 | RTD1:S11 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9482 |  |  |  | HR9481 (Lo-16bits)
9483 | RTD1:S11 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9484 |  |  |  | HR9483 (Lo-16bits)
9485 | RTD1:S11 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9486 |  |  |  | HR9485 (Lo-16bits)
9487 | RTD1:S12 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9488 |  |  |  | HR9487 (Lo-16bits)
9489 | RTD1:S12 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9490 |  |  |  | HR9489 (Lo-16bits)
9491 | RTD1:S12 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9492 |  |  |  | HR9491 (Lo-16bits)
9493 | RTD1:S13 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9494 |  |  |  | HR9493 (Lo-16bits)
9495 | RTD1:S13 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9496 |  |  |  | HR9495 (Lo-16bits)
9497 | RTD1:S13 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9498 |  |  |  | HR9497 (Lo-16bits)
9499 | RTD1:S14 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9500 |  |  |  | HR9499 (Lo-16bits)
9501 | RTD1:S14 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9502 |  |  |  | HR9501 (Lo-16bits)
9503 | RTD1:S14 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9504 |  |  |  | HR9503 (Lo-16bits)
9505 | RTD1:S15 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9506 |  |  |  | HR9505 (Lo-16bits)
9507 | RTD1:S15 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9508 |  |  |  | HR9507 (Lo-16bits)
9509 | RTD1:S15 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9510 |  |  |  | HR9509 (Lo-16bits)
9511 | RTD1:S16 ALARM1 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9512 |  |  |  | HR9511 (Lo-16bits)
9513 | RTD1:S16 ALARM2 ON | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9514 |  |  |  | HR9513 (Lo-16bits)
9515 | RTD1:S16 MEAS INVALID | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9516 |  |  |  | HR9515 (Lo-16bits)
9517 | ARC1:I/I0 Arc> condition | R | 1 | 0b=Z1 Trip;1b=Z1 Blocked;2b=Z2 Trip;3b=Z2 Blocked;4b=Z3 Trip;5b=Z3 Blocked;6b=Z4 Trip;7b=Z4 Blocked
9518 | ARC1:I/I0 Arc> S1 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9519 |  |  |  | HR9518 (Lo-16bits)
9520 | ARC1:I/I0 Arc> S2 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9521 |  |  |  | HR9520 (Lo-16bits)
9522 | ARC1:I/I0 Arc> S3 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9523 |  |  |  | HR9522 (Lo-16bits)
9524 | ARC1:I/I0 Arc> S4 Sensor fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9525 |  |  |  | HR9524 (Lo-16bits)
9526 | ARC1:I/I0 Arc> IO unit fault | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9527 |  |  |  | HR9526 (Lo-16bits)
9528 | CTS1:CTS1 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9529 | CTS2:CTS2 condition | R | 1 | 0=Normal;1=Alarm;2=Blocked
9530 | VTS1:VTS condition | R | 1 | 0=Normal;1=Start;2=VTBusfail;3=VTLinefail;4=Blocked
9531 | VTS1:Bus voltages | R | 1 | 0=Bus dead;1=Bus Live VTS Ok SEQ Ok;2=Bus Live VTS Ok SEQ Rev;3=Bus Live VTS Ok SEQ Undef;4=Bus Live VTS problem
9532 | FLX1:Fault locator condition | R | 1 | 0=Idle;1=Triggered;2=Calc ready
9533 | THD1:THD condition | R | 1 | 0=Normal;1=Start;2=Alarm;3=Blocked
9534 | CBW1:CBW condition | R | 1 | 0=Normal;1=Alarm1 On;2=Alarm2 On
9535 | NJK1:U0> RECL condition | R | 1 | 0=Normal;1=Requested;2=Blocked;3=Active;4=BK clo cmd;5=Bk Closed.U0> blocked
9536 | SOF1:SOTF condition | R | 1 | 0=Normal;1=Init;2=Active;3=Trip;4=Blocked
9537 | PCS1:PCS1 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9538 |  |  |  | HR9537 (Lo-16bits)
9539 | PCS2:PCS2 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9540 |  |  |  | HR9539 (Lo-16bits)
9541 | PCS3:PCS3 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9542 |  |  |  | HR9541 (Lo-16bits)
9543 | PCS4:PCS4 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9544 |  |  |  | HR9543 (Lo-16bits)
9545 | PCS5:PCS5 Switch Status | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9546 |  |  |  | HR9545 (Lo-16bits)
9547 | SYN1:SYN1 Condition | R | 2 | 0b=SYN1 Blocked;1b=SYN1 Ok;2b=SYN1 Bypass;3b=SYN1 Vcond Ok;4b=SYN1 Vdiff Ok;5b=SYN1 Adiff Ok;6b=SYN1 fdiff Ok (Hi-16bits)
9548 |  |  |  | HR9547 (Lo-16bits)
9549 | SYN1:SYN2 Condition | R | 2 | 0b=SYN2 Blocked;1b=SYN2 Ok;2b=SYN2 Bypass;3b=SYN2 Vcond Ok;4b=SYN2 Vdiff Ok;5b=SYN2 Adiff Ok;6b=SYN2 fdiff Ok (Hi-16bits)
9550 |  |  |  | HR9549 (Lo-16bits)
9551 | SYN1:SYN3 Condition | R | 2 | 0b=SYN3 Blocked;1b=SYN3 Ok;2b=SYN3 Bypass;3b=SYN3 Vcond Ok;4b=SYN3 Vdiff Ok;5b=SYN3 Adiff Ok;6b=SYN3 fdiff Ok (Hi-16bits)
9552 |  |  |  | HR9551 (Lo-16bits)
9553 | SYN1:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9554 |  |  |  | HR9553 (Lo-16bits)
9555 | SYN1:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9556 |  |  |  | HR9555 (Lo-16bits)
9557 | SYN1:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9558 |  |  |  | HR9557 (Lo-16bits)
9559 | SYN1:SYN2 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9560 |  |  |  | HR9559 (Lo-16bits)
9561 | SYN1:SYN2 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9562 |  |  |  | HR9561 (Lo-16bits)
9563 | SYN1:SYN2 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9564 |  |  |  | HR9563 (Lo-16bits)
9565 | SYN1:SYN3 Estimated BRK Closing time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9566 |  |  |  | HR9565 (Lo-16bits)
9567 | SYN1:SYN3 Networks rotating time | R | 2 | FLOAT [0...360.000] (Hi-16bits)
9568 |  |  |  | HR9567 (Lo-16bits)
9569 | SYN1:SYN3 Networks placement atm | R | 2 | FLOAT [-360.000...360.000] (Hi-16bits)
9570 |  |  |  | HR9569 (Lo-16bits)
9571 | VJP1:<DELTA><alpha> > condition | R | 1 | 0=Normal;1=Blocked;2=Trip;3=Alarm
9572 | VJP1:Voltage meas selected | R | 1 | 0=Selection Ok;1=Selection not available
9573 | OBJ1:Object1 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9574 | OBJ2:Object2 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9575 | OBJ3:Object3 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9576 | OBJ4:Object4 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9577 | OBJ5:Object5 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9578 | OBJ6:Object6 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9579 | OBJ7:Object7 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9580 | OBJ8:Object8 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9581 | OBJ9:Object9 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9582 | OBJ10:Object10 Breaker Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9583 | CIN1:Ind.1 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9584 | CIN2:Ind.2 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9585 | CIN3:Ind.3 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9586 | CIN4:Ind.4 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9587 | CIN5:Ind.5 Object Status | R | 1 | 0=Intermediate;1=Open;2=Closed;3=Bad
9588 | AR1:Auto-recloser [79] Mode | RW | 1 | 0=Disabled;1=Activated
9589 | AR1:AR Status | R | 2 | 0b=AR is inhibit;1b=AR is ready;2b=AR is locked;3b=AR is running;4b=AR is not running;5b=Lock out delay is running;6b=Reclaim time counting;7b=Start time counting;8b=Dead time counting;9b=Arcing or discr time counting;10b=Reclaim time counting;11b=AR1 Requested;12b=AR2 Requested;13b=AR3 Requested;14b=AR4 Requested;15b=AR5 Requested;16b=Executing Shot1;17b=Executing Shot2;18b=Executing Shot3;19b=Executing Shot4;20b=Executing Shot5;21b=Shot Clear (Hi-16bits)
9590 |  |  |  | HR9589 (Lo-16bits)
9591 | AR1:Timer active | R | 1 | 0=-;1=AR Lockout;2=AR Reset Reclaim;3=AR Start Delay;4=AR Dead Time;5=AR Discrimination;6=AR Shot Reclaim;
9592 | VRG1:Vreg settings condition | R | 2 | 0b=U>> set too low;1b=U< set too high;2b=U> set higher than U>>;3b=U< set lower than U<<;4=U>>> set too low;5=U<<< set too high;6=VT selection not ok (Hi-16bits)
9593 |  |  |  | HR9592 (Lo-16bits)
9594 | VRG1:Vreg condition | R | 2 | 0b=Raise command on;1b=Lower command on;2b=Operation blocked;3b=Output control blocked;4b=U<<< Block on;5b=I> block on;6b=Tap on highlimit;7b=Tap on lowlimit;8b=Operation blocked;9b=U>/< pickup on;10b=U>>/<< pickup on;11b=Control wait time on;12b=Manual control on (Hi-16bits)
9595 |  |  |  | HR9594 (Lo-16bits)
9596 | VRG1:Vreg timer active | R | 1 | 0=-;1=Fine tune Decrease;2=Fine tune Increase;3=Low set Decrease;4=High set Degrease;5=Instant Decrease;6=Low set Increase;7=High set Increase
9597 | VRG1:Voltage now | R | 2 | FLOAT [0...140] (Hi-16bits)
9598 |  |  |  | HR9597 (Lo-16bits)
9599 | VRG1:Voltage difference to set target | R | 2 | FLOAT [-140...140] (Hi-16bits)
9600 |  |  |  | HR9599 (Lo-16bits)
9601 | VRG1:Voltage meas condition | R | 1 | 0=Not configured;1=System U12;2=System U23;3=System U31;4=VT4 meas U12;5=VT4 meas U23;6=VT4 meas U31;7=VT4 conf not ok
9602 | VRG1:Tap location now (- 0 +) | R | 2 | FLOAT [-30...30] (Hi-16bits)
9603 |  |  |  | HR9602 (Lo-16bits)
9604 | VRG1:Absolute tap location | R | 2 | FLOAT [0...50] (Hi-16bits)
9605 |  |  |  | HR9604 (Lo-16bits)
9606 | VRG1:Control mode | R | 1 | 0=Auto;1=Manual (loc&rem)
9607 | VRG1:Remote tap control input | RW | 1 | 0=Stop;1=Lower;2=Higher
9608 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9609 |  |  |  | HR9608 (Lo-16bits)
9610 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9611 |  |  |  | HR9610 (Lo-16bits)
9612 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9613 |  |  |  | HR9612 (Lo-16bits)
9614 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9615 |  |  |  | HR9614 (Lo-16bits)
9616 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9617 |  |  |  | HR9616 (Lo-16bits)
9618 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9619 |  |  |  | HR9618 (Lo-16bits)
9620 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9621 |  |  |  | HR9620 (Lo-16bits)
9622 | VRG1:Target Voltage (UTGT) | RW | 2 | FLOAT [70...140] (Hi-16bits)
9623 |  |  |  | HR9622 (Lo-16bits)
9624 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9625 |  |  |  | HR9624 (Lo-16bits)
9626 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9627 |  |  |  | HR9626 (Lo-16bits)
9628 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9629 |  |  |  | HR9628 (Lo-16bits)
9630 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9631 |  |  |  | HR9630 (Lo-16bits)
9632 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9633 |  |  |  | HR9632 (Lo-16bits)
9634 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9635 |  |  |  | HR9634 (Lo-16bits)
9636 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9637 |  |  |  | HR9636 (Lo-16bits)
9638 | VRG1:U> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9639 |  |  |  | HR9638 (Lo-16bits)
9640 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9641 |  |  |  | HR9640 (Lo-16bits)
9642 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9643 |  |  |  | HR9642 (Lo-16bits)
9644 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9645 |  |  |  | HR9644 (Lo-16bits)
9646 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9647 |  |  |  | HR9646 (Lo-16bits)
9648 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9649 |  |  |  | HR9648 (Lo-16bits)
9650 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9651 |  |  |  | HR9650 (Lo-16bits)
9652 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9653 |  |  |  | HR9652 (Lo-16bits)
9654 | VRG1:U< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9655 |  |  |  | HR9654 (Lo-16bits)
9656 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9657 |  |  |  | HR9656 (Lo-16bits)
9658 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9659 |  |  |  | HR9658 (Lo-16bits)
9660 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9661 |  |  |  | HR9660 (Lo-16bits)
9662 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9663 |  |  |  | HR9662 (Lo-16bits)
9664 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9665 |  |  |  | HR9664 (Lo-16bits)
9666 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9667 |  |  |  | HR9666 (Lo-16bits)
9668 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9669 |  |  |  | HR9668 (Lo-16bits)
9670 | VRG1:U>> setting (+UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9671 |  |  |  | HR9670 (Lo-16bits)
9672 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9673 |  |  |  | HR9672 (Lo-16bits)
9674 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9675 |  |  |  | HR9674 (Lo-16bits)
9676 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9677 |  |  |  | HR9676 (Lo-16bits)
9678 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9679 |  |  |  | HR9678 (Lo-16bits)
9680 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9681 |  |  |  | HR9680 (Lo-16bits)
9682 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9683 |  |  |  | HR9682 (Lo-16bits)
9684 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9685 |  |  |  | HR9684 (Lo-16bits)
9686 | VRG1:U<< setting (-UTGT) | RW | 2 | FLOAT [0.1...30] (Hi-16bits)
9687 |  |  |  | HR9686 (Lo-16bits)
9688 | EMON1:I> (50) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9689 | EMON1:I0> (50N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9690 | EMON1:Idir> (67) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9691 | EMON1:I0dir> (67N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9692 | EMON1:I0Int> (67NT) Monitor condition | R | 1 | 0=Normal;1=FLT FW;2=FLT REV
9693 | EMON1:U< (27) Monitor condition | R | 1 | 0=Normal;1=Undervoltage;2=No voltage
9694 | EMON1:U0> (59N) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9695 | EMON1:FL (21FL) Monitor condition | R | 1 | 0=Normal;1=FLT detected
9696 | ALARM:Alarms 1-32 | R | 2 | 0b=A1;1b=A2;2b=A3;3b=A4;4b=A5;5b=A6;6b=A7;7b=A8;8b=A9;9b=A10;10b=A11;11b=A12;12b=A13;13b=A14;14b=A15;15b=A16;16b=A17;17b=A18;18b=A19;19b=A20;20b=A21;21b=A22;22b=A23;23b=A24;24b=A25;25b=A26;26b=A27;27b=A28;28b=A29;29b=A30;30b=A31;31b=A32 (Hi-16bits)
9697 |  |  |  | HR9696 (Lo-16bits)
9698 | ALARM:Alarms 33-64 | R | 2 | 0b=A33;1b=A34;2b=A35;3b=A36;4b=A37;5b=A38;6b=A39;7b=A40;8b=A41;9b=A42;10b=A43;11b=A44;12b=A45;13b=A46;14b=A47;15b=A48;16b=A49;17b=A50;18b=A51;19b=A52;20b=A53;21b=A54;22b=A55;23b=A56;24b=A57;25b=A58;26b=A59;27b=A60;28b=A61;29b=A62;30b=A63;31b=A64 (Hi-16bits)
9699 |  |  |  | HR9698 (Lo-16bits)
9700 | GSYN:Synchronizer mode | RW | 1 | 0=Disabled;1=Activated
9701 | GSYN:Synchronizing by | RW | 1 | 0=Autosynchronizer;1=Manual commands
9702 | GSYN:Manual switching mode | RW | 1 | 0=Assisted synchroswitch;1=I know what I am doing
9703 | GSYN:Magnitude side A | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9704 |  |  |  | HR9703 (Lo-16bits)
9705 | GSYN:Magnitude side B | R | 2 | FLOAT [0.000...200.000] (Hi-16bits)
9706 |  |  |  | HR9705 (Lo-16bits)
9707 | GSYN:Frequency side A | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9708 |  |  |  | HR9707 (Lo-16bits)
9709 | GSYN:Frequency side B | R | 2 | FLOAT [0.000...75.000] (Hi-16bits)
9710 |  |  |  | HR9709 (Lo-16bits)
9711 | GSYN:Magnitude difference | R | 2 | FLOAT [-200...200] (Hi-16bits)
9712 |  |  |  | HR9711 (Lo-16bits)
9713 | GSYN:Frequency difference | R | 2 | FLOAT [-100...100] (Hi-16bits)
9714 |  |  |  | HR9713 (Lo-16bits)
9715 | GSYN:Angle difference | R | 2 | FLOAT [-360...360] (Hi-16bits)
9716 |  |  |  | HR9715 (Lo-16bits)
9717 | GSYN:Magnitude difference on closing BRK | R | 2 | FLOAT [-200...200] (Hi-16bits)
9718 |  |  |  | HR9717 (Lo-16bits)
9719 | GSYN:Frequency difference on closing BRK | R | 2 | FLOAT [-100...100] (Hi-16bits)
9720 |  |  |  | HR9719 (Lo-16bits)
9721 | GSYN:Angle difference on closing BRK | R | 2 | FLOAT [-360...360] (Hi-16bits)
9722 |  |  |  | HR9721 (Lo-16bits)
9723 | GSYN:Estimated BRK Closing time | R | 2 | FLOAT [0...360] (Hi-16bits)
9724 |  |  |  | HR9723 (Lo-16bits)
9725 | GSYN:Networks rotating time | R | 2 | FLOAT [0...360] (Hi-16bits)
9726 |  |  |  | HR9725 (Lo-16bits)
9727 | GSYN:Networks placement atm | R | 2 | FLOAT [-360...360] (Hi-16bits)
9728 |  |  |  | HR9727 (Lo-16bits)
9729 | GSYN:Synchronizing time left | R | 2 | FLOAT [0...1800] (Hi-16bits)
9730 |  |  |  | HR9729 (Lo-16bits)
9731 | GSYN:Magnitude difference fine tune | RW | 2 | FLOAT [-200...200] (Hi-16bits)
9732 |  |  |  | HR9731 (Lo-16bits)
9733 | GSYN:Frequency difference fine tune | RW | 2 | FLOAT [-100...100] (Hi-16bits)
9734 |  |  |  | HR9733 (Lo-16bits)
9735 | GSYN:Angle difference fine tune | RW | 2 | FLOAT [-360...360] (Hi-16bits)
9736 |  |  |  | HR9735 (Lo-16bits)
9737 | GSYN:Start Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9738 |  |  |  | HR9737 (Lo-16bits)
9739 | GSYN:Stop Synchronizer | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9740 |  |  |  | HR9739 (Lo-16bits)
9741 | GSYN:Block and Interrupt Synchronizing | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9742 |  |  |  | HR9741 (Lo-16bits)
9743 | GSYN:Breaker Closed | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9744 |  |  |  | HR9743 (Lo-16bits)
9745 | GSYN:Manual increase voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9746 |  |  |  | HR9745 (Lo-16bits)
9747 | GSYN:Manual decrease voltage | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9748 |  |  |  | HR9747 (Lo-16bits)
9749 | GSYN:Manual increase frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9750 |  |  |  | HR9749 (Lo-16bits)
9751 | GSYN:Manual decrease frequency | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9752 |  |  |  | HR9751 (Lo-16bits)
9753 | GSYN:Manual Close Breaker | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9754 |  |  |  | HR9753 (Lo-16bits)
9755 | GSYN:GSYN Voltage Mag.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9756 |  |  |  | HR9755 (Lo-16bits)
9757 | GSYN:GSYN Voltage Freq.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9758 |  |  |  | HR9757 (Lo-16bits)
9759 | GSYN:GSYN Voltage Ang.Difference Ok | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9760 |  |  |  | HR9759 (Lo-16bits)
9761 | GSYN:GSYN Blocked | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9762 |  |  |  | HR9761 (Lo-16bits)
9763 | GSYN:GSYN Running | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9764 |  |  |  | HR9763 (Lo-16bits)
9765 | GSYN:GSYN Increase Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9766 |  |  |  | HR9765 (Lo-16bits)
9767 | GSYN:GSYN Decrease Voltage | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9768 |  |  |  | HR9767 (Lo-16bits)
9769 | GSYN:GSYN Increase Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9770 |  |  |  | HR9769 (Lo-16bits)
9771 | GSYN:GSYN Decrease Frequency | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9772 |  |  |  | HR9771 (Lo-16bits)
9773 | GSYN:GSYN Breaker Close Pulse | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9774 |  |  |  | HR9773 (Lo-16bits)
9775 | GSYN:GSYN Long Sync Time | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9776 |  |  |  | HR9775 (Lo-16bits)
9777 | GSYN:GSYN Nets Standstill | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9778 |  |  |  | HR9777 (Lo-16bits)
9779 | GSYN:GSYN Nets Departing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9780 |  |  |  | HR9779 (Lo-16bits)
9781 | GSYN:GSYN Nets Enclosing | RW | 2 | SIGNAL_OUT [0...4294967295] (Hi-16bits)
9782 |  |  |  | HR9781 (Lo-16bits)
9783 | VREC:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9784 | VREC:Scale current values to primary | RW | 1 | 0=No;1=Yes
9785 | VREC:Record fault types (Overcurrrent & Voltage Over/Under) faults | RW | 1 | 0=No;1=Yes
9786 | VREC:Trigger register to memory | RW | 2 | SIGNAL_IN [0...4294967295] (Hi-16bits)
9787 |  |  |  | HR9786 (Lo-16bits)
9788 | VREC:VREC Magnitude 1 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9789 |  |  |  | HR9788 (Lo-16bits)
9790 | VREC:VREC Magnitude 2 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9791 |  |  |  | HR9790 (Lo-16bits)
9792 | VREC:VREC Magnitude 3 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9793 |  |  |  | HR9792 (Lo-16bits)
9794 | VREC:VREC Magnitude 4 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9795 |  |  |  | HR9794 (Lo-16bits)
9796 | VREC:VREC Magnitude 5 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9797 |  |  |  | HR9796 (Lo-16bits)
9798 | VREC:VREC Magnitude 6 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9799 |  |  |  | HR9798 (Lo-16bits)
9800 | VREC:VREC Magnitude 7 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9801 |  |  |  | HR9800 (Lo-16bits)
9802 | VREC:VREC Magnitude 8 | R | 2 | FLOAT [0...1800] (Hi-16bits)
9803 |  |  |  | HR9802 (Lo-16bits)
9804 | RTB:Measurement value recorder mode | RW | 1 | 0=Disabled;1=Activated
9805 | RTB:Scale current values to primary | RW | 1 | 0=No;1=Yes
9806 | RTB:RTS to bus Magnitude 1 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9807 |  |  |  | HR9806 (Lo-16bits)
9808 | RTB:RTS to bus Magnitude 2 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9809 |  |  |  | HR9808 (Lo-16bits)
9810 | RTB:RTS to bus Magnitude 3 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9811 |  |  |  | HR9810 (Lo-16bits)
9812 | RTB:RTS to bus Magnitude 4 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9813 |  |  |  | HR9812 (Lo-16bits)
9814 | RTB:RTS to bus Magnitude 5 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9815 |  |  |  | HR9814 (Lo-16bits)
9816 | RTB:RTS to bus Magnitude 6 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9817 |  |  |  | HR9816 (Lo-16bits)
9818 | RTB:RTS to bus Magnitude 7 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9819 |  |  |  | HR9818 (Lo-16bits)
9820 | RTB:RTS to bus Magnitude 8 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9821 |  |  |  | HR9820 (Lo-16bits)
9822 | RTB:RTS to bus Magnitude 9 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9823 |  |  |  | HR9822 (Lo-16bits)
9824 | RTB:RTS to bus Magnitude 10 | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9825 |  |  |  | HR9824 (Lo-16bits)
9826 | AOUT:mA In Channel 1 | R | 2 | FLOAT [0...24] (Hi-16bits)
9827 |  |  |  | HR9826 (Lo-16bits)
9828 | AOUT:mA In Channel 2 | R | 2 | FLOAT [0...24] (Hi-16bits)
9829 |  |  |  | HR9828 (Lo-16bits)
9830 | AOUT:mA Out Channel 1 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9831 |  |  |  | HR9830 (Lo-16bits)
9832 | AOUT:mA Out Channel 1 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9833 |  |  |  | HR9832 (Lo-16bits)
9834 | AOUT:mA Out Channel 2 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9835 |  |  |  | HR9834 (Lo-16bits)
9836 | AOUT:mA Out Channel 2 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9837 |  |  |  | HR9836 (Lo-16bits)
9838 | AOUT:mA Out Channel 3 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9839 |  |  |  | HR9838 (Lo-16bits)
9840 | AOUT:mA Out Channel 3 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9841 |  |  |  | HR9840 (Lo-16bits)
9842 | AOUT:mA Out Channel 4 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9843 |  |  |  | HR9842 (Lo-16bits)
9844 | AOUT:mA Out Channel 4 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9845 |  |  |  | HR9844 (Lo-16bits)
9846 | AOUT:mA Out Channel 5 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9847 |  |  |  | HR9846 (Lo-16bits)
9848 | AOUT:mA Out Channel 5 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9849 |  |  |  | HR9848 (Lo-16bits)
9850 | AOUT:mA Out Channel 6 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9851 |  |  |  | HR9850 (Lo-16bits)
9852 | AOUT:mA Out Channel 6 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9853 |  |  |  | HR9852 (Lo-16bits)
9854 | AOUT:mA Out Channel 7 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9855 |  |  |  | HR9854 (Lo-16bits)
9856 | AOUT:mA Out Channel 7 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9857 |  |  |  | HR9856 (Lo-16bits)
9858 | AOUT:mA Out Channel 8 Input Magnitude now | R | 2 | FLOAT [-10000000...10000000] (Hi-16bits)
9859 |  |  |  | HR9858 (Lo-16bits)
9860 | AOUT:mA Out Channel 8 Outputs now | R | 2 | FLOAT [0...24] (Hi-16bits)
9861 |  |  |  | HR9860 (Lo-16bits)
9906 | Object6 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9907 | Object7 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9908 | Object8 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9909 | Object9 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020
9910 | Object10 control register | R=0/W | 1 | SELECTOPEN=0xA001;SELECTCLOSE=0xA002,CANCEL=0xA004,OPERATE=0xA008,DIRECTOPEN=0xA010,DIRECTCLOSE=0xA020